## User Parameters
| Country | ηboiler | Cconversion, fossil | Cconversion, elec | CO2conversion,heat,fossil | CO2conversion,conventional, elec | Cost Solar Thermal System(FP) | Cost Solar Thermal System(ET) | Installation CostsSolarSystem | Cost Storage | Cost Chillerthermal | Cost Chillerref | Cost Heat Rejection | Installation CostsChiller;th | Installation CostsChiller;ref | Cfuel | Celectricity | Cwater | Cplanning,ref | Coperating,ref | Cmaintance,ref | Cplanning,SC+ | Coperating,SC+ | Cmaintance,SC+ | i | n | a
|  | [-] | [kWhheat, fossil/kWhPE] | [kWhelec, fossil/kWhPE] | [kgCO2l/kWhheat,useful] | [kgCO2l/kWhheat,useful] | [€/m²] | [€/m²] | [€/m²] | [€/m³] | [€] | [€] | [€] | [€] | [€] | [€/kWh] | [€/kWh] | [€/m³] | [€] | [€] | [€] | [€] | [€] | [€] | [%] | [a] | [-]
1 |  | 0.9 | 0.9 | 0.6 | 0.25 | 0.6 | 350 | 550 | 1 | 1000 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 20 | 8
1 | Italy | 0.9 | 0.9 | 0.6 | 0.25 | 0.6 | 350 | 550 | 1 | 1000 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 20 | 8
2 | Germany | 0.9 | 0.9 | 0.6 | 0.25 | 0.6 | 350 | 550 | 1 | 1000 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 20 | 8
3 | France | 0.9 | 0.9 | 0.6 | 0.25 | 0.6 | 350 | 550 | 1 | 1000 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 20 | 8
4 | Austria | 0.9 | 0.9 | 0.6 | 0.25 | 0.6 | 350 | 550 | 1 | 1000 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 20 | 8
5 | Spain | 0.9 | 0.9 | 0.6 | 0.25 | 0.6 | 350 | 550 | 1 | 1000 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 20 | 8
6 | Greece | 0.9 | 0.9 | 0.6 | 0.25 | 0.6 | 350 | 550 | 1 | 1000 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 20 | 8
7 | Portugal | 0.9 | 0.9 | 0.6 | 0.25 | 0.6 | 350 | 550 | 1 | 1000 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 20 | 8
8 | Sweden | 0.9 | 0.9 | 0.6 | 0.25 | 0.6 | 350 | 550 | 1 | 1000 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 20 | 8
9 | General | 0.9 | 0.9 | 0.6 | 0.25 | 0.6 | 350 | 550 | 1 | 1000 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 20 | 8
10 | User | 0.9 | 0.9 | 0.6 | 0.25 | 0.6 | 350 | 550 | 1 | 1000 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 20 | 8
row containing the integral data in single excel files (8673 in case of hourly data, 8762 in case of UNIBG, 15 in case of monthly data)
8763
1 | EURAC | 8763
2 | ISE | 15
3 | AEE | 15
4 | UNIBG | 8762
5 | CRES | 8763
MACRO

## Enviromental & Economic Results
Code | Code | ΔPEfossil | ΔPEelectricity | PEsave | PEref | Relative PEsave | PERSC+ | PERref | COPPE,SC+ | COPPE, ref | CO2save | Isolar system | Ichiller, thermal | Ichiller,compression | Coperating,SC+ | Coperating,ref | Cannual, ref | Cannual, SC+ | CPE
|  | [kWhPE] | [kWhPE] | [kWhPE] | [kWhPE] | [%] | [-] | [-] | [-] | [-] | [kgCO2] | [€] | [€] | [€] | [€/a] | [€/a] | [€/a] | [€/a] | [€/kWh/a]
1 | C-SOK-NAP-CC-ET-HC-R100 | -1585.7064 | 2775.6961 | 1189.9897 | 19593.7982 | 0.060733 | 1.0425 | 0.99423 | 1.1532 | 5.1533 | -1716.6656 | 9488 | 3 | 4 | 16286.5639 | 16524.8457 | 16565.8457 | 92223.5639 | 63.5785
2 | C-SOK-NAP-CC-ET-HC-R100 | -1023.4779 | 2771.0181 | 1747.5402 | 19655.974 | 0.088906 | 1.0742 | 0.99372 | 1.1647 | 5.1545 | 524.4519 | 9900 | 3 | 4 | 15839.3119 | 16580.7927 | 16621.7927 | 95072.312 | 44.892
3 | C-SOK-NAP-CC-ET-HC-R100 | -791.0228 | 2767.9817 | 1976.9589 | 19669.0309 | 0.10051 | 1.0879 | 0.99357 | 1.1788 | 5.1541 | 1449.2115 | 10313 | 3 | 4 | 15643.6767 | 16592.5452 | 16633.5452 | 98180.6767 | 41.2488
4 | C-SOK-NAP-CC-ET-HC-R100 | 705.2049 | 2827.8512 | 3533.056 | 19665.8665 | 0.17965 | 1.193 | 0.99367 | 1.378 | 5.1551 | 7533.9047 | 12938 | 3 | 4 | 14258.2656 | 16589.6607 | 16630.6607 | 117795.2657 | 28.6337
5 | C-SOK-NAP-CC-ET-HC-R100 | 1609.823 | 2821.4212 | 4431.2442 | 19708.3128 | 0.22484 | 1.262 | 0.99324 | 1.4564 | 5.1549 | 11141.6607 | 13500 | 3 | 4 | 13486.2074 | 16627.9008 | 16668.9008 | 121519.2074 | 23.6616
6 | C-SOK-NAP-CC-ET-HC-R100 | 2030.4281 | 2817.795 | 4848.2231 | 19713.9373 | 0.24593 | 1.2973 | 0.99324 | 1.519 | 5.1555 | 12818.0374 | 14063 | 3 | 4 | 13114.8423 | 16632.9046 | 16673.9046 | 125651.8423 | 22.4779
7 | C-SOK-NAP-CC-ET-HC-R100 | 2203.1491 | 2845.0018 | 5048.1509 | 19712.5143 | 0.25609 | 1.3152 | 0.99335 | 1.5058 | 5.157 | 13554.2659 | 16675 | 3 | 4 | 12941.7982 | 16631.6334 | 16672.6334 | 146374.7983 | 25.693
8 | C-SOK-NAP-CC-ET-HC-R100 | 3575.545 | 2846.0533 | 6421.5983 | 19744.1094 | 0.32524 | 1.4496 | 0.99308 | 1.716 | 5.1575 | 19045.6021 | 17400 | 3 | 4 | 11734.4423 | 16660.0647 | 16701.0647 | 150967.4423 | 20.9086
9 | C-SOK-NAP-CC-ET-HC-R100 | 4316.0553 | 2835.0898 | 7151.1451 | 19740.9967 | 0.36225 | 1.5339 | 0.9932 | 1.896 | 5.1589 | 21989.371 | 18125 | 3 | 4 | 11071.7309 | 16657.2345 | 16698.2345 | 156104.7309 | 19.4943
10 | C-SOK-NAP-CC-ET-HC-R10 | 3648.6132 | 2867.4306 | 6516.0438 | 19741.4191 | 0.33007 | 1.4603 | 0.99327 | 1.7041 | 5.1599 | 19373.5038 | 20125 | 3 | 4 | 11653.381 | 16657.5912 | 16698.5912 | 172686.3811 | 23.939
11 | C-SOK-NAP-CC-ET-HC-R10 | 5170.141 | 2859.6758 | 8029.8168 | 19770.9029 | 0.40614 | 1.647 | 0.99301 | 2.0175 | 5.1602 | 25446.6903 | 21000 | 3 | 4 | 10315.1872 | 16684.1195 | 16725.1195 | 178348.1872 | 20.1279
12 | C-SOK-NAP-CC-ET-HC-R10 | 6197.4108 | 2847.584 | 9044.9949 | 19766.4809 | 0.45759 | 1.8033 | 0.99305 | 2.3769 | 5.1601 | 29535.6167 | 21875 | 3 | 4 | 9393.9138 | 16680.134 | 16721.134 | 184426.9138 | 18.5413
13 | C-SOK-NAP-CC-ET-HC-R10 | 4750.874 | 2867.8063 | 7618.6804 | 19764.4669 | 0.38547 | 1.5917 | 0.99305 | 1.8578 | 5.16 | 23783.1733 | 23575 | 3 | 4 | 10681.8747 | 16678.3451 | 16719.3451 | 199314.8747 | 23.9668
14 | C-SOK-NAP-CC-ET-HC-R10 | 6492.579 | 2861.0046 | 9353.5836 | 19799.7401 | 0.47241 | 1.8534 | 0.99274 | 2.3459 | 5.1602 | 30738.6569 | 24600 | 3 | 4 | 9150.1141 | 16710.0379 | 16751.0379 | 205983.1141 | 20.231
15 | C-SOK-NAP-CC-ET-HC-R10 | 7740.9151 | 2856.2198 | 10597.1349 | 19796.8416 | 0.53529 | 2.1042 | 0.99276 | 2.9484 | 5.1601 | 35724.0267 | 25625 | 3 | 4 | 8026.9213 | 16707.4767 | 16748.4767 | 213059.9213 | 18.525
16 | C-SOK-NAP-CC-ET-HC-R600 | -2671.2725 | 3097.6969 | 426.4245 | 15393.5231 | 0.027702 | 1.0864 | 1.0744 | 1.1253 | 5.1941 | -5522.2616 | 9488 | 3 | 4 | 13189.603 | 12644.0759 | 12685.0759 | 89126.6031 | 179.2616
17 | C-SOK-NAP-CC-ET-HC-R600 | -2159.1917 | 3093.6967 | 934.505 | 15495.673 | 0.060307 | 1.1223 | 1.0725 | 1.1325 | 5.1935 | -3480.6055 | 9900 | 3 | 4 | 12823.0396 | 12735.9852 | 12776.9852 | 92056.0397 | 84.8353
18 | C-SOK-NAP-CC-ET-HC-R600 | -1889.9273 | 3090.8333 | 1200.906 | 15512.77 | 0.077414 | 1.1428 | 1.0722 | 1.1495 | 5.1933 | -2408.3204 | 10313 | 3 | 4 | 12597.8085 | 12751.3739 | 12792.3739 | 95134.8085 | 68.5669
19 | C-SOK-NAP-CC-ET-HC-R600 | -569.5697 | 3148.492 | 2578.9223 | 15505.373 | 0.16632 | 1.2648 | 1.0723 | 1.3236 | 5.1931 | 2969.2078 | 12938 | 3 | 4 | 11368.2178 | 12744.7003 | 12785.7003 | 114905.2179 | 39.5977
20 | C-SOK-NAP-CC-ET-HC-R600 | 335.0987 | 3141.8435 | 3476.9422 | 15576.8815 | 0.22321 | 1.3561 | 1.0712 | 1.402 | 5.1937 | 6576.8008 | 13500 | 3 | 4 | 10622.4081 | 12809.1031 | 12850.1031 | 118655.4081 | 30.4306
21 | C-SOK-NAP-CC-ET-HC-R600 | 891.3107 | 3138.1448 | 4029.4555 | 15582.0537 | 0.2586 | 1.4208 | 1.0711 | 1.4736 | 5.1943 | 8795.4841 | 14063 | 3 | 4 | 10128.6233 | 12813.6898 | 12854.6898 | 122665.6233 | 27.2521
22 | C-SOK-NAP-CC-ET-HC-R600 | 720.2027 | 3166.7093 | 3886.912 | 15575.6991 | 0.24955 | 1.4039 | 1.0713 | 1.4432 | 5.1954 | 8158.6595 | 16675 | 3 | 4 | 10259.77 | 12807.978 | 12848.978 | 143692.7701 | 33.6627
23 | C-SOK-NAP-CC-ET-HC-R600 | 2062.3414 | 3167.0643 | 5229.4056 | 15634.3568 | 0.33448 | 1.5817 | 1.0704 | 1.6446 | 5.1957 | 13527.8059 | 17400 | 3 | 4 | 9104.4617 | 12860.8075 | 12901.8075 | 148337.4617 | 25.8989
24 | C-SOK-NAP-CC-ET-HC-R600 | 2892.3471 | 3158.7807 | 6051.1278 | 15640.4991 | 0.38689 | 1.7168 | 1.0703 | 1.8075 | 5.1961 | 16834.0227 | 18125 | 3 | 4 | 8367.9218 | 12866.3026 | 12907.3026 | 153400.9218 | 23.2178
25 | C-SOK-NAP-CC-ET-HC-R60 | 2015.659 | 3189.9727 | 5205.6317 | 15618.0883 | 0.33331 | 1.5796 | 1.0709 | 1.6315 | 5.1978 | 13379.2572 | 20125 | 3 | 4 | 9118.024 | 12846.1008 | 12887.1008 | 170151.0241 | 30.2103
26 | C-SOK-NAP-CC-ET-HC-R60 | 3510.7809 | 3186.773 | 6697.5539 | 15664.3143 | 0.42757 | 1.8385 | 1.0701 | 1.936 | 5.1979 | 19354.4118 | 21000 | 3 | 4 | 7815.9346 | 12887.7012 | 12928.7012 | 175848.9346 | 24.3253
27 | C-SOK-NAP-CC-ET-HC-R60 | 4570.7801 | 3172.4979 | 7743.278 | 15672.2688 | 0.49408 | 2.08 | 1.0699 | 2.2653 | 5.1981 | 23570.6167 | 21875 | 3 | 4 | 6877.6942 | 12894.8949 | 12935.8949 | 181910.6942 | 21.8221
28 | C-SOK-NAP-CC-ET-HC-R60 | 2914.8476 | 3186.6948 | 6101.5424 | 15654.4134 | 0.38977 | 1.7248 | 1.0702 | 1.7616 | 5.1976 | 16970.5485 | 23575 | 3 | 4 | 8343.3964 | 12878.7761 | 12919.7761 | 196976.3964 | 30.1656
29 | C-SOK-NAP-CC-ET-HC-R60 | 4644.2916 | 3187.7815 | 7832.0732 | 15687.5018 | 0.49926 | 2.101 | 1.0697 | 2.2106 | 5.1978 | 23890.1358 | 24600 | 3 | 4 | 6816.0408 | 12908.5722 | 12949.5722 | 203649.0408 | 24.3485
30 | C-SOK-NAP-CC-ET-HC-R60 | 5861.0425 | 3180.0806 | 9041.1231 | 15704.1549 | 0.57572 | 2.4791 | 1.0695 | 2.7573 | 5.1984 | 28744.3045 | 25625 | 3 | 4 | 5740.5213 | 12923.5079 | 12964.5079 | 210773.5213 | 21.8788
31 | C-SOK-NAP-CC-ET-WC-R100 | -2627.295 | 3676.1433 | 1048.8483 | 27052.7946 | 0.03877 | 1.0253 | 0.99646 | 1.1181 | 5.0971 | -4382.2745 | 13250 | 3 | 4 | 22982.8158 | 22798.0898 | 22839.0898 | 129015.8159 | 101.2317
32 | C-SOK-NAP-CC-ET-WC-R100 | -1845.3404 | 3666.4042 | 1821.0638 | 27120.7918 | 0.067146 | 1.056 | 0.99599 | 1.1376 | 5.0971 | -1270.688 | 13800 | 3 | 4 | 22346.1143 | 22859.291 | 22900.291 | 132779.1143 | 60.3377
33 | C-SOK-NAP-CC-ET-WC-R100 | -1568.5083 | 3661.2663 | 2092.7581 | 27137.4282 | 0.077117 | 1.0673 | 0.99588 | 1.1445 | 5.0971 | -171.9225 | 14400 | 3 | 4 | 22115.0512 | 22874.2721 | 22915.2721 | 137348.0512 | 54.6804
34 | C-SOK-NAP-CC-ET-WC-R100 | 255.2566 | 3700.4475 | 3955.7041 | 27153.5993 | 0.14568 | 1.1528 | 0.99576 | 1.2869 | 5.097 | 7188.4388 | 18400 | 3 | 4 | 20464.6833 | 22888.7861 | 22929.7861 | 167697.6834 | 36.5973
35 | C-SOK-NAP-CC-ET-WC-R100 | 1544.2425 | 3686.2303 | 5230.4728 | 27203.358 | 0.19227 | 1.2191 | 0.9956 | 1.3554 | 5.0996 | 12320.6871 | 19200 | 3 | 4 | 19357.8728 | 22933.4856 | 22974.4856 | 172990.8728 | 28.6812
36 | C-SOK-NAP-CC-ET-WC-R100 | 2167.6336 | 3680.5854 | 5848.2191 | 27206.7364 | 0.21495 | 1.2544 | 0.99561 | 1.4164 | 5.1002 | 14804.8436 | 20000 | 3 | 4 | 18803.293 | 22936.5434 | 22977.5434 | 178836.293 | 26.6506
37 | C-SOK-NAP-CC-ET-WC-R100 | 2359.8584 | 3720.6937 | 6080.5522 | 27208.45 | 0.22348 | 1.2681 | 0.99557 | 1.4264 | 5.0997 | 15640.5899 | 23275 | 3 | 4 | 18607.7257 | 22938.0805 | 22979.0805 | 204840.7257 | 29.9087
38 | C-SOK-NAP-CC-ET-WC-R100 | 4120.4219 | 3702.1588 | 7822.5807 | 27253.0778 | 0.28703 | 1.3807 | 0.99525 | 1.5735 | 5.0995 | 22651.9524 | 24325 | 3 | 4 | 17074.5312 | 22978.2172 | 23019.2172 | 211707.5312 | 24.121
39 | C-SOK-NAP-CC-ET-WC-R100 | 5094.9799 | 3696.0284 | 8791.0084 | 27246.1338 | 0.32265 | 1.4536 | 0.99544 | 1.7195 | 5.1017 | 26539.9672 | 25325 | 3 | 4 | 16194.8933 | 22971.9498 | 23012.9498 | 218827.8933 | 22.2745
40 | C-SOK-NAP-CC-ET-WC-R10 | 4152.7943 | 3728.2073 | 7881.0015 | 27256.819 | 0.28914 | 1.3849 | 0.99533 | 1.5524 | 5.1011 | 22824.8558 | 28200 | 3 | 4 | 17033.0695 | 22981.5364 | 23022.5364 | 242666.0695 | 27.87
41 | C-SOK-NAP-CC-ET-WC-R10 | 6164.0571 | 3712.0652 | 9876.1223 | 27288.817 | 0.36191 | 1.5425 | 0.9951 | 1.7857 | 5.1009 | 30843.0037 | 29400 | 3 | 4 | 15261.4596 | 23010.3161 | 23051.3161 | 250494.4596 | 23.0296
42 | C-SOK-NAP-CC-ET-WC-R10 | 7524.7411 | 3700.1568 | 11224.898 | 27279.9562 | 0.41147 | 1.6726 | 0.99519 | 2.0416 | 5.1013 | 36265.8926 | 30650 | 3 | 4 | 14036.0931 | 23002.3535 | 23043.3535 | 259269.0931 | 21.0448
43 | C-SOK-NAP-CC-ET-WC-R10 | 5579.193 | 3726.3871 | 9305.5801 | 27290.333 | 0.34098 | 1.4935 | 0.9951 | 1.6586 | 5.101 | 28527.4172 | 33350 | 3 | 4 | 15780.6009 | 23011.6969 | 23052.6969 | 282613.6009 | 27.893
44 | C-SOK-NAP-CC-ET-WC-R10 | 7968.2136 | 3707.5228 | 11675.7364 | 27328.0728 | 0.42724 | 1.7181 | 0.99488 | 2.0113 | 5.1015 | 38052.059 | 34800 | 3 | 4 | 13675.7855 | 23045.6032 | 23086.6032 | 292108.7855 | 23.0411
45 | C-SOK-NAP-CC-ET-WC-R10 | 9665.3282 | 3690.1915 | 13355.5197 | 27325.6402 | 0.48875 | 1.9248 | 0.99488 | 2.428 | 5.1014 | 44811.632 | 36250 | 3 | 4 | 12156.76 | 23043.4938 | 23084.4938 | 302189.76 | 20.8981
46 | C-SOK-NAP-CC-ET-WC-R600 | -4402.6489 | 4088.9567 | -313.6922 | 21004.0239 | -0.014935 | 1.0518 | 1.0808 | 1.0862 | 5.1393 | -10795.6679 | 13250 | 3 | 4 | 18743.6888 | 17205.8584 | 17246.8584 | 124776.6889 | -342.7877
47 | C-SOK-NAP-CC-ET-WC-R600 | -3703.2785 | 4077.5043 | 374.2258 | 21105.2526 | 0.017731 | 1.0854 | 1.0794 | 1.1 | 5.1384 | -8017.2734 | 13800 | 3 | 4 | 18212.2243 | 17296.95 | 17337.95 | 128645.2243 | 297.4334
48 | C-SOK-NAP-CC-ET-WC-R600 | -3379.9283 | 4072.1676 | 692.2392 | 21114.9194 | 0.032784 | 1.1022 | 1.0793 | 1.111 | 5.1388 | -6732.7674 | 14400 | 3 | 4 | 17933.1356 | 17305.65 | 17346.65 | 133166.1356 | 167.3114
49 | C-SOK-NAP-CC-ET-WC-R600 | -1848.3929 | 4113.768 | 2265.3751 | 21141.9588 | 0.10715 | 1.1935 | 1.0788 | 1.231 | 5.1374 | -537.2915 | 18400 | 3 | 4 | 16554.1311 | 17329.9766 | 17370.9766 | 163787.1312 | 64.6322
50 | C-SOK-NAP-CC-ET-WC-R600 | -574.3052 | 4098.8924 | 3524.5873 | 21217.01 | 0.16612 | 1.277 | 1.078 | 1.3041 | 5.1391 | 4534.2667 | 19200 | 3 | 4 | 15483.9479 | 17397.4973 | 17438.4973 | 169116.9479 | 43.0344
51 | C-SOK-NAP-CC-ET-WC-R600 | 182.3993 | 4093.0089 | 4275.4082 | 21217.5601 | 0.2015 | 1.3337 | 1.0781 | 1.362 | 5.14 | 7551.2786 | 20000 | 3 | 4 | 14806.9571 | 17397.9848 | 17438.9848 | 174839.9571 | 36.8154
52 | C-SOK-NAP-CC-ET-WC-R600 | 20.7388 | 4135.5388 | 4156.2776 | 21220.4185 | 0.19586 | 1.3242 | 1.078 | 1.3639 | 5.1392 | 6975.5198 | 23275 | 3 | 4 | 14929.472 | 17400.5565 | 17441.5565 | 201162.472 | 44.2032
53 | C-SOK-NAP-CC-ET-WC-R600 | 1712.9834 | 4117.8164 | 5830.7998 | 21286.6778 | 0.27392 | 1.4655 | 1.0772 | 1.503 | 5.1393 | 13714.9609 | 24325 | 3 | 4 | 13476.724 | 17460.1396 | 17501.1396 | 208109.724 | 32.69
54 | C-SOK-NAP-CC-ET-WC-R600 | 2878.4019 | 4109.185 | 6987.5869 | 21286.7316 | 0.32826 | 1.5842 | 1.0773 | 1.6388 | 5.1406 | 18362.2492 | 25325 | 3 | 4 | 12433.1367 | 17460.2022 | 17501.2022 | 215066.1367 | 28.2737
55 | C-SOK-NAP-CC-ET-WC-R60 | 1530.6535 | 4141.574 | 5672.2275 | 21284.2403 | 0.2665 | 1.4508 | 1.0772 | 1.48 | 5.1397 | 13025.2374 | 28200 | 3 | 4 | 13624.3485 | 17457.9231 | 17498.9231 | 239257.3485 | 39.0955
56 | C-SOK-NAP-CC-ET-WC-R60 | 3479.8261 | 4127.6922 | 7607.5184 | 21326.0705 | 0.35672 | 1.6536 | 1.0768 | 1.6963 | 5.1404 | 20798.7916 | 29400 | 3 | 4 | 11916.1937 | 17495.6452 | 17536.6452 | 247149.1937 | 30.1823
57 | C-SOK-NAP-CC-ET-WC-R60 | 4969.0759 | 4112.9091 | 9081.9851 | 21334.9676 | 0.42569 | 1.8519 | 1.0766 | 1.9452 | 5.1403 | 26731.1522 | 30650 | 3 | 4 | 10592.7883 | 17503.6158 | 17544.6158 | 255825.7883 | 26.2367
58 | C-SOK-NAP-CC-ET-WC-R60 | 2740.7771 | 4142.5049 | 6883.282 | 21326.8621 | 0.32275 | 1.5707 | 1.0768 | 1.5828 | 5.141 | 17867.2834 | 33350 | 3 | 4 | 12573.1082 | 17496.3086 | 17537.3086 | 279406.1082 | 38.0442
59 | C-SOK-NAP-CC-ET-WC-R60 | 5086.9224 | 4122.9352 | 9209.8576 | 21356.5691 | 0.43124 | 1.8697 | 1.0764 | 1.9089 | 5.141 | 27219.2484 | 34800 | 3 | 4 | 10500.1143 | 17523.0275 | 17564.0275 | 288933.1143 | 29.4651
60 | C-SOK-NAP-CC-ET-WC-R60 | 6773.9068 | 4105.9892 | 10879.896 | 21378.2811 | 0.50892 | 2.1649 | 1.0761 | 2.2986 | 5.1408 | 33938.9425 | 36250 | 3 | 4 | 9011.644 | 17542.5787 | 17583.5787 | 299044.644 | 25.8698
61 | C-SOK-NAP-CC-FP-HC-R100 | -2881.0715 | 2756.0408 | -125.0307 | 19556.6035 | -0.0063933 | 0.97323 | 0.99458 | 1.0266 | 5.1531 | -6930.8847 | 6188 | 3 | 4 | 17430.6848 | 16491.345 | 16532.345 | 66967.6849 | -403.3836
62 | C-SOK-NAP-CC-FP-HC-R100 | -2293.306 | 2755.6409 | 462.3349 | 19621.4822 | 0.023563 | 1.0025 | 0.99393 | 1.0273 | 5.1527 | -4580.4892 | 6600 | 3 | 4 | 16960.3376 | 16549.7467 | 16590.7467 | 69793.3377 | 115.0737
63 | C-SOK-NAP-CC-FP-HC-R100 | -2040.2285 | 2756.7669 | 716.5384 | 19634.5937 | 0.036494 | 1.0158 | 0.99381 | 1.032 | 5.1527 | -3566.3025 | 7013 | 3 | 4 | 16743.6828 | 16561.5373 | 16602.5373 | 72880.6828 | 78.5417
64 | C-SOK-NAP-CC-FP-HC-R100 | -873.0928 | 2793.9462 | 1920.8534 | 19629.9798 | 0.097853 | 1.0851 | 0.99395 | 1.1704 | 5.1543 | 1164.2058 | 8438 | 3 | 4 | 15666.8017 | 16557.3859 | 16598.3859 | 83203.8018 | 34.6749
65 | C-SOK-NAP-CC-FP-HC-R100 | -24.5827 | 2793.9697 | 2769.3869 | 19675.4158 | 0.14075 | 1.1388 | 0.99348 | 1.2044 | 5.1535 | 4558.2852 | 9000 | 3 | 4 | 14943.9928 | 16598.2501 | 16639.2501 | 86976.9928 | 25.3983
66 | C-SOK-NAP-CC-FP-HC-R100 | 414.7271 | 2796.0026 | 3210.7297 | 19683.013 | 0.16312 | 1.1692 | 0.99347 | 1.237 | 5.1546 | 6318.9126 | 9563 | 3 | 4 | 14554.2386 | 16605.0946 | 16646.0946 | 91091.2386 | 23.1864
67 | C-SOK-NAP-CC-FP-HC-R100 | 605.4942 | 2803.2752 | 3408.7694 | 19678.4719 | 0.17322 | 1.1836 | 0.9936 | 1.2723 | 5.156 | 7094.1022 | 10875 | 3 | 4 | 14374.1067 | 16601.0166 | 16642.0166 | 101407.1068 | 24.8668
68 | C-SOK-NAP-CC-FP-HC-R100 | 1803.8823 | 2805.8082 | 4609.6905 | 19716.2832 | 0.2338 | 1.2768 | 0.9933 | 1.3741 | 5.1568 | 11891.8762 | 11600 | 3 | 4 | 13328.0562 | 16635.0352 | 16676.0352 | 106161.0562 | 19.4124
69 | C-SOK-NAP-CC-FP-HC-R100 | 2449.9338 | 2800.7706 | 5250.7044 | 19719.6179 | 0.26627 | 1.3333 | 0.99327 | 1.4473 | 5.1569 | 14467.6863 | 12325 | 3 | 4 | 12752.6566 | 16638.0594 | 16679.0594 | 111385.6566 | 18.0369
70 | C-SOK-NAP-CC-FP-HC-R10 | 1849.1037 | 2816.2258 | 4665.3295 | 19710.4738 | 0.23669 | 1.2819 | 0.99345 | 1.3944 | 5.1582 | 12090.1245 | 13125 | 3 | 4 | 13275.8184 | 16629.7472 | 16670.7472 | 118308.8185 | 21.7858
71 | C-SOK-NAP-CC-FP-HC-R10 | 3364.7537 | 2816.2605 | 6181.0143 | 19744.4251 | 0.31305 | 1.424 | 0.9932 | 1.5788 | 5.1594 | 18152.7825 | 14000 | 3 | 4 | 11942.2851 | 16660.3198 | 16701.3198 | 123975.2851 | 17.3554
72 | C-SOK-NAP-CC-FP-HC-R10 | 4290.2056 | 2810.2278 | 7100.4335 | 19740.9139 | 0.35968 | 1.5276 | 0.99311 | 1.7434 | 5.1574 | 21844.5356 | 14875 | 3 | 4 | 11109.8504 | 16657.1721 | 16698.1721 | 130142.8504 | 15.9771
73 | C-SOK-NAP-CC-FP-HC-R10 | 2824.3112 | 2817.9265 | 5642.2376 | 19736.6289 | 0.28588 | 1.37 | 0.99328 | 1.4887 | 5.1594 | 15993.7889 | 15375 | 3 | 4 | 12420.6356 | 16653.2715 | 16694.2715 | 135453.6356 | 21.0483
74 | C-SOK-NAP-CC-FP-HC-R10 | 4648.6781 | 2820.676 | 7469.3541 | 19765.775 | 0.37789 | 1.5722 | 0.99301 | 1.7913 | 5.1594 | 23295.8392 | 16400 | 3 | 4 | 10803.2703 | 16679.4863 | 16720.4863 | 142036.2703 | 16.7773
75 | C-SOK-NAP-CC-FP-HC-R10 | 5759.139 | 2820.3168 | 8579.4558 | 19760.1316 | 0.43418 | 1.7286 | 0.99303 | 2.0732 | 5.1589 | 27737.0842 | 17425 | 3 | 4 | 9799.0138 | 16674.429 | 16715.429 | 149232.0138 | 15.4458
76 | C-SOK-NAP-CC-FP-HC-R600 | -4038.143 | 3076.3763 | -961.7667 | 15329.6829 | -0.062739 | 0.99485 | 1.0754 | 1.0084 | 5.1931 | -11025.2782 | 6188 | 3 | 4 | 14375.1085 | 12586.6056 | 12627.6056 | 63912.1086 | -53.3232
77 | C-SOK-NAP-CC-FP-HC-R600 | -3517.4926 | 3075.6812 | -441.8114 | 15431.5356 | -0.02863 | 1.0262 | 1.0736 | 1.0084 | 5.1925 | -8943.8351 | 6600 | 3 | 4 | 13998.6244 | 12678.2897 | 12719.2897 | 66831.6245 | -122.4784
78 | C-SOK-NAP-CC-FP-HC-R600 | -3295.0523 | 3076.25 | -218.8023 | 15453.1392 | -0.014159 | 1.0405 | 1.0732 | 1.0132 | 5.1924 | -8053.1257 | 7013 | 3 | 4 | 13817.5461 | 12697.7491 | 12738.7491 | 69954.5461 | -261.4954
79 | C-SOK-NAP-CC-FP-HC-R600 | -2182.8211 | 3110.5621 | 927.741 | 15442.6109 | 0.060077 | 1.123 | 1.0735 | 1.1397 | 5.1939 | -3547.0143 | 8438 | 3 | 4 | 12786.4458 | 12688.2441 | 12729.2441 | 80323.4459 | 72.8589
80 | C-SOK-NAP-CC-FP-HC-R600 | -1403.3377 | 3110.4393 | 1707.1016 | 15523.9176 | 0.10997 | 1.1845 | 1.0721 | 1.1744 | 5.1942 | -429.2854 | 9000 | 3 | 4 | 12158.1486 | 12761.4083 | 12802.4083 | 84191.1486 | 41.8187
81 | C-SOK-NAP-CC-FP-HC-R600 | -967.3585 | 3110.9121 | 2143.5536 | 15533.7719 | 0.13799 | 1.2228 | 1.0719 | 1.2032 | 5.1937 | 1315.4195 | 9563 | 3 | 4 | 11774.3362 | 12770.2608 | 12811.2608 | 88311.3362 | 35.2219
82 | C-SOK-NAP-CC-FP-HC-R600 | -965.9614 | 3119.585 | 2153.6236 | 15521.1138 | 0.13875 | 1.2241 | 1.0721 | 1.226 | 5.194 | 1335.4629 | 10875 | 3 | 4 | 11756.5001 | 12758.8859 | 12799.8859 | 98789.5002 | 39.9279
83 | C-SOK-NAP-CC-FP-HC-R600 | 200.0068 | 3121.5665 | 3321.5733 | 15582.1617 | 0.21317 | 1.3389 | 1.0713 | 1.3315 | 5.1956 | 6002.6381 | 11600 | 3 | 4 | 10760.8659 | 12813.8119 | 12854.8119 | 103593.8659 | 27.3181
84 | C-SOK-NAP-CC-FP-HC-R600 | 890.2351 | 3115.494 | 4005.7291 | 15586.136 | 0.25701 | 1.4177 | 1.0711 | 1.3963 | 5.1947 | 8753.4305 | 12325 | 3 | 4 | 10146.9481 | 12817.4561 | 12858.4561 | 108779.9481 | 23.9461
85 | C-SOK-NAP-CC-FP-HC-R60 | 172.8381 | 3137.2244 | 3310.0625 | 15570.7395 | 0.21258 | 1.3382 | 1.0715 | 1.3444 | 5.1959 | 5920.0596 | 13125 | 3 | 4 | 10765.5961 | 12803.485 | 12844.485 | 115798.5962 | 31.1034
86 | C-SOK-NAP-CC-FP-HC-R60 | 1562.7259 | 3133.799 | 4696.5249 | 15621.4785 | 0.30065 | 1.5057 | 1.0707 | 1.5132 | 5.1974 | 11473.9021 | 14000 | 3 | 4 | 9562.4557 | 12849.1884 | 12890.1884 | 121595.4557 | 23.1459
87 | C-SOK-NAP-CC-FP-HC-R60 | 2519.4365 | 3129.1638 | 5648.6003 | 15621.9936 | 0.36158 | 1.6493 | 1.0707 | 1.6638 | 5.1967 | 15293.0189 | 14875 | 3 | 4 | 8704.6339 | 12849.6251 | 12890.6251 | 127737.6339 | 20.3319
88 | C-SOK-NAP-CC-FP-HC-R60 | 1000.3551 | 3131.8767 | 4132.2318 | 15605.9816 | 0.26479 | 1.4325 | 1.071 | 1.4368 | 5.197 | 9221.215 | 15375 | 3 | 4 | 10055.7934 | 12835.239 | 12876.239 | 133088.7934 | 29.0914
89 | C-SOK-NAP-CC-FP-HC-R60 | 2659.0938 | 3138.3882 | 5797.4821 | 15648.1567 | 0.37049 | 1.6722 | 1.0704 | 1.6964 | 5.198 | 15867.0224 | 16400 | 3 | 4 | 8596.9364 | 12873.1538 | 12914.1538 | 139829.9364 | 21.8915
90 | C-SOK-NAP-CC-FP-HC-R60 | 3858.9374 | 3137.1055 | 6996.0429 | 15655.5522 | 0.44687 | 1.9028 | 1.0702 | 1.96 | 5.1974 | 20664.2587 | 17425 | 3 | 4 | 7524.4806 | 12879.7875 | 12920.7875 | 146957.4806 | 19.1589
91 | C-SOK-NAP-CC-FP-WC-R100 | -3855.5623 | 3679.0908 | -176.4716 | 27009.3742 | -0.0065337 | 0.97946 | 0.99683 | 1.0365 | 5.0979 | -9290.4313 | 8650 | 3 | 4 | 24047.3077 | 22758.9278 | 22799.9278 | 93280.3078 | -399.3866
92 | C-SOK-NAP-CC-FP-WC-R100 | -3081.9815 | 3672.2415 | 590.2599 | 27088.4353 | 0.02179 | 1.0073 | 0.99628 | 1.0394 | 5.098 | -6207.5237 | 9200 | 3 | 4 | 23426.3851 | 22830.1119 | 22871.1119 | 97059.3851 | 125.6875
93 | C-SOK-NAP-CC-FP-WC-R100 | -2730.666 | 3673.6425 | 942.9765 | 27104.691 | 0.03479 | 1.0208 | 0.99624 | 1.0418 | 5.0991 | -4799.9266 | 9800 | 3 | 4 | 23123.9933 | 22844.7317 | 22885.7317 | 101556.9933 | 83.4287
94 | C-SOK-NAP-CC-FP-WC-R100 | -1278.714 | 3690.9791 | 2412.2652 | 27106.6057 | 0.088992 | 1.0815 | 0.99616 | 1.1527 | 5.098 | 1036.7761 | 12000 | 3 | 4 | 21808.5644 | 22846.4489 | 22887.4489 | 117841.5644 | 39.3631
95 | C-SOK-NAP-CC-FP-WC-R100 | -18.2826 | 3685.8513 | 3667.5687 | 27167.5419 | 0.135 | 1.1386 | 0.99581 | 1.1942 | 5.0991 | 6069.9551 | 12800 | 3 | 4 | 20732.0667 | 22901.2328 | 22942.2328 | 123165.0667 | 27.3268
96 | C-SOK-NAP-CC-FP-WC-R100 | 614.6065 | 3685.0313 | 4299.6379 | 27177.5408 | 0.15821 | 1.17 | 0.99583 | 1.2275 | 5.1005 | 8600.1451 | 13600 | 3 | 4 | 20172.0135 | 22910.2633 | 22951.2633 | 129005.0135 | 24.6657
97 | C-SOK-NAP-CC-FP-WC-R100 | 658.9542 | 3698.6058 | 4357.56 | 27165.9339 | 0.16041 | 1.1732 | 0.9959 | 1.2548 | 5.1002 | 8800.1599 | 15175 | 3 | 4 | 20113.4265 | 22899.7585 | 22940.7585 | 141546.4265 | 27.2184
98 | C-SOK-NAP-CC-FP-WC-R100 | 2382.2976 | 3691.9249 | 6074.2225 | 27221.56 | 0.22314 | 1.2675 | 0.99551 | 1.3494 | 5.1001 | 15682.3987 | 16225 | 3 | 4 | 18616.512 | 22949.8031 | 22990.8031 | 148449.512 | 20.6543
99 | C-SOK-NAP-CC-FP-WC-R100 | 3391.7036 | 3689.4247 | 7081.1283 | 27221.9184 | 0.26013 | 1.3308 | 0.99552 | 1.4375 | 5.1002 | 19715.8555 | 17225 | 3 | 4 | 17709.9285 | 22950.1349 | 22991.1349 | 155542.9285 | 18.719
100 | C-SOK-NAP-CC-FP-WC-R10 | 2231.8231 | 3701.744 | 5933.567 | 27216.3208 | 0.21802 | 1.2592 | 0.99556 | 1.3385 | 5.1004 | 15096.8656 | 18400 | 3 | 4 | 18741.3289 | 22945.1096 | 22986.1096 | 165974.3289 | 24.0982
101 | C-SOK-NAP-CC-FP-WC-R10 | 4287.4616 | 3690.5459 | 7978.0074 | 27264.2139 | 0.29262 | 1.3916 | 0.99524 | 1.4989 | 5.1005 | 23300.756 | 19600 | 3 | 4 | 16941.1798 | 22988.241 | 23029.241 | 173774.1798 | 18.8951
102 | C-SOK-NAP-CC-FP-WC-R10 | 5735.4071 | 3687.8939 | 9423.301 | 27254.8297 | 0.34575 | 1.5047 | 0.99532 | 1.6741 | 5.1007 | 29088.1183 | 20850 | 3 | 4 | 15631.2196 | 22979.7724 | 23020.7724 | 182464.2196 | 16.9201
103 | C-SOK-NAP-CC-FP-WC-R10 | 3544.7061 | 3692.409 | 7237.1152 | 27251.6289 | 0.26557 | 1.3405 | 0.99536 | 1.4172 | 5.1011 | 20332.8397 | 21750 | 3 | 4 | 17597.1615 | 22976.8899 | 23017.8899 | 191630.1615 | 23.2983
104 | C-SOK-NAP-CC-FP-WC-R10 | 6039.1834 | 3681.3005 | 9720.4839 | 27293.6106 | 0.35615 | 1.5287 | 0.99509 | 1.6696 | 5.1011 | 30292.2344 | 23200 | 3 | 4 | 15396.6528 | 23014.6476 | 23055.6476 | 201029.6528 | 18.3092
105 | C-SOK-NAP-CC-FP-WC-R10 | 7811.7365 | 3673.0801 | 11484.8166 | 27286.6081 | 0.4209 | 1.6996 | 0.99507 | 1.9662 | 5.1002 | 37368.7462 | 24650 | 3 | 4 | 13800.1267 | 23008.4099 | 23049.4099 | 211033.1267 | 16.368
106 | C-SOK-NAP-CC-FP-WC-R600 | -5743.0364 | 4089.7107 | -1653.3257 | 20939.3841 | -0.078958 | 0.99007 | 1.0816 | 1.0075 | 5.1389 | -16155.9611 | 8650 | 3 | 4 | 19891.3783 | 17147.6752 | 17188.6752 | 89124.3783 | -43.5097
107 | C-SOK-NAP-CC-FP-WC-R600 | -5072.555 | 4083.4743 | -989.0807 | 21053.3448 | -0.04698 | 1.019 | 1.0802 | 1.0115 | 5.1394 | -13484.4296 | 9200 | 3 | 4 | 19394.209 | 17250.1921 | 17291.1921 | 93027.209 | -76.5721
108 | C-SOK-NAP-CC-FP-WC-R600 | -4765.2923 | 4085.1569 | -680.1354 | 21073.8418 | -0.032274 | 1.0333 | 1.0799 | 1.015 | 5.1395 | -12252.5743 | 9800 | 3 | 4 | 19135.1396 | 17268.6576 | 17309.6576 | 97568.1396 | -118.0037
109 | C-SOK-NAP-CC-FP-WC-R600 | -3424.0984 | 4104.0661 | 679.9677 | 21074.6992 | 0.032265 | 1.102 | 1.0797 | 1.1147 | 5.1373 | -6856.2835 | 12000 | 3 | 4 | 17917.5024 | 17269.4337 | 17310.4337 | 113950.5025 | 142.1245
110 | C-SOK-NAP-CC-FP-WC-R600 | -2299.8223 | 4096.6471 | 1796.8248 | 21164.9626 | 0.084896 | 1.1644 | 1.0787 | 1.1563 | 5.1391 | -2371.5441 | 12800 | 3 | 4 | 16991.3761 | 17350.6769 | 17391.6769 | 119424.3761 | 56.785
111 | C-SOK-NAP-CC-FP-WC-R600 | -1620.6251 | 4097.1044 | 2476.4793 | 21167.7543 | 0.11699 | 1.2067 | 1.0787 | 1.1896 | 5.1395 | 346.0069 | 13600 | 3 | 4 | 16382.3081 | 17353.1328 | 17394.1328 | 125215.3081 | 43.5381
112 | C-SOK-NAP-CC-FP-WC-R600 | -1790.4003 | 4111.3024 | 2320.9021 | 21159.0145 | 0.10969 | 1.1969 | 1.0788 | 1.2048 | 5.1394 | -309.4306 | 15175 | 3 | 4 | 16518.6829 | 17345.2605 | 17386.2605 | 137951.6829 | 51.9477
113 | C-SOK-NAP-CC-FP-WC-R600 | -213.5895 | 4104.9284 | 3891.3389 | 21227.8207 | 0.18331 | 1.3038 | 1.0779 | 1.2994 | 5.1393 | 5987.1894 | 16225 | 3 | 4 | 15165.3646 | 17407.1948 | 17448.1948 | 144998.3646 | 32.778
114 | C-SOK-NAP-CC-FP-WC-R600 | 883.5973 | 4101.6323 | 4985.2297 | 21231.8406 | 0.2348 | 1.3915 | 1.0779 | 1.3812 | 5.1402 | 10370.4433 | 17225 | 3 | 4 | 14183.5261 | 17410.7998 | 17451.7998 | 152016.5261 | 26.9927
115 | C-SOK-NAP-CC-FP-WC-R60 | -464.0028 | 4112.0013 | 3647.9986 | 21223.3108 | 0.17189 | 1.286 | 1.0781 | 1.2858 | 5.1405 | 4997.3244 | 18400 | 3 | 4 | 15382.3814 | 17403.0893 | 17444.0893 | 162615.3814 | 39.7948
116 | C-SOK-NAP-CC-FP-WC-R60 | 1375.9225 | 4103.7466 | 5479.6691 | 21279.5516 | 0.25751 | 1.4334 | 1.0773 | 1.4268 | 5.1404 | 12343.2675 | 19600 | 3 | 4 | 13782.1281 | 17453.7522 | 17494.7522 | 170615.1281 | 27.9434
117 | C-SOK-NAP-CC-FP-WC-R60 | 2920.2688 | 4098.8483 | 7019.1172 | 21285.0232 | 0.32977 | 1.5878 | 1.0773 | 1.59 | 5.1403 | 18512.4892 | 20850 | 3 | 4 | 12400.1746 | 17458.6961 | 17499.6961 | 179233.1746 | 23.0419
118 | C-SOK-NAP-CC-FP-WC-R60 | 607.7485 | 4104.8317 | 4712.5802 | 21268.7784 | 0.22157 | 1.3673 | 1.0774 | 1.3586 | 5.1398 | 9272.3801 | 21750 | 3 | 4 | 14463.0423 | 17443.997 | 17484.997 | 188496.0423 | 36.2882
119 | C-SOK-NAP-CC-FP-WC-R60 | 2905.4268 | 4094.437 | 6999.8639 | 21316.2725 | 0.32838 | 1.584 | 1.0769 | 1.5843 | 5.1406 | 18445.7691 | 23200 | 3 | 4 | 12444.2574 | 17486.7819 | 17527.7819 | 198077.2574 | 25.7933
120 | C-SOK-NAP-CC-FP-WC-R60 | 4722.9727 | 4086.5041 | 8809.4768 | 21327.2769 | 0.41306 | 1.8123 | 1.0768 | 1.8495 | 5.1408 | 25702.7309 | 24650 | 3 | 4 | 10823.2104 | 17496.6732 | 17537.6732 | 208056.2104 | 21.6265
121 | C-SOK-NAP-FC-ET-HC-OFF0 | -5973.525 | 2563.6008 | -3409.9242 | 4503.2058 | -0.75722 | 0.8073 | 1.4792 | 1.1468 | 4.5265 | -19621.4321 | 6613 | 3 | 4 | 6777.6503 | 2939.6383 | 2980.6383 | 59714.6504 | -16.6379
122 | C-SOK-NAP-FC-ET-HC-OFF0 | -5781.664 | 2571.739 | -3209.925 | 4503.9974 | -0.71268 | 0.82814 | 1.4789 | 1.1636 | 4.5254 | -18840.4244 | 6900 | 3 | 4 | 6600.5675 | 2940.1133 | 2981.1133 | 61833.5676 | -18.3345
123 | C-SOK-NAP-FC-ET-HC-OFF0 | -5670.1513 | 2570.5323 | -3099.6191 | 4503.7633 | -0.68823 | 0.84019 | 1.479 | 1.1771 | 4.5258 | -18396.3849 | 7188 | 3 | 4 | 6500.7896 | 2939.9728 | 2980.9728 | 64037.7897 | -19.6982
124 | C-SOK-NAP-FC-ET-HC-OFF0 | -4064.308 | 2660.5003 | -1403.8077 | 4503.562 | -0.31171 | 1.0813 | 1.4789 | 1.5603 | 4.5255 | -11823.065 | 8913 | 3 | 4 | 5001.4291 | 2939.852 | 2980.852 | 76338.4291 | -52.2561
125 | C-SOK-NAP-FC-ET-HC-OFF0 | -3697.7084 | 2662.4978 | -1035.2107 | 4503.2721 | -0.22988 | 1.1533 | 1.479 | 1.6519 | 4.5259 | -10353.3375 | 9300 | 3 | 4 | 4670.117 | 2939.6781 | 2980.6781 | 79103.1171 | -73.5333
126 | C-SOK-NAP-FC-ET-HC-OFF0 | -3506.5271 | 2662.7557 | -843.7714 | 4503.9585 | -0.18734 | 1.1944 | 1.4788 | 1.7096 | 4.525 | -9588.1821 | 9688 | 3 | 4 | 4498.3109 | 2940.0899 | 2981.0899 | 82035.3109 | -93.6915
127 | C-SOK-NAP-FC-ET-HC-OFF0 | -2673.25 | 2751.5176 | 78.2675 | 4502.8259 | 0.017382 | 1.4437 | 1.4792 | 2.1226 | 4.5266 | -6107.1375 | 11500 | 3 | 4 | 3694.4249 | 2939.4104 | 2980.4104 | 95727.4249 | 1184.9996
128 | C-SOK-NAP-FC-ET-HC-OFF0 | -2213.33 | 2753.3849 | 540.055 | 4502.7331 | 0.11994 | 1.6119 | 1.4792 | 2.3708 | 4.5266 | -4264.345 | 12000 | 3 | 4 | 3279.3207 | 2939.3547 | 2980.3547 | 99312.3207 | 178.3744
129 | C-SOK-NAP-FC-ET-HC-OFF0 | -1897.4439 | 2755.6819 | 858.238 | 4503.4077 | 0.19058 | 1.7524 | 1.479 | 2.5786 | 4.5259 | -2996.9724 | 12500 | 3 | 4 | 2994.0498 | 2939.7594 | 2980.7594 | 103027.0498 | 116.5717
130 | C-SOK-NAP-FC-ET-HC-OFF | -2331.2984 | 2768.2292 | 436.9308 | 4503.1888 | 0.097027 | 1.5711 | 1.4792 | 2.3091 | 4.5266 | -4711.4783 | 13800 | 3 | 4 | 3376.8592 | 2939.6281 | 2980.6281 | 113809.8592 | 253.654
131 | C-SOK-NAP-FC-ET-HC-OFF | -1764.8151 | 2773.2717 | 1008.4567 | 4503.2713 | 0.22394 | 1.8277 | 1.479 | 2.7058 | 4.5259 | -2437.1407 | 14400 | 3 | 4 | 2864.0481 | 2939.6776 | 2980.6776 | 118097.0481 | 114.151
132 | C-SOK-NAP-FC-ET-HC-OFF | -1252.18 | 2777.3087 | 1525.1287 | 4503.0795 | 0.33869 | 2.1449 | 1.479 | 3.2293 | 4.5261 | -379.8722 | 15000 | 3 | 4 | 2400.1393 | 2939.5625 | 2980.5625 | 122433.1393 | 78.3229
133 | C-SOK-NAP-FC-ET-HC-OFF | -1581.8706 | 2803.724 | 1221.8534 | 4502.9133 | 0.27135 | 1.9471 | 1.4794 | 2.921 | 4.5272 | -1654.609 | 16388 | 3 | 4 | 2680.9119 | 2939.4628 | 2980.4628 | 133817.912 | 107.0811
134 | C-SOK-NAP-FC-ET-HC-OFF | -842.1252 | 2812.3782 | 1970.2531 | 4502.6868 | 0.43757 | 2.5225 | 1.4793 | 3.9252 | 4.5269 | 1318.7964 | 17100 | 3 | 4 | 2009.8126 | 2939.3269 | 2980.3269 | 138842.8126 | 68.9569
135 | C-SOK-NAP-FC-ET-HC-OFF | -493.9414 | 2816.4498 | 2322.5084 | 4502.6641 | 0.51581 | 2.9297 | 1.4791 | 4.7186 | 4.5264 | 2718.3174 | 17813 | 3 | 4 | 1693.9907 | 2939.3133 | 2980.3133 | 144230.9907 | 60.8182
136 | C-SOK-NAP-FC-ET-HC-R100 | -2798.2455 | 1914.9039 | -883.3415 | 11945.9042 | -0.073945 | 0.90613 | 0.99797 | 0.90997 | 4.6435 | -8001.4753 | 6613 | 3 | 4 | 11269.2713 | 9899.7927 | 9940.7927 | 64206.2713 | -61.432
137 | C-SOK-NAP-FC-ET-HC-R100 | -2472.9231 | 1919.1291 | -553.794 | 11956.549 | -0.046317 | 0.92996 | 0.99785 | 0.91937 | 4.6439 | -6693.1438 | 6900 | 3 | 4 | 10983.4484 | 9909.2951 | 9950.2951 | 66216.4485 | -101.6012
138 | C-SOK-NAP-FC-ET-HC-R100 | -2298.7402 | 1920.9152 | -377.825 | 11957.8086 | -0.031597 | 0.94323 | 0.99785 | 0.93334 | 4.644 | -5993.4354 | 7188 | 3 | 4 | 10826.7204 | 9910.4033 | 9951.4033 | 68363.7205 | -154.6015
139 | C-SOK-NAP-FC-ET-HC-R100 | -1092.5705 | 1984.2022 | 891.6317 | 11961.6876 | 0.074541 | 1.0513 | 0.99774 | 1.092 | 4.6439 | -1063.2784 | 8913 | 3 | 4 | 9706.8135 | 9914.0213 | 9955.0213 | 81043.8135 | 79.7289
140 | C-SOK-NAP-FC-ET-HC-R100 | -550.6232 | 1982.0925 | 1431.4692 | 11966.8787 | 0.11962 | 1.1051 | 0.9977 | 1.139 | 4.6445 | 1100.9945 | 9300 | 3 | 4 | 9224.9995 | 9918.694 | 9959.694 | 83657.9995 | 51.4844
141 | C-SOK-NAP-FC-ET-HC-R100 | -264.5963 | 1979.7471 | 1715.1507 | 11966.0446 | 0.14333 | 1.1357 | 0.99768 | 1.1826 | 4.6442 | 2241.1932 | 9688 | 3 | 4 | 8968.2797 | 9917.9913 | 9958.9913 | 86505.2797 | 44.6295
142 | C-SOK-NAP-FC-ET-HC-R100 | 172.9525 | 2040.2159 | 2213.1684 | 11970.6939 | 0.18488 | 1.1936 | 0.99767 | 1.2499 | 4.6452 | 4092.1698 | 11500 | 3 | 4 | 8542.4707 | 9922.2575 | 9963.2575 | 100575.4708 | 40.9423
143 | C-SOK-NAP-FC-ET-HC-R100 | 986.9951 | 2036.1684 | 3023.1634 | 11974.335 | 0.25247 | 1.3013 | 0.99756 | 1.3765 | 4.6447 | 7341.5943 | 12000 | 3 | 4 | 7815.5645 | 9925.5611 | 9966.5611 | 103848.5645 | 31.0542
144 | C-SOK-NAP-FC-ET-HC-R100 | 1510.8313 | 2033.1828 | 3544.0141 | 11971.7159 | 0.29603 | 1.382 | 0.99767 | 1.4978 | 4.6455 | 9431.9631 | 12500 | 3 | 4 | 7343.5351 | 9923.1929 | 9964.1929 | 107376.5351 | 27.4864
145 | C-SOK-NAP-FC-ET-HC-R10 | 809.2202 | 2041.5676 | 2850.7878 | 11976.0516 | 0.23804 | 1.2767 | 0.99752 | 1.2986 | 4.6444 | 6639.4935 | 13800 | 3 | 4 | 7973.8186 | 9927.0573 | 9968.0573 | 118406.8186 | 38.0382
146 | C-SOK-NAP-FC-ET-HC-R10 | 1857.8135 | 2042.5078 | 3900.3213 | 11981.2174 | 0.32554 | 1.4422 | 0.99749 | 1.5066 | 4.6454 | 10835.4335 | 14400 | 3 | 4 | 7034.2691 | 9931.8059 | 9972.8059 | 122267.2691 | 28.7911
147 | C-SOK-NAP-FC-ET-HC-R10 | 2520.7345 | 2039.6243 | 4560.3589 | 11980.2091 | 0.38066 | 1.5706 | 0.99749 | 1.6901 | 4.6448 | 13482.3121 | 15000 | 3 | 4 | 6438.3831 | 9930.8188 | 9971.8188 | 126471.3831 | 25.5461
148 | C-SOK-NAP-FC-ET-HC-R10 | 1584.6405 | 2061.4098 | 3646.0503 | 11980.9845 | 0.30432 | 1.3982 | 0.99746 | 1.4081 | 4.6448 | 9774.2451 | 16388 | 3 | 4 | 7268.5286 | 9931.5509 | 9972.5509 | 138405.5287 | 35.2252
149 | C-SOK-NAP-FC-ET-HC-R10 | 2840.1355 | 2059.9452 | 4900.0806 | 11987.1171 | 0.40878 | 1.6451 | 0.99737 | 1.7338 | 4.6449 | 14793.7838 | 17100 | 3 | 4 | 6144.9878 | 9937.0768 | 9978.0768 | 142977.9878 | 27.1424
150 | C-SOK-NAP-FC-ET-HC-R10 | 3696.8786 | 2062.9833 | 5759.862 | 11987.4177 | 0.48049 | 1.8722 | 0.99735 | 2.0447 | 4.6446 | 18225.82 | 17813 | 3 | 4 | 5372.3303 | 9937.311 | 9978.311 | 147909.3303 | 23.9469
151 | C-SOK-NAP-FC-ET-HC-R600 | -3413.453 | 2079.6493 | -1333.8037 | 9566.4123 | -0.13943 | 0.91068 | 1.0665 | 0.8974 | 4.6636 | -10187.7298 | 6613 | 3 | 4 | 9532.303 | 7707.9848 | 7748.9848 | 62469.303 | -41.0258
152 | C-SOK-NAP-FC-ET-HC-R600 | -3093.5308 | 2085.5553 | -1007.9755 | 9587.9225 | -0.10513 | 0.93839 | 1.0658 | 0.9075 | 4.6625 | -8898.1977 | 6900 | 3 | 4 | 9260.17 | 7727.3255 | 7768.3255 | 64493.1701 | -56.276
153 | C-SOK-NAP-FC-ET-HC-R600 | -2914.2991 | 2086.4251 | -827.874 | 9589.4653 | -0.086332 | 0.95461 | 1.0658 | 0.92117 | 4.6631 | -8179.8213 | 7188 | 3 | 4 | 9099.8352 | 7728.8211 | 7769.8211 | 66636.8353 | -71.1062
154 | C-SOK-NAP-FC-ET-HC-R600 | -1836.8642 | 2151.5133 | 314.6491 | 9595.5503 | 0.032791 | 1.0721 | 1.0656 | 1.0654 | 4.6639 | -3761.6013 | 8913 | 3 | 4 | 8096.6994 | 7734.4296 | 7775.4296 | 79433.6994 | 227.7403
155 | C-SOK-NAP-FC-ET-HC-R600 | -1319.9741 | 2148.1071 | 828.133 | 9611.1234 | 0.086164 | 1.1343 | 1.0652 | 1.111 | 4.6632 | -1699.7178 | 9300 | 3 | 4 | 7647.459 | 7748.3466 | 7789.3466 | 82080.4591 | 89.7092
156 | C-SOK-NAP-FC-ET-HC-R600 | -964.9655 | 2145.0372 | 1180.0716 | 9609.71 | 0.1228 | 1.1818 | 1.0653 | 1.1555 | 4.6643 | -284.8002 | 9688 | 3 | 4 | 7328.6256 | 7747.1789 | 7788.1789 | 84865.6256 | 65.3159
157 | C-SOK-NAP-FC-ET-HC-R600 | -739.2303 | 2204.9141 | 1465.6838 | 9613.6275 | 0.15246 | 1.223 | 1.0651 | 1.2094 | 4.6639 | 717.9358 | 11500 | 3 | 4 | 7093.0597 | 7750.7009 | 7791.7009 | 99126.0598 | 62.3152
158 | C-SOK-NAP-FC-ET-HC-R600 | 55.2341 | 2202.4018 | 2257.6359 | 9624.136 | 0.23458 | 1.354 | 1.0649 | 1.3338 | 4.6652 | 3891.6059 | 12000 | 3 | 4 | 6389.1597 | 7760.3114 | 7801.3114 | 102422.1597 | 41.9115
159 | C-SOK-NAP-FC-ET-HC-R600 | 593.3889 | 2198.3213 | 2791.7103 | 9625.9497 | 0.29002 | 1.4595 | 1.0648 | 1.4434 | 4.6645 | 6037.4246 | 12500 | 3 | 4 | 5908.8687 | 7761.9115 | 7802.9115 | 105941.8687 | 35.1537
160 | C-SOK-NAP-FC-ET-HC-R60 | -135.3754 | 2210.6796 | 2075.3042 | 9623.8825 | 0.21564 | 1.3212 | 1.0649 | 1.2808 | 4.6641 | 3142.9643 | 13800 | 3 | 4 | 6555.3851 | 7759.955 | 7800.955 | 116988.3852 | 52.6127
161 | C-SOK-NAP-FC-ET-HC-R60 | 765.3881 | 2205.3624 | 2970.7505 | 9631.4651 | 0.30844 | 1.4983 | 1.0647 | 1.4487 | 4.6649 | 6737.1564 | 14400 | 3 | 4 | 5754.875 | 7766.9417 | 7807.9417 | 120987.875 | 38.0981
162 | C-SOK-NAP-FC-ET-HC-R60 | 1424.9339 | 2204.946 | 3629.8799 | 9634.8872 | 0.37674 | 1.6622 | 1.0646 | 1.6266 | 4.6641 | 9374.6456 | 15000 | 3 | 4 | 5164.4774 | 7769.8856 | 7810.8856 | 125197.4774 | 32.339
163 | C-SOK-NAP-FC-ET-HC-R60 | 460.5272 | 2227.7456 | 2688.2728 | 9633.9925 | 0.27904 | 1.4371 | 1.0646 | 1.3627 | 4.6646 | 5555.0182 | 16388 | 3 | 4 | 6017.981 | 7769.1029 | 7810.1029 | 137154.9811 | 48.1145
164 | C-SOK-NAP-FC-ET-HC-R60 | 1643.8442 | 2225.2258 | 3869.0701 | 9639.4124 | 0.40138 | 1.7305 | 1.0645 | 1.6513 | 4.6646 | 10284.0866 | 17100 | 3 | 4 | 4959.511 | 7774.1063 | 7815.1063 | 141792.511 | 34.6278
165 | C-SOK-NAP-FC-ET-HC-R60 | 2458.4546 | 2228.8866 | 4687.3412 | 9647.2305 | 0.48587 | 2.0147 | 1.0643 | 1.9679 | 4.6652 | 13548.6295 | 17813 | 3 | 4 | 4231.1287 | 7781.0698 | 7822.0698 | 146768.1287 | 29.6428
166 | C-SOK-NAP-FC-ET-WC-OFF0 | -9798.6493 | 4090.4938 | -5708.1555 | 7119.7135 | -0.80174 | 0.78648 | 1.4547 | 1.0958 | 4.4364 | -32377.1075 | 10350 | 3 | 4 | 11042.8061 | 4648.1817 | 4689.1817 | 93875.8061 | -15.6244
167 | C-SOK-NAP-FC-ET-WC-OFF0 | -9533.1269 | 4090.1161 | -5443.0109 | 7119.798 | -0.76449 | 0.80298 | 1.4545 | 1.108 | 4.4357 | -31315.6476 | 10800 | 3 | 4 | 10804.1138 | 4648.2324 | 4689.2324 | 97237.1139 | -17.0031
168 | C-SOK-NAP-FC-ET-WC-OFF0 | -9434.549 | 4089.569 | -5344.98 | 7119.9094 | -0.75071 | 0.80926 | 1.4545 | 1.1137 | 4.4355 | -30922.2478 | 11250 | 3 | 4 | 10715.7902 | 4648.2992 | 4689.2992 | 100748.7902 | -17.9719
169 | C-SOK-NAP-FC-ET-WC-OFF0 | -7273.5153 | 4119.7916 | -3153.7237 | 7120.2102 | -0.44293 | 0.98273 | 1.4557 | 1.3876 | 4.4397 | -22227.7418 | 14075 | 3 | 4 | 8752.9842 | 4648.4797 | 4689.4797 | 121385.9843 | -37.0028
170 | C-SOK-NAP-FC-ET-WC-OFF0 | -6836.366 | 4120.1401 | -2716.2259 | 7120.3376 | -0.38147 | 1.0264 | 1.4557 | 1.4366 | 4.4396 | -20478.5638 | 14725 | 3 | 4 | 8359.4205 | 4648.5562 | 4689.5562 | 126192.4205 | -44.7322
171 | C-SOK-NAP-FC-ET-WC-OFF0 | -6618.9356 | 4117.8096 | -2501.126 | 7120.1109 | -0.35128 | 1.0494 | 1.4558 | 1.4652 | 4.4399 | -19612.7265 | 15325 | 3 | 4 | 8164.998 | 4648.4202 | 4689.4202 | 130797.998 | -50.4207
172 | C-SOK-NAP-FC-ET-WC-OFF0 | -5401.4777 | 4149.6451 | -1251.8326 | 7119.283 | -0.17584 | 1.2068 | 1.4567 | 1.7244 | 4.4432 | -14689.8358 | 17850 | 3 | 4 | 7049.6554 | 4647.9234 | 4688.9234 | 149882.6555 | -115.9849
173 | C-SOK-NAP-FC-ET-WC-OFF0 | -4786.044 | 4146.3793 | -639.6646 | 7120.5837 | -0.089833 | 1.3018 | 1.4564 | 1.8568 | 4.4422 | -12233.5436 | 18600 | 3 | 4 | 6498.5112 | 4648.7038 | 4689.7038 | 155331.5112 | -235.5012
174 | C-SOK-NAP-FC-ET-WC-OFF0 | -4407.7239 | 4145.0281 | -262.6958 | 7119.4075 | -0.036899 | 1.3683 | 1.4565 | 1.9423 | 4.4426 | -10722.5155 | 19400 | 3 | 4 | 6158.1237 | 4647.9981 | 4688.9981 | 161391.1237 | -596.5154
175 | C-SOK-NAP-FC-ET-WC-OFF | -4131.5692 | 4173.4198 | 41.8506 | 7119.644 | 0.0058782 | 1.4275 | 1.4568 | 2.0677 | 4.4435 | -9570.577 | 21850 | 3 | 4 | 5892.6368 | 4648.14 | 4689.14 | 180725.6369 | 4206.3058
176 | C-SOK-NAP-FC-ET-WC-OFF | -3119.4529 | 4168.1203 | 1048.6673 | 7119.9845 | 0.14729 | 1.6648 | 1.4573 | 2.4328 | 4.4451 | -5530.9447 | 22800 | 3 | 4 | 4985.1548 | 4648.3443 | 4689.3443 | 187418.1548 | 174.2486
177 | C-SOK-NAP-FC-ET-WC-OFF | -2661.8626 | 4164.5625 | 1502.6999 | 7120.1584 | 0.21105 | 1.799 | 1.457 | 2.6515 | 4.4442 | -3706.5129 | 23750 | 3 | 4 | 4575.5661 | 4648.4487 | 4689.4487 | 194608.5661 | 126.3853
178 | C-SOK-NAP-FC-ET-WC-OFF | -3233.3445 | 4191.9362 | 958.5917 | 7119.7151 | 0.13464 | 1.6404 | 1.4572 | 2.4112 | 4.4449 | -5946.8176 | 25575 | 3 | 4 | 5073.1194 | 4648.1827 | 4689.1827 | 209706.1194 | 213.873
179 | C-SOK-NAP-FC-ET-WC-OFF | -2063.3629 | 4184.2148 | 2120.8519 | 7119.47 | 0.29789 | 2.0222 | 1.4575 | 3.0468 | 4.4459 | -1279.7602 | 26725 | 3 | 4 | 4024.6732 | 4648.0356 | 4689.0356 | 217857.6732 | 100.5109
180 | C-SOK-NAP-FC-ET-WC-OFF | -1467.0942 | 4183.0873 | 2715.9931 | 7120.4247 | 0.38144 | 2.2944 | 1.457 | 3.5603 | 4.444 | 1103.4354 | 27825 | 3 | 4 | 3489.2756 | 4648.6084 | 4689.6084 | 226122.2756 | 81.5292
181 | C-SOK-NAP-FC-ET-WC-R100 | -5403.929 | 2848.5822 | -2555.3467 | 18503.5735 | -0.1381 | 0.86221 | 0.9973 | 0.80859 | 4.5678 | -16868.0788 | 10350 | 3 | 4 | 18514.7277 | 15338.012 | 15379.012 | 101347.7278 | -33.6427
182 | C-SOK-NAP-FC-ET-WC-R100 | -4833.3659 | 2846.1673 | -1987.1986 | 18540.0727 | -0.10718 | 0.886 | 0.99695 | 0.81793 | 4.5682 | -14589.8515 | 10800 | 3 | 4 | 18035.5659 | 15370.9071 | 15411.9071 | 104468.566 | -44.8152
183 | C-SOK-NAP-FC-ET-WC-R100 | -4646.5323 | 2846.7378 | -1799.7945 | 18546.1462 | -0.097044 | 0.89411 | 0.99686 | 0.82142 | 4.5677 | -13841.5663 | 11250 | 3 | 4 | 17872.4289 | 15376.2508 | 15417.2508 | 107905.4289 | -51.3882
184 | C-SOK-NAP-FC-ET-WC-R100 | -3345.312 | 2869.6228 | -475.6892 | 18553.6771 | -0.025639 | 0.95644 | 0.99693 | 0.89381 | 4.5696 | -8598.5433 | 14075 | 3 | 4 | 16694.4156 | 15383.048 | 15424.048 | 129327.4156 | -239.4491
185 | C-SOK-NAP-FC-ET-WC-R100 | -2537.1898 | 2867.2764 | 330.0866 | 18578.6301 | 0.017767 | 0.99848 | 0.99669 | 0.91451 | 4.5696 | -5369.9651 | 14725 | 3 | 4 | 15990.9426 | 15405.4724 | 15446.4724 | 133823.9426 | 358.6254
186 | C-SOK-NAP-FC-ET-WC-R100 | -2167.1867 | 2866.3802 | 699.1935 | 18576.8265 | 0.037638 | 1.0192 | 0.99675 | 0.93375 | 4.5702 | -3891.4466 | 15325 | 3 | 4 | 15656.9268 | 15403.9123 | 15444.9123 | 138289.9268 | 175.6953
187 | C-SOK-NAP-FC-ET-WC-R100 | -1470.8208 | 2895.6713 | 1424.8505 | 18589.1768 | 0.076649 | 1.062 | 0.99654 | 0.98544 | 4.5694 | -1057.1644 | 17850 | 3 | 4 | 15023.7474 | 15415.1156 | 15456.1156 | 157856.7475 | 99.9408
188 | C-SOK-NAP-FC-ET-WC-R100 | -417.709 | 2895.0483 | 2477.3393 | 18606.8066 | 0.13314 | 1.1311 | 0.9964 | 1.0394 | 4.5697 | 3154.2444 | 18600 | 3 | 4 | 14092.0751 | 15430.8607 | 15471.8607 | 162925.0751 | 59.5208
189 | C-SOK-NAP-FC-ET-WC-R100 | 311.5696 | 2897.9291 | 3209.4987 | 18598.3422 | 0.17257 | 1.1851 | 0.9965 | 1.0936 | 4.5698 | 6076.1602 | 19400 | 3 | 4 | 13426.3392 | 15423.2144 | 15464.2144 | 168659.3392 | 47.7318
190 | C-SOK-NAP-FC-ET-WC-R10 | -40.8705 | 2913.7793 | 2872.9088 | 18612.0099 | 0.15436 | 1.1595 | 0.99644 | 1.0683 | 4.571 | 4692.8168 | 21850 | 3 | 4 | 13746.4611 | 15435.651 | 15476.651 | 188579.4612 | 60.2535
191 | C-SOK-NAP-FC-ET-WC-R10 | 1401.8146 | 2914.5134 | 4316.328 | 18631.8197 | 0.23166 | 1.276 | 0.99625 | 1.1721 | 4.571 | 10464.7808 | 22800 | 3 | 4 | 12465.349 | 15453.39 | 15494.39 | 194898.349 | 41.564
192 | C-SOK-NAP-FC-ET-WC-R10 | 2415.7096 | 2917.1601 | 5332.8697 | 18627.3227 | 0.28629 | 1.3736 | 0.99623 | 1.2724 | 4.5702 | 14524.7718 | 23750 | 3 | 4 | 11547.1964 | 15449.3424 | 15490.3424 | 201580.1964 | 34.8949
193 | C-SOK-NAP-FC-ET-WC-R10 | 1047.8784 | 2923.7686 | 3971.647 | 18631.5329 | 0.21317 | 1.2459 | 0.99617 | 1.1365 | 4.5699 | 9064.4611 | 25575 | 3 | 4 | 12778.0347 | 15453.0927 | 15494.0927 | 217411.0347 | 50.8396
194 | C-SOK-NAP-FC-ET-WC-R10 | 2871.2328 | 2925.9297 | 5797.1624 | 18651.3076 | 0.31082 | 1.4222 | 0.99605 | 1.3029 | 4.571 | 16361.4805 | 26725 | 3 | 4 | 11153.5997 | 15470.9737 | 15511.9737 | 224986.5997 | 36.134
195 | C-SOK-NAP-FC-ET-WC-R10 | 4118.805 | 2926.3133 | 7045.1183 | 18649.5923 | 0.37776 | 1.5752 | 0.99606 | 1.4574 | 4.5706 | 21352.4088 | 27825 | 3 | 4 | 10028.885 | 15469.2818 | 15510.2818 | 232661.885 | 30.823
196 | C-SOK-NAP-FC-ET-WC-R600 | -6669.2614 | 3080.6361 | -3588.6253 | 14671.4073 | -0.2446 | 0.843 | 1.068 | 0.7945 | 4.5888 | -21542.6522 | 10350 | 3 | 4 | 15979.8925 | 11801.7261 | 11842.7261 | 98812.8926 | -24.235
197 | C-SOK-NAP-FC-ET-WC-R600 | -6151.6433 | 3078.8248 | -3072.8185 | 14727.0389 | -0.20865 | 0.86737 | 1.0671 | 0.80337 | 4.5893 | -19475.1985 | 10800 | 3 | 4 | 15565.1395 | 11851.7391 | 11892.7391 | 101998.1396 | -29.3234
198 | C-SOK-NAP-FC-ET-WC-R600 | -5918.0355 | 3076.9887 | -2841.0468 | 14731.3848 | -0.19286 | 0.87878 | 1.067 | 0.80892 | 4.5893 | -18543.8275 | 11250 | 3 | 4 | 15360.0447 | 11855.7754 | 11896.7754 | 105393.0447 | -32.9091
199 | C-SOK-NAP-FC-ET-WC-R600 | -4981.7715 | 3097.3958 | -1884.3757 | 14745.9061 | -0.12779 | 0.9292 | 1.0666 | 0.86191 | 4.5884 | -14764.7596 | 14075 | 3 | 4 | 14518.1569 | 11868.7546 | 11909.7546 | 127151.1569 | -61.1563
200 | C-SOK-NAP-FC-ET-WC-R600 | -4098.5646 | 3097.8501 | -1000.7145 | 14790.1703 | -0.067661 | 0.98105 | 1.0661 | 0.89496 | 4.5903 | -11231.1748 | 14725 | 3 | 4 | 13762.8471 | 11908.5984 | 11949.5984 | 131595.8471 | -119.5608
201 | C-SOK-NAP-FC-ET-WC-R600 | -3667.3828 | 3097.5974 | -569.7853 | 14787.8306 | -0.038531 | 1.0087 | 1.0662 | 0.91291 | 4.5911 | -9506.8687 | 15325 | 3 | 4 | 13372.7733 | 11906.4268 | 11947.4268 | 136005.7733 | -217.7282
202 | C-SOK-NAP-FC-ET-WC-R600 | -3195.7321 | 3126.1713 | -69.5607 | 14795.3588 | -0.0047015 | 1.0425 | 1.066 | 0.96151 | 4.5907 | -7572.6426 | 17850 | 3 | 4 | 12938.0263 | 11913.3868 | 11954.3868 | 155771.0264 | -2067.4984
203 | C-SOK-NAP-FC-ET-WC-R600 | -2202.4745 | 3127.1281 | 924.6536 | 14824.1679 | 0.062375 | 1.1166 | 1.0655 | 1.0127 | 4.5908 | -3598.0179 | 18600 | 3 | 4 | 12069.4578 | 11939.3277 | 11980.3277 | 160902.4578 | 161.0572
204 | C-SOK-NAP-FC-ET-WC-R600 | -1480.5186 | 3128.3834 | 1647.8648 | 14828.7891 | 0.11113 | 1.1778 | 1.0655 | 1.0602 | 4.5908 | -708.102 | 19400 | 3 | 4 | 11422.9491 | 11943.3094 | 11984.3094 | 166655.9491 | 93.8618
205 | C-SOK-NAP-FC-ET-WC-R60 | -1936.3638 | 3145.053 | 1208.6892 | 14828.408 | 0.081512 | 1.1399 | 1.0656 | 1.0405 | 4.592 | -2503.7002 | 21850 | 3 | 4 | 11822.9479 | 11943.0749 | 11984.0749 | 186655.9481 | 144.5135
206 | C-SOK-NAP-FC-ET-WC-R60 | -529.3958 | 3147.2779 | 2617.8821 | 14845.1393 | 0.17635 | 1.2708 | 1.0652 | 1.1437 | 4.5916 | 3127.88 | 22800 | 3 | 4 | 10570.5051 | 11958.2376 | 11999.2376 | 193003.5051 | 69.1415
207 | C-SOK-NAP-FC-ET-WC-R60 | 395.5431 | 3146.4232 | 3541.9664 | 14857.7681 | 0.23839 | 1.374 | 1.065 | 1.234 | 4.5916 | 6826.2113 | 23750 | 3 | 4 | 9749.863 | 11969.5165 | 12010.5165 | 199782.863 | 53.0136
208 | C-SOK-NAP-FC-ET-WC-R60 | -957.196 | 3155.5766 | 2198.3806 | 14852.1286 | 0.14802 | 1.2284 | 1.0651 | 1.1075 | 4.5914 | 1430.5102 | 25575 | 3 | 4 | 10956.7076 | 11964.4109 | 12005.4109 | 215589.7076 | 92.6065
209 | C-SOK-NAP-FC-ET-WC-R60 | 732.2527 | 3157.1965 | 3889.4492 | 14868.5361 | 0.26159 | 1.4171 | 1.0649 | 1.258 | 4.5924 | 8191.005 | 26725 | 3 | 4 | 9450.0578 | 11979.2198 | 12020.2198 | 223283.0578 | 54.3169
210 | C-SOK-NAP-FC-ET-WC-R60 | 1853.5425 | 3156.0738 | 5009.6163 | 14888.5172 | 0.33648 | 1.5765 | 1.0645 | 1.404 | 4.5922 | 12674.2931 | 27825 | 3 | 4 | 8459.631 | 11997.2676 | 12038.2676 | 231092.631 | 43.7268
211 | C-SOK-NAP-FC-FP-HC-OFF0 | -7797.3481 | 2560.133 | -5237.2151 | 4503.4718 | -1.1629 | 0.65586 | 1.4792 | 0.91659 | 4.5264 | -26922.5041 | 4313 | 3 | 4 | 8421.3314 | 2939.7979 | 2980.7979 | 42958.3314 | -7.6334
212 | C-SOK-NAP-FC-FP-HC-OFF0 | -7680.2598 | 2566.3129 | -5113.9469 | 4504.3656 | -1.1353 | 0.66419 | 1.4788 | 0.91797 | 4.5251 | -26443.851 | 4600 | 3 | 4 | 8312.7803 | 2940.3342 | 2981.3342 | 45145.7803 | -8.245
213 | C-SOK-NAP-FC-FP-HC-OFF0 | -7631.3143 | 2567.977 | -5063.3372 | 4504.5966 | -1.124 | 0.66769 | 1.4787 | 0.91801 | 4.5249 | -26245.2953 | 4888 | 3 | 4 | 8267.8694 | 2940.4728 | 2981.4728 | 47404.8695 | -8.7735
214 | C-SOK-NAP-FC-FP-HC-OFF0 | -6285.2911 | 2627.5773 | -3657.7138 | 4503.8019 | -0.81214 | 0.78264 | 1.4788 | 1.0969 | 4.5252 | -20761.8689 | 5813 | 3 | 4 | 7020.2116 | 2939.996 | 2980.996 | 53557.2116 | -13.8273
215 | C-SOK-NAP-FC-FP-HC-OFF0 | -6016.709 | 2631.6259 | -3385.0831 | 4504.483 | -0.75149 | 0.80973 | 1.4788 | 1.1245 | 4.525 | -19680.7929 | 6200 | 3 | 4 | 6776.4672 | 2940.4046 | 2981.4046 | 56409.4673 | -15.7834
216 | C-SOK-NAP-FC-FP-HC-OFF0 | -5841.8418 | 2634.5388 | -3207.303 | 4504.4329 | -0.71203 | 0.82842 | 1.4788 | 1.1468 | 4.5252 | -18976.4691 | 6588 | 3 | 4 | 6617.3088 | 2940.3745 | 2981.3745 | 59354.3088 | -17.5764
217 | C-SOK-NAP-FC-FP-HC-OFF0 | -5088.5869 | 2695.3053 | -2393.2816 | 4503.7352 | -0.5314 | 0.92617 | 1.4789 | 1.3024 | 4.5255 | -15862.1722 | 7500 | 3 | 4 | 5902.501 | 2939.9559 | 2980.9559 | 65935.5011 | -26.3047
218 | C-SOK-NAP-FC-FP-HC-OFF0 | -4596.4735 | 2701.2903 | -1895.1832 | 4503.4418 | -0.42083 | 0.99828 | 1.479 | 1.395 | 4.5257 | -13883.7436 | 8000 | 3 | 4 | 5455.8319 | 2939.7799 | 2980.7799 | 69488.8319 | -35.0932
219 | C-SOK-NAP-FC-FP-HC-OFF0 | -4349.9103 | 2706.0357 | -1643.8746 | 4504.0758 | -0.36497 | 1.039 | 1.4788 | 1.4535 | 4.5251 | -12889.5816 | 8500 | 3 | 4 | 5231.4581 | 2940.1603 | 2981.1603 | 73264.4581 | -42.7547
220 | C-SOK-NAP-FC-FP-HC-OFF | -4655.9749 | 2703.6839 | -1952.291 | 4503.5779 | -0.4335 | 0.98949 | 1.479 | 1.3896 | 4.5259 | -14117.7599 | 9000 | 3 | 4 | 5508.0286 | 2939.8615 | 2980.8615 | 77541.0287 | -38.1911
221 | C-SOK-NAP-FC-FP-HC-OFF | -3931.2457 | 2715.7934 | -1215.4523 | 4503.5605 | -0.26989 | 1.1169 | 1.4789 | 1.5652 | 4.5255 | -11198.6603 | 9600 | 3 | 4 | 4848.4962 | 2939.8511 | 2980.8511 | 81681.4962 | -64.7501
222 | C-SOK-NAP-FC-FP-HC-OFF | -3474.0061 | 2720.305 | -753.7011 | 4503.1227 | -0.16737 | 1.2153 | 1.4793 | 1.7089 | 4.5268 | -9362.1827 | 10200 | 3 | 4 | 4434.0109 | 2939.5884 | 2980.5884 | 86067.0109 | -110.2379
223 | C-SOK-NAP-FC-FP-HC-OFF | -3815.2317 | 2739.6038 | -1075.6279 | 4502.807 | -0.23888 | 1.1452 | 1.4793 | 1.6179 | 4.527 | -10694.9204 | 10688 | 3 | 4 | 4729.3453 | 2939.399 | 2980.399 | 90266.3453 | -81.1488
224 | C-SOK-NAP-FC-FP-HC-OFF | -3010.6417 | 2754.0148 | -256.627 | 4503.0354 | -0.05699 | 1.342 | 1.4791 | 1.8973 | 4.5263 | -7452.5423 | 11400 | 3 | 4 | 3996.7048 | 2939.5361 | 2980.5361 | 95229.7048 | -359.468
225 | C-SOK-NAP-FC-FP-HC-OFF | -2548.6381 | 2754.3901 | 205.752 | 4503.1122 | 0.045691 | 1.4863 | 1.479 | 2.1039 | 4.5259 | -5603.9021 | 12113 | 3 | 4 | 3580.7223 | 2939.5821 | 2980.5821 | 100517.7223 | 474.0519
226 | C-SOK-NAP-FC-FP-HC-R100 | -3661.8527 | 1892.3917 | -1769.461 | 11939.5011 | -0.1482 | 0.84766 | 0.99814 | 0.82659 | 4.644 | -11493.4247 | 4313 | 3 | 4 | 12054.1636 | 9893.9312 | 9934.9312 | 46591.1636 | -20.716
227 | C-SOK-NAP-FC-FP-HC-R100 | -3318.265 | 1900.557 | -1417.7079 | 11948.7143 | -0.11865 | 0.86994 | 0.99799 | 0.82691 | 4.644 | -10105.4648 | 4600 | 3 | 4 | 11748.3198 | 9902.2156 | 9943.2156 | 48581.3199 | -27.2539
228 | C-SOK-NAP-FC-FP-HC-R100 | -3141.5571 | 1901.4165 | -1240.1406 | 11950.1144 | -0.10378 | 0.88164 | 0.99796 | 0.83245 | 4.644 | -9397.2009 | 4888 | 3 | 4 | 11590.047 | 9903.4955 | 9944.4955 | 50727.0471 | -32.8854
229 | C-SOK-NAP-FC-FP-HC-R100 | -2259.4111 | 1943.2053 | -316.2057 | 11954.611 | -0.026451 | 0.948 | 0.99789 | 0.9366 | 4.644 | -5798.9687 | 5813 | 3 | 4 | 10775.0676 | 9907.5209 | 9948.5209 | 57312.0677 | -149.7871
230 | C-SOK-NAP-FC-FP-HC-R100 | -1750.7127 | 1946.194 | 195.4813 | 11960.4343 | 0.016344 | 0.9891 | 0.99774 | 0.9573 | 4.6434 | -3759.1942 | 6200 | 3 | 4 | 10320.7585 | 9912.8334 | 9953.8334 | 59953.7585 | 255.7786
231 | C-SOK-NAP-FC-FP-HC-R100 | -1456.9329 | 1947.6369 | 490.7041 | 11961.6196 | 0.041023 | 1.0145 | 0.99772 | 0.97926 | 4.6434 | -2581.6699 | 6588 | 3 | 4 | 10056.5418 | 9913.8844 | 9954.8844 | 62793.5418 | 107.6793
232 | C-SOK-NAP-FC-FP-HC-R100 | -1120.3205 | 1987.7319 | 867.4114 | 11963.2186 | 0.072507 | 1.0491 | 0.99781 | 1.0381 | 4.6454 | -1168.3956 | 7500 | 3 | 4 | 9731.1362 | 9915.4869 | 9956.4869 | 69764.1363 | 68.9496
233 | C-SOK-NAP-FC-FP-HC-R100 | -377.8459 | 1991.5788 | 1613.7329 | 11969.0405 | 0.13483 | 1.1246 | 0.99771 | 1.1013 | 4.6455 | 1807.9146 | 8000 | 3 | 4 | 9065.8997 | 9920.7857 | 9961.7857 | 73098.8997 | 39.1249
234 | C-SOK-NAP-FC-FP-HC-R100 | 88.0075 | 1992.9922 | 2080.9997 | 11968.5508 | 0.17387 | 1.1777 | 0.99771 | 1.1594 | 4.6451 | 3673.6835 | 8500 | 3 | 4 | 8645.2646 | 9920.2666 | 9961.2666 | 76678.2646 | 32.0601
235 | C-SOK-NAP-FC-FP-HC-R10 | -492.7951 | 1995.7751 | 1502.98 | 11969.5738 | 0.12557 | 1.1126 | 0.99765 | 1.0841 | 4.6448 | 1355.1113 | 9000 | 3 | 4 | 9167.3008 | 9921.2502 | 9962.2502 | 81200.3009 | 47.3979
236 | C-SOK-NAP-FC-FP-HC-R10 | 539.2138 | 1998.6123 | 2537.8261 | 11975.089 | 0.21193 | 1.2343 | 0.99752 | 1.2088 | 4.644 | 5487.8757 | 9600 | 3 | 4 | 8241.6592 | 9926.119 | 9967.119 | 85074.6592 | 29.5952
237 | C-SOK-NAP-FC-FP-HC-R10 | 1114.1338 | 2002.5398 | 3116.6736 | 11972.8991 | 0.26031 | 1.3152 | 0.99764 | 1.3 | 4.6452 | 7794.1015 | 10200 | 3 | 4 | 7719.9609 | 9924.2051 | 9965.2051 | 89352.9609 | 25.472
238 | C-SOK-NAP-FC-FP-HC-R10 | 255.8467 | 2013.6136 | 2269.4603 | 11975.543 | 0.18951 | 1.2003 | 0.9976 | 1.1633 | 4.6452 | 4379.4095 | 10688 | 3 | 4 | 8488.1302 | 9926.5604 | 9967.5604 | 94025.1303 | 37.0386
239 | C-SOK-NAP-FC-FP-HC-R10 | 1453.601 | 2017.5046 | 3471.1056 | 11979.4351 | 0.28976 | 1.3696 | 0.99752 | 1.3462 | 4.6455 | 9176.9117 | 11400 | 3 | 4 | 7411.505 | 9930.2487 | 9971.2487 | 98644.505 | 25.5461
240 | C-SOK-NAP-FC-FP-HC-R10 | 2224.027 | 2021.6316 | 4245.6586 | 11979.8458 | 0.3544 | 1.5067 | 0.99745 | 1.5049 | 4.6442 | 12265.4941 | 12113 | 3 | 4 | 6715.8503 | 9930.4536 | 9971.4536 | 103652.8503 | 22.0652
241 | C-SOK-NAP-FC-FP-HC-R600 | -4279.3039 | 2056.3343 | -2222.9696 | 9548.6276 | -0.23281 | 0.84197 | 1.0669 | 0.82117 | 4.6627 | -13689.9919 | 4313 | 3 | 4 | 10309.5599 | 7691.987 | 7732.987 | 44846.56 | -16.6955
242 | C-SOK-NAP-FC-FP-HC-R600 | -3962.7917 | 2064.7777 | -1898.0139 | 9570.8175 | -0.19831 | 0.86577 | 1.0663 | 0.82262 | 4.663 | -12409.8704 | 4600 | 3 | 4 | 10039.6726 | 7712.0268 | 7753.0268 | 46872.6727 | -20.6108
243 | C-SOK-NAP-FC-FP-HC-R600 | -3802.3748 | 2068.2905 | -1734.0843 | 9575.8631 | -0.18109 | 0.87828 | 1.0661 | 0.82718 | 4.6629 | -11762.3484 | 4888 | 3 | 4 | 9897.7354 | 7716.5724 | 7757.5724 | 49034.7355 | -23.8034
244 | C-SOK-NAP-FC-FP-HC-R600 | -2976.9377 | 2107.7135 | -869.2242 | 9580.8496 | -0.090725 | 0.95097 | 1.066 | 0.92523 | 4.6634 | -8394.8951 | 5813 | 3 | 4 | 9135.7439 | 7721.128 | 7762.128 | 55672.7439 | -55.1188
245 | C-SOK-NAP-FC-FP-HC-R600 | -2525.8981 | 2111.7961 | -414.1019 | 9597.0332 | -0.043149 | 0.99399 | 1.0656 | 0.94582 | 4.6636 | -6583.9321 | 6200 | 3 | 4 | 8741.9601 | 7735.7295 | 7776.7295 | 58374.9602 | -122.1879
246 | C-SOK-NAP-FC-FP-HC-R600 | -2222.5137 | 2111.8355 | -110.6782 | 9598.0518 | -0.011531 | 1.025 | 1.0656 | 0.96876 | 4.6633 | -5370.3288 | 6588 | 3 | 4 | 8469.6307 | 7736.4697 | 7777.4697 | 61206.6307 | -482.7434
247 | C-SOK-NAP-FC-FP-HC-R600 | -1984.5156 | 2152.7522 | 168.2367 | 9600.3704 | 0.017524 | 1.0553 | 1.0655 | 1.0204 | 4.6642 | -4350.1419 | 7500 | 3 | 4 | 8233.2187 | 7738.806 | 7779.806 | 68266.2188 | 359.5317
248 | C-SOK-NAP-FC-FP-HC-R600 | -1301.7135 | 2156.4442 | 854.7308 | 9613.6521 | 0.088908 | 1.1377 | 1.0651 | 1.082 | 4.6641 | -1612.7801 | 8000 | 3 | 4 | 7628.4383 | 7750.7628 | 7791.7628 | 71661.4383 | 74.7249
249 | C-SOK-NAP-FC-FP-HC-R600 | -845.3506 | 2158.612 | 1313.2613 | 9613.0532 | 0.13661 | 1.2006 | 1.0652 | 1.1344 | 4.6643 | 216.2841 | 8500 | 3 | 4 | 7215.8208 | 7750.1725 | 7791.1725 | 75248.8208 | 51.3665
250 | C-SOK-NAP-FC-FP-HC-R60 | -1472.713 | 2160.9881 | 688.2751 | 9612.1356 | 0.071605 | 1.1165 | 1.0652 | 1.067 | 4.6644 | -2289.2053 | 9000 | 3 | 4 | 7778.2523 | 7749.4034 | 7790.4034 | 79811.2524 | 104.6396
251 | C-SOK-NAP-FC-FP-HC-R60 | -557.5016 | 2165.2705 | 1607.7689 | 9622.8844 | 0.16708 | 1.2442 | 1.0649 | 1.1756 | 4.6647 | 1378.7777 | 9600 | 3 | 4 | 6961.7934 | 7759.2043 | 7800.2043 | 83794.7934 | 47.2671
252 | C-SOK-NAP-FC-FP-HC-R60 | 35.0503 | 2166.9705 | 2202.0208 | 9623.847 | 0.22881 | 1.3437 | 1.0649 | 1.2627 | 4.6639 | 3751.8188 | 10200 | 3 | 4 | 6428.1806 | 7759.9082 | 7800.9082 | 88061.1806 | 36.4485
253 | C-SOK-NAP-FC-FP-HC-R60 | -854.3379 | 2176.8907 | 1322.5528 | 9621.7987 | 0.13745 | 1.2016 | 1.065 | 1.1388 | 4.665 | 210.7994 | 10688 | 3 | 4 | 7220.8621 | 7758.0924 | 7799.0924 | 92757.8622 | 64.2385
254 | C-SOK-NAP-FC-FP-HC-R60 | 222.2976 | 2185.5181 | 2407.8157 | 9630.2947 | 0.25003 | 1.3815 | 1.0647 | 1.3026 | 4.6642 | 4531.7207 | 11400 | 3 | 4 | 6254.3922 | 7765.7709 | 7806.7709 | 97487.3922 | 37.2456
255 | C-SOK-NAP-FC-FP-HC-R60 | 931.0805 | 2184.1732 | 3115.2537 | 9633.3993 | 0.32338 | 1.5312 | 1.0646 | 1.4423 | 4.664 | 7364.6107 | 12113 | 3 | 4 | 5620.0598 | 7768.5362 | 7809.5362 | 102557.0598 | 30.4141
256 | C-SOK-NAP-FC-FP-WC-OFF0 | -11809.3532 | 4116.6975 | -7692.6557 | 7120.1491 | -1.0804 | 0.681 | 1.4544 | 0.93854 | 4.4354 | -40376.2502 | 6750 | 3 | 4 | 12836.9127 | 4648.4431 | 4689.4431 | 66869.9128 | -8.0831
257 | C-SOK-NAP-FC-FP-WC-OFF0 | -11625.8174 | 4120.548 | -7505.2694 | 7120.0927 | -1.0541 | 0.68962 | 1.4542 | 0.94061 | 4.4346 | -39635.6897 | 7200 | 3 | 4 | 12669.3841 | 4648.4093 | 4689.4093 | 70302.3842 | -8.7423
258 | C-SOK-NAP-FC-FP-WC-OFF0 | -11536.1976 | 4118.7055 | -7417.4921 | 7119.2184 | -1.0419 | 0.69387 | 1.4545 | 0.94366 | 4.4357 | -39280.2813 | 7650 | 3 | 4 | 12589.3103 | 4647.8847 | 4688.8847 | 73822.3103 | -9.3203
259 | C-SOK-NAP-FC-FP-WC-OFF0 | -9868.7117 | 4137.0672 | -5731.6445 | 7120.1552 | -0.80499 | 0.78525 | 1.4551 | 1.0854 | 4.4375 | -32579.735 | 9175 | 3 | 4 | 11078.1639 | 4648.4467 | 4689.4467 | 84511.164 | -13.9265
260 | C-SOK-NAP-FC-FP-WC-OFF0 | -9553.8583 | 4138.7771 | -5415.0812 | 7119.9386 | -0.76055 | 0.80494 | 1.4548 | 1.102 | 4.4367 | -31317.4713 | 9825 | 3 | 4 | 10793.6316 | 4648.3167 | 4689.3167 | 89426.6316 | -15.6484
261 | C-SOK-NAP-FC-FP-WC-OFF0 | -9409.1986 | 4137.1655 | -5272.0331 | 7119.5648 | -0.7405 | 0.81435 | 1.4551 | 1.1133 | 4.4375 | -30741.5186 | 10425 | 3 | 4 | 10664.1903 | 4648.0925 | 4689.0925 | 94097.1903 | -16.9589
262 | C-SOK-NAP-FC-FP-WC-OFF0 | -8379.418 | 4158.5953 | -4220.8227 | 7120.4297 | -0.59278 | 0.89033 | 1.4558 | 1.2343 | 4.44 | -26586.68 | 11650 | 3 | 4 | 9725.0178 | 4648.6114 | 4689.6114 | 102958.0179 | -23.2818
263 | C-SOK-NAP-FC-FP-WC-OFF0 | -7885.371 | 4156.8785 | -3728.4925 | 7120.0371 | -0.52366 | 0.93104 | 1.4563 | 1.282 | 4.4417 | -24613.353 | 12400 | 3 | 4 | 9281.1982 | 4648.3758 | 4689.3758 | 108514.1982 | -27.8463
264 | C-SOK-NAP-FC-FP-WC-OFF0 | -7653.0906 | 4155.6193 | -3497.4712 | 7120.1958 | -0.4912 | 0.95119 | 1.4561 | 1.309 | 4.4412 | -23686.3301 | 13200 | 3 | 4 | 9072.9869 | 4648.4711 | 4689.4711 | 114705.9869 | -31.456
265 | C-SOK-NAP-FC-FP-WC-OFF | -7262.9945 | 4173.4173 | -3089.5772 | 7119.9455 | -0.43393 | 0.98937 | 1.4564 | 1.3768 | 4.4421 | -22096.2826 | 14250 | 3 | 4 | 8711.0602 | 4648.3209 | 4689.3209 | 122744.0603 | -38.2106
266 | C-SOK-NAP-FC-FP-WC-OFF | -6422.4545 | 4170.5783 | -2251.8762 | 7120.2436 | -0.31626 | 1.0776 | 1.4561 | 1.4924 | 4.4409 | -18738.854 | 15200 | 3 | 4 | 7956.4609 | 4648.4998 | 4689.4998 | 129589.4609 | -55.4648
267 | C-SOK-NAP-FC-FP-WC-OFF | -5879.8188 | 4170.9622 | -1708.8565 | 7120.543 | -0.23999 | 1.144 | 1.4563 | 1.5842 | 4.4415 | -16567.6714 | 16150 | 3 | 4 | 7468.0639 | 4648.6794 | 4689.6794 | 136701.0639 | -77.2513
268 | C-SOK-NAP-FC-FP-WC-OFF | -6418.5326 | 4184.181 | -2234.3515 | 7120.4593 | -0.31379 | 1.0801 | 1.4567 | 1.5115 | 4.4431 | -18700.4953 | 16675 | 3 | 4 | 7944.8656 | 4648.6292 | 4689.6292 | 141377.8656 | -61.1758
269 | C-SOK-NAP-FC-FP-WC-OFF | -5243.8051 | 4180.27 | -1063.5351 | 7120.4215 | -0.14936 | 1.2345 | 1.4567 | 1.7274 | 4.4429 | -14008.1038 | 17825 | 3 | 4 | 6889.9691 | 4648.6065 | 4689.6065 | 149522.9691 | -136.1811
270 | C-SOK-NAP-FC-FP-WC-OFF | -4460.2029 | 4178.4329 | -281.7699 | 7119.984 | -0.039575 | 1.3651 | 1.4569 | 1.9187 | 4.4438 | -10876.7566 | 18925 | 3 | 4 | 6185.5933 | 4648.344 | 4689.344 | 157618.5933 | -542.7451
271 | C-SOK-NAP-FC-FP-WC-R100 | -6394.9506 | 2848.8719 | -3546.0787 | 18481.2953 | -0.19187 | 0.82352 | 0.99757 | 0.75881 | 4.5685 | -20831.6825 | 6750 | 3 | 4 | 19386.5039 | 15318.0521 | 15359.0521 | 73419.504 | -16.3731
272 | C-SOK-NAP-FC-FP-WC-R100 | -5803.2879 | 2852.3265 | -2950.9614 | 18520.3437 | -0.15934 | 0.84633 | 0.99718 | 0.7612 | 4.5685 | -18459.2742 | 7200 | 3 | 4 | 18886.9605 | 15353.0772 | 15394.0772 | 76519.9606 | -20.7139
273 | C-SOK-NAP-FC-FP-WC-R100 | -5565.4053 | 2854.6811 | -2710.7241 | 18526.6599 | -0.14631 | 0.8559 | 0.99713 | 0.76435 | 4.5688 | -17503.8192 | 7650 | 3 | 4 | 18677.241 | 15358.858 | 15399.858 | 79910.241 | -23.7982
274 | C-SOK-NAP-FC-FP-WC-R100 | -4765.5686 | 2860.2552 | -1905.3134 | 18528.6636 | -0.10283 | 0.88961 | 0.99708 | 0.80811 | 4.5685 | -14295.1824 | 9175 | 3 | 4 | 17955.8488 | 15360.6566 | 15401.6566 | 91388.8489 | -39.8817
275 | C-SOK-NAP-FC-FP-WC-R100 | -3934.104 | 2864.3614 | -1069.7425 | 18560.5341 | -0.057635 | 0.92733 | 0.99674 | 0.82004 | 4.5681 | -10962.4801 | 9825 | 3 | 4 | 17233.6623 | 15389.2548 | 15430.2548 | 95866.6623 | -75.1923
276 | C-SOK-NAP-FC-FP-WC-R100 | -3551.9516 | 2866.8165 | -685.1352 | 18563.5799 | -0.036907 | 0.94582 | 0.99669 | 0.82887 | 4.5678 | -9429.7791 | 10425 | 3 | 4 | 16890.9851 | 15391.982 | 15432.982 | 100323.9851 | -123.904
277 | C-SOK-NAP-FC-FP-WC-R100 | -2996.7796 | 2883.1077 | -113.6719 | 18567.9324 | -0.0061219 | 0.97488 | 0.99681 | 0.88047 | 4.5699 | -7181.939 | 11650 | 3 | 4 | 16385.4375 | 15395.9212 | 15436.9212 | 109618.4376 | -828.5382
278 | C-SOK-NAP-FC-FP-WC-R100 | -1900.2388 | 2889.2417 | 989.0029 | 18591.1112 | 0.053198 | 1.0358 | 0.99662 | 0.9187 | 4.5706 | -2785.5525 | 12400 | 3 | 4 | 15415.8061 | 15416.8401 | 15457.8401 | 114648.8061 | 100.2939
279 | C-SOK-NAP-FC-FP-WC-R100 | -1254.2876 | 2895.6624 | 1641.3748 | 18586.5426 | 0.08831 | 1.0757 | 0.99663 | 0.94707 | 4.5699 | -191.0465 | 13200 | 3 | 4 | 14826.3958 | 15412.6459 | 15453.6459 | 120459.3958 | 63.9743
280 | C-SOK-NAP-FC-FP-WC-R10 | -1683.2993 | 2892.5301 | 1209.2308 | 18591.7268 | 0.065041 | 1.049 | 0.99669 | 0.94235 | 4.5714 | -1912.3139 | 14250 | 3 | 4 | 15219.0582 | 15417.2831 | 15458.2831 | 129252.0583 | 94.1043
281 | C-SOK-NAP-FC-FP-WC-R10 | -235.7592 | 2896.3466 | 2660.5875 | 18613.6608 | 0.14294 | 1.144 | 0.99642 | 1.0132 | 4.5708 | 3884.2078 | 15200 | 3 | 4 | 13933.7357 | 15437.0305 | 15478.0305 | 135566.7357 | 45.1362
282 | C-SOK-NAP-FC-FP-WC-R10 | 712.6196 | 2901.29 | 3613.9096 | 18608.1528 | 0.19421 | 1.2168 | 0.99641 | 1.0774 | 4.5698 | 7685.9617 | 16150 | 3 | 4 | 13072.1984 | 15432.0019 | 15473.0019 | 142305.1984 | 35.0956
283 | C-SOK-NAP-FC-FP-WC-R10 | -705.3404 | 2894.284 | 2188.9437 | 18610.7997 | 0.11762 | 1.1112 | 0.9964 | 0.98905 | 4.5702 | 2002.4452 | 16675 | 3 | 4 | 14355.0253 | 15434.4539 | 15475.4539 | 147788.0253 | 60.4459
284 | C-SOK-NAP-FC-FP-WC-R10 | 1049.0999 | 2899.3538 | 3948.4537 | 18630.7273 | 0.21193 | 1.244 | 0.99622 | 1.0964 | 4.5705 | 9028.6558 | 17825 | 3 | 4 | 12790.9308 | 15452.3835 | 15493.3835 | 155423.9308 | 35.4393
285 | C-SOK-NAP-FC-FP-WC-R10 | 2403.2284 | 2904.6308 | 5307.8592 | 18628.3923 | 0.28493 | 1.3711 | 0.9963 | 1.2175 | 4.571 | 14453.9648 | 18925 | 3 | 4 | 11566.8981 | 15450.2252 | 15491.2252 | 162999.8981 | 27.7906
286 | C-SOK-NAP-FC-FP-WC-R600 | -7671.4667 | 3081.1989 | -4590.2678 | 14629.6503 | -0.31376 | 0.79919 | 1.0688 | 0.74967 | 4.5895 | -25550.5354 | 6750 | 3 | 4 | 16843.9605 | 11764.1552 | 11805.1552 | 70876.9605 | -12.8689
287 | C-SOK-NAP-FC-FP-WC-R600 | -7201.6446 | 3084.8025 | -4116.8421 | 14696.2255 | -0.28013 | 0.81934 | 1.0676 | 0.74998 | 4.5894 | -23665.2409 | 7200 | 3 | 4 | 16478.8049 | 11824.0036 | 11865.0036 | 74111.805 | -15.12
288 | C-SOK-NAP-FC-FP-WC-R600 | -6976.6114 | 3086.6313 | -3889.9801 | 14705.5409 | -0.26452 | 0.82934 | 1.0675 | 0.75266 | 4.5896 | -22762.0601 | 7650 | 3 | 4 | 16283.639 | 11832.4665 | 11873.4665 | 77516.639 | -16.8749
289 | C-SOK-NAP-FC-FP-WC-R600 | -6262.598 | 3090.8028 | -3171.7952 | 14706.8456 | -0.21567 | 0.86268 | 1.0675 | 0.79535 | 4.59 | -19899.0541 | 9175 | 3 | 4 | 15639.7381 | 11833.6639 | 11874.6639 | 89072.7382 | -24.3389
290 | C-SOK-NAP-FC-FP-WC-R600 | -5550.0055 | 3094.9123 | -2455.0932 | 14756.8245 | -0.16637 | 0.89838 | 1.0665 | 0.80824 | 4.5893 | -17041.8348 | 9825 | 3 | 4 | 15040.9643 | 11878.6905 | 11919.6905 | 93673.9643 | -33.2999
291 | C-SOK-NAP-FC-FP-WC-R600 | -5168.8773 | 3099.3646 | -2069.5127 | 14757.1345 | -0.14024 | 0.91905 | 1.0666 | 0.81632 | 4.59 | -15509.9015 | 10425 | 3 | 4 | 14695.4096 | 11878.8165 | 11919.8165 | 98128.4096 | -41.6565
292 | C-SOK-NAP-FC-FP-WC-R600 | -4737.1409 | 3110.9922 | -1626.1487 | 14764.9823 | -0.11014 | 0.94396 | 1.0666 | 0.8636 | 4.5913 | -13763.5766 | 11650 | 3 | 4 | 14307.0535 | 11886.0415 | 11927.0415 | 107540.0536 | -58.7972
293 | C-SOK-NAP-FC-FP-WC-R600 | -3794.414 | 3120.7444 | -673.6696 | 14797.4955 | -0.045526 | 1.0018 | 1.066 | 0.89825 | 4.5912 | -9976.4153 | 12400 | 3 | 4 | 13481.9611 | 11915.2666 | 11956.2666 | 112714.9611 | -149.5669
294 | C-SOK-NAP-FC-FP-WC-R600 | -3149.2601 | 3126.8098 | -22.4503 | 14795.9481 | -0.0015173 | 1.0458 | 1.066 | 0.92467 | 4.5909 | -7385.6908 | 13200 | 3 | 4 | 12896.2354 | 11913.8289 | 11954.8289 | 118529.2354 | -4747.1243
295 | C-SOK-NAP-FC-FP-WC-R60 | -3592.5886 | 3124.0096 | -468.5789 | 14796.1076 | -0.031669 | 1.0154 | 1.0661 | 0.9233 | 4.5921 | -9163.6716 | 14250 | 3 | 4 | 13297.137 | 11914.0207 | 11955.0207 | 127330.1371 | -246.2234
296 | C-SOK-NAP-FC-FP-WC-R60 | -2338.5379 | 3129.1679 | 790.6299 | 14823.4825 | 0.053336 | 1.106 | 1.0656 | 0.98749 | 4.5915 | -4138.872 | 15200 | 3 | 4 | 12189.976 | 11938.5954 | 11979.5954 | 133822.976 | 154.1092
297 | C-SOK-NAP-FC-FP-WC-R60 | -1361.4399 | 3133.3554 | 1771.9155 | 14829.6752 | 0.11948 | 1.189 | 1.0655 | 1.0513 | 4.5915 | -223.5007 | 16150 | 3 | 4 | 11313.6417 | 11944.1635 | 11985.1635 | 140546.6417 | 72.5551
298 | C-SOK-NAP-FC-FP-WC-R60 | -2790.1241 | 3125.4558 | 335.3316 | 14819.0659 | 0.022628 | 1.0713 | 1.0657 | 0.96592 | 4.5914 | -5951.4036 | 16675 | 3 | 4 | 12594.7704 | 11934.7331 | 11975.7331 | 146027.7704 | 399.7596
299 | C-SOK-NAP-FC-FP-WC-R60 | -1138.8831 | 3133.5613 | 1994.6782 | 14841.8974 | 0.1344 | 1.2094 | 1.0654 | 1.0717 | 4.5926 | 667.0699 | 17825 | 3 | 4 | 11124.3318 | 11955.2667 | 11996.2667 | 153757.3318 | 71.0696
300 | C-SOK-NAP-FC-FP-WC-R60 | -10.618 | 3136.1668 | 3125.5488 | 14853.4578 | 0.21043 | 1.3256 | 1.0652 | 1.1665 | 4.5926 | 5184.4727 | 18925 | 3 | 4 | 10117.7593 | 11965.6671 | 12006.6671 | 161550.7593 | 47.8457
301 | C-SOK-STR-FC-ET-HC-OFF0 | -3315.1065 | 1343.0207 | -1972.0858 | 9537.1761 | -0.20678 | 0.79056 | 0.98622 | 1.0709 | 4.8145 | -11022.0582 | 6613 | 3 | 4 | 10139.5527 | 7961.7693 | 8002.7693 | 63076.5528 | -27.9267
302 | C-SOK-STR-FC-ET-HC-OFF0 | -3162.7243 | 1344.1353 | -1818.589 | 9537.6805 | -0.19067 | 0.80127 | 0.98623 | 1.0959 | 4.8141 | -10410.6716 | 6900 | 3 | 4 | 10002.0426 | 7962.072 | 8003.072 | 65235.0427 | -31.4705
303 | C-SOK-STR-FC-ET-HC-OFF0 | -3097.5343 | 1344.1522 | -1753.3821 | 9537.1923 | -0.18385 | 0.80592 | 0.98628 | 1.1016 | 4.8153 | -10149.8837 | 7188 | 3 | 4 | 9943.0686 | 7961.779 | 8002.779 | 67480.0687 | -33.9215
304 | C-SOK-STR-FC-ET-HC-OFF0 | -2057.7598 | 1372.7629 | -684.9969 | 9537.2019 | -0.071824 | 0.89014 | 0.98626 | 1.3727 | 4.815 | -5943.1011 | 8913 | 3 | 4 | 8990.1109 | 7961.7848 | 8002.7848 | 80327.1109 | -105.5834
305 | C-SOK-STR-FC-ET-HC-OFF0 | -1758.8134 | 1374.5207 | -384.2927 | 9537.4938 | -0.040293 | 0.91704 | 0.98617 | 1.4625 | 4.8134 | -4744.3859 | 9300 | 3 | 4 | 8720.1796 | 7961.9599 | 8002.9599 | 83153.1797 | -195.5546
306 | C-SOK-STR-FC-ET-HC-OFF0 | -1571.9269 | 1372.5206 | -199.4063 | 9537.0541 | -0.020909 | 0.9345 | 0.98623 | 1.5301 | 4.8147 | -4000.1733 | 9688 | 3 | 4 | 8552.918 | 7961.6961 | 8002.6961 | 86089.918 | -391.5986
307 | C-SOK-STR-FC-ET-HC-OFF0 | -869.0114 | 1399.8382 | 530.8268 | 9536.7815 | 0.055661 | 1.0104 | 0.98631 | 1.8276 | 4.8163 | -1142.9819 | 11500 | 3 | 4 | 7903.7399 | 7961.5326 | 8002.5326 | 99936.7399 | 173.1906
308 | C-SOK-STR-FC-ET-HC-OFF0 | -430.3212 | 1402.0206 | 971.6994 | 9536.5118 | 0.10189 | 1.0624 | 0.98632 | 2.0772 | 4.8168 | 615.4161 | 12000 | 3 | 4 | 7507.4475 | 7961.3707 | 8002.3707 | 103540.4475 | 98.3206
309 | C-SOK-STR-FC-ET-HC-OFF0 | -209.11 | 1402.1483 | 1193.0384 | 9536.6822 | 0.1251 | 1.0905 | 0.98631 | 2.2513 | 4.8164 | 1500.474 | 12500 | 3 | 4 | 7308.3829 | 7961.473 | 8002.473 | 107341.3829 | 83.2655
310 | C-SOK-STR-FC-ET-HC-OFF | -72.3542 | 1419.4461 | 1347.0919 | 9536.4709 | 0.14126 | 1.111 | 0.98628 | 2.3121 | 4.8162 | 2076.3266 | 13800 | 3 | 4 | 7174.7973 | 7961.3462 | 8002.3462 | 117607.7974 | 81.3645
311 | C-SOK-STR-FC-ET-HC-OFF | 415.2906 | 1418.9062 | 1834.1968 | 9536.8247 | 0.19233 | 1.1813 | 0.98631 | 2.7521 | 4.8161 | 4026.006 | 14400 | 3 | 4 | 6736.4532 | 7961.5585 | 8002.5585 | 121969.4532 | 62.1345
312 | C-SOK-STR-FC-ET-HC-OFF | 712.5008 | 1423.1225 | 2135.6233 | 9536.9045 | 0.22393 | 1.2294 | 0.98625 | 3.142 | 4.8153 | 5221.8739 | 15000 | 3 | 4 | 6466.4822 | 7961.6064 | 8002.6064 | 126499.4822 | 55.4859
313 | C-SOK-STR-FC-ET-HC-OFF | 692.6386 | 1434.553 | 2127.1916 | 9536.7732 | 0.22305 | 1.2281 | 0.98634 | 3.0115 | 4.8167 | 5161.4762 | 16388 | 3 | 4 | 6477.421 | 7961.5276 | 8002.5276 | 137614.4211 | 60.931
314 | C-SOK-STR-FC-ET-HC-OFF | 1242.0882 | 1434.2843 | 2676.3726 | 9536.2784 | 0.28065 | 1.3263 | 0.9863 | 3.9102 | 4.8167 | 7358.8268 | 17100 | 3 | 4 | 5982.7807 | 7961.2307 | 8002.2307 | 142815.7807 | 50.3717
315 | C-SOK-STR-FC-ET-HC-OFF | 1531.4597 | 1439.8801 | 2971.3398 | 9536.6053 | 0.31157 | 1.3859 | 0.98626 | 4.8231 | 4.8157 | 8525.6389 | 17813 | 3 | 4 | 5719.185 | 7961.4268 | 8002.4268 | 148256.185 | 47.2022
316 | C-SOK-STR-FC-ET-WC-OFF0 | -5840.517 | 1996.6339 | -3843.8831 | 14963.2614 | -0.25689 | 0.7659 | 0.9831 | 0.91555 | 4.7364 | -20034.3447 | 10350 | 3 | 4 | 16597.5714 | 12523.5088 | 12564.5088 | 99430.5715 | -22.5985
317 | C-SOK-STR-FC-ET-WC-OFF0 | -5694.0168 | 1993.8112 | -3700.2056 | 14962.9553 | -0.24729 | 0.77182 | 0.98313 | 0.92017 | 4.7371 | -19453.0484 | 10800 | 3 | 4 | 16467.2456 | 12523.3251 | 12564.3251 | 102900.2457 | -24.4138
318 | C-SOK-STR-FC-ET-WC-OFF0 | -5556.8088 | 1992.154 | -3564.6548 | 14963.2407 | -0.23823 | 0.77745 | 0.98311 | 0.92753 | 4.7366 | -18906.9784 | 11250 | 3 | 4 | 16344.9241 | 12523.4964 | 12564.4964 | 106377.9241 | -26.3177
319 | C-SOK-STR-FC-ET-WC-OFF0 | -4057.2463 | 2004.5248 | -2052.7215 | 14963.5062 | -0.13718 | 0.84657 | 0.98316 | 1.0941 | 4.737 | -12888.1107 | 14075 | 3 | 4 | 14988.1004 | 12523.6557 | 12564.6557 | 127621.1004 | -56.0507
320 | C-SOK-STR-FC-ET-WC-OFF0 | -3692.2455 | 2003.0427 | -1689.2028 | 14963.5794 | -0.11289 | 0.865 | 0.9831 | 1.1249 | 4.7361 | -11430.5776 | 14725 | 3 | 4 | 14660.548 | 12523.6996 | 12564.6996 | 132493.548 | -70.9973
321 | C-SOK-STR-FC-ET-WC-OFF0 | -3486.2952 | 2002.3378 | -1483.9574 | 14963.5231 | -0.099172 | 0.87579 | 0.98309 | 1.1468 | 4.7361 | -10607.951 | 15325 | 3 | 4 | 14475.5874 | 12523.6659 | 12564.6659 | 137108.5874 | -83.9269
322 | C-SOK-STR-FC-ET-WC-OFF0 | -2492.7364 | 2017.9206 | -474.8158 | 14963.5249 | -0.031732 | 0.93305 | 0.98311 | 1.3087 | 4.7363 | -6607.7446 | 17850 | 3 | 4 | 13572.0011 | 12523.6669 | 12564.6669 | 156405.0012 | -302.9392
323 | C-SOK-STR-FC-ET-WC-OFF0 | -2009.0997 | 2016.4614 | 7.3617 | 14963.3553 | 0.00049198 | 0.96313 | 0.98311 | 1.3729 | 4.7365 | -4675.6297 | 18600 | 3 | 4 | 13137.5167 | 12523.5652 | 12564.5652 | 161970.5167 | 20294.947
324 | C-SOK-STR-FC-ET-WC-OFF0 | -1714.0686 | 2013.685 | 299.6164 | 14963.3195 | 0.020023 | 0.98236 | 0.98314 | 1.4231 | 4.7369 | -3500.1329 | 19400 | 3 | 4 | 12873.6474 | 12523.5437 | 12564.5437 | 168106.6474 | 519.1375
325 | C-SOK-STR-FC-ET-WC-OFF | -1179.827 | 2024.7352 | 844.9082 | 14963.7021 | 0.056464 | 1.0203 | 0.98314 | 1.5596 | 4.7366 | -1344.7494 | 21850 | 3 | 4 | 12386.4115 | 12523.7733 | 12564.7733 | 187219.4116 | 206.7143
326 | C-SOK-STR-FC-ET-WC-OFF | -442.8706 | 2022.2235 | 1579.3529 | 14963.6301 | 0.10555 | 1.0762 | 0.98311 | 1.7218 | 4.7362 | 1598.8901 | 22800 | 3 | 4 | 11724.6341 | 12523.7301 | 12564.7301 | 194157.6341 | 114.9793
327 | C-SOK-STR-FC-ET-WC-OFF | -22.0981 | 2020.1084 | 1998.0103 | 14963.2188 | 0.13353 | 1.111 | 0.98311 | 1.8397 | 4.7366 | 3278.4548 | 23750 | 3 | 4 | 11346.9708 | 12523.4833 | 12564.4833 | 201379.9708 | 94.5018
328 | C-SOK-STR-FC-ET-WC-OFF | -187.763 | 2026.3773 | 1838.6143 | 14963.1511 | 0.12288 | 1.0975 | 0.9831 | 1.7884 | 4.7365 | 2626.2436 | 25575 | 3 | 4 | 11492.2461 | 12523.4427 | 12564.4427 | 216125.2461 | 110.7143
329 | C-SOK-STR-FC-ET-WC-OFF | 756.7091 | 2022.7402 | 2779.4493 | 14963.5283 | 0.18575 | 1.1822 | 0.98307 | 2.1083 | 4.7358 | 6398.07 | 26725 | 3 | 4 | 10644.6543 | 12523.669 | 12564.669 | 224477.6543 | 76.2428
330 | C-SOK-STR-FC-ET-WC-OFF | 1208.9652 | 2020.0144 | 3228.9795 | 14963.3508 | 0.21579 | 1.2276 | 0.98315 | 2.3466 | 4.7371 | 8202.5513 | 27825 | 3 | 4 | 10239.1647 | 12523.5625 | 12564.5625 | 232872.1647 | 68.2282
331 | C-SOK-STR-FC-FP-HC-OFF0 | -4697.5438 | 1358.0337 | -3339.5101 | 9537.4461 | -0.35015 | 0.70655 | 0.98614 | 0.8363 | 4.8129 | -16526.7857 | 4313 | 3 | 4 | 11374.9005 | 7961.9313 | 8002.9313 | 45911.9005 | -11.3517
332 | C-SOK-STR-FC-FP-HC-OFF0 | -4624.2203 | 1362.6382 | -3261.582 | 9537.4199 | -0.34198 | 0.7109 | 0.9862 | 0.83415 | 4.8139 | -16225.8174 | 4600 | 3 | 4 | 11306.1309 | 7961.9156 | 8002.9156 | 48139.131 | -12.3058
333 | C-SOK-STR-FC-FP-HC-OFF0 | -4622.852 | 1362.7246 | -3260.1274 | 9537.4477 | -0.34182 | 0.711 | 0.98623 | 0.82999 | 4.8143 | -16220.2003 | 4888 | 3 | 4 | 11304.8643 | 7961.9323 | 8002.9323 | 50441.8644 | -13.0176
334 | C-SOK-STR-FC-FP-HC-OFF0 | -3867.5668 | 1374.675 | -2492.8918 | 9536.9703 | -0.26139 | 0.75631 | 0.9862 | 0.93846 | 4.8144 | -13179.1422 | 5813 | 3 | 4 | 10617.651 | 7961.6458 | 8002.6458 | 57154.651 | -19.7169
335 | C-SOK-STR-FC-FP-HC-OFF0 | -3678.2465 | 1377.7293 | -2300.5172 | 9536.8465 | -0.24122 | 0.76863 | 0.98623 | 0.95392 | 4.815 | -12416.7706 | 6200 | 3 | 4 | 10445.3558 | 7961.5716 | 8002.5716 | 60078.3559 | -22.6366
336 | C-SOK-STR-FC-FP-HC-OFF0 | -3562.9615 | 1378.5611 | -2184.4004 | 9536.739 | -0.22905 | 0.7763 | 0.9863 | 0.9596 | 4.8162 | -11954.2443 | 6588 | 3 | 4 | 10341.0358 | 7961.5071 | 8002.5071 | 63078.0358 | -25.2131
337 | C-SOK-STR-FC-FP-HC-OFF0 | -3143.1359 | 1388.7257 | -1754.4103 | 9537.3841 | -0.18395 | 0.80575 | 0.98616 | 1.0404 | 4.8133 | -10258.0009 | 7500 | 3 | 4 | 9957.4811 | 7961.8941 | 8002.8941 | 69990.4811 | -35.3324
338 | C-SOK-STR-FC-FP-HC-OFF0 | -2778.3754 | 1392.3847 | -1385.9907 | 9537.2982 | -0.14532 | 0.83295 | 0.98618 | 1.0977 | 4.8138 | -8792.8604 | 8000 | 3 | 4 | 9626.9496 | 7961.8426 | 8002.8426 | 73659.9496 | -47.372
339 | C-SOK-STR-FC-FP-HC-OFF0 | -2589.4459 | 1393.5464 | -1195.8995 | 9536.8591 | -0.1254 | 0.84781 | 0.98632 | 1.1258 | 4.8163 | -8035.2063 | 8500 | 3 | 4 | 9455.9526 | 7961.5791 | 8002.5791 | 77488.9526 | -58.1039
340 | C-SOK-STR-FC-FP-HC-OFF | -2625.3121 | 1394.6393 | -1230.6729 | 9536.8104 | -0.12904 | 0.84501 | 0.98624 | 1.1229 | 4.8152 | -8176.8497 | 9000 | 3 | 4 | 9487.5472 | 7961.5499 | 8002.5499 | 81520.5473 | -59.7381
341 | C-SOK-STR-FC-FP-HC-OFF | -2132.1421 | 1400.0944 | -732.0477 | 9536.508 | -0.076763 | 0.8861 | 0.98631 | 1.213 | 4.8166 | -6195.0778 | 9600 | 3 | 4 | 9040.2397 | 7961.3685 | 8002.3685 | 85873.2397 | -106.374
342 | C-SOK-STR-FC-FP-HC-OFF | -1868.9603 | 1401.9196 | -467.0406 | 9537.0326 | -0.048971 | 0.90954 | 0.98627 | 1.262 | 4.8154 | -5139.3083 | 10200 | 3 | 4 | 8802.5957 | 7961.6832 | 8002.6832 | 90435.5957 | -176.5005
343 | C-SOK-STR-FC-FP-HC-OFF | -2053.6544 | 1399.1262 | -654.5283 | 9537.4428 | -0.068627 | 0.89272 | 0.98617 | 1.2305 | 4.8135 | -5882.7408 | 10688 | 3 | 4 | 8970.7426 | 7961.9293 | 8002.9293 | 94507.7427 | -132.1636
344 | C-SOK-STR-FC-FP-HC-OFF | -1446.9331 | 1409.6869 | -37.2462 | 9537.2903 | -0.0039053 | 0.95034 | 0.98624 | 1.3662 | 4.8147 | -3438.2543 | 11400 | 3 | 4 | 8418.2655 | 7961.8378 | 8002.8378 | 99651.2655 | -2460.6093
345 | C-SOK-STR-FC-FP-HC-OFF | -1151.6117 | 1409.2358 | 257.6241 | 9537.1583 | 0.027013 | 0.98053 | 0.98623 | 1.4338 | 4.8146 | -2257.7205 | 12113 | 3 | 4 | 8152.6677 | 7961.7586 | 8002.7586 | 105089.6677 | 376.855
346 | C-SOK-TOU-CC-ET-HC-R100 | 3321.8345 | 920.3591 | 4242.1936 | 33265.4534 | 0.12753 | 0.96449 | 0.85047 | 1.1185 | 5.1742 | 14821.27 | 9488 | 3 | 4 | 25911.9757 | 29453.8422 | 29494.8422 | 101848.9757 | 17.0558
347 | C-SOK-TOU-CC-ET-HC-R100 | 4106.3087 | 911.2268 | 5017.5355 | 33327.5208 | 0.15055 | 0.99049 | 0.85034 | 1.1566 | 5.1701 | 17943.9462 | 9900 | 3 | 4 | 25267.3331 | 29509.7471 | 29550.7471 | 104500.3332 | 14.9375
348 | C-SOK-TOU-CC-ET-HC-R100 | 4381.4523 | 909.1305 | 5290.5828 | 33340.841 | 0.15868 | 1.0001 | 0.85033 | 1.1858 | 5.1708 | 19041.0265 | 10313 | 3 | 4 | 25032.9267 | 29521.712 | 29562.712 | 107569.9267 | 14.7445
349 | C-SOK-TOU-CC-ET-HC-R100 | 5388.4042 | 947.4211 | 6335.8253 | 33335.8604 | 0.19006 | 1.0389 | 0.85038 | 1.3901 | 5.1744 | 23132.6518 | 12938 | 3 | 4 | 24099.2642 | 29517.2806 | 29558.2806 | 127636.2643 | 15.4799
350 | C-SOK-TOU-CC-ET-HC-R100 | 6385.7006 | 939.5374 | 7325.2381 | 33393.6263 | 0.21936 | 1.0778 | 0.85034 | 1.5193 | 5.1756 | 27108.6983 | 13500 | 3 | 4 | 23258.343 | 29569.196 | 29610.196 | 131291.343 | 13.8809
351 | C-SOK-TOU-CC-ET-HC-R100 | 6775.2659 | 940.7974 | 7716.0634 | 33398.2456 | 0.23103 | 1.0941 | 0.8503 | 1.6066 | 5.1737 | 28669.0595 | 14063 | 3 | 4 | 22911.1462 | 29573.364 | 29614.364 | 135448.1462 | 13.716
352 | C-SOK-TOU-CC-ET-HC-R100 | 7104.1201 | 954.692 | 8058.8121 | 33386.0261 | 0.24138 | 1.1091 | 0.85035 | 1.6036 | 5.1757 | 30007.6336 | 16675 | 3 | 4 | 22595.8481 | 29562.3714 | 29603.3714 | 156028.8482 | 15.6879
353 | C-SOK-TOU-CC-ET-HC-R100 | 8309.7655 | 955.2559 | 9265.0215 | 33445.617 | 0.27702 | 1.1637 | 0.85025 | 1.8488 | 5.1742 | 34831.1553 | 17400 | 3 | 4 | 21564.0498 | 29615.9923 | 29656.9923 | 160797.0498 | 14.1543
354 | C-SOK-TOU-CC-ET-HC-R100 | 8775.5122 | 950.1658 | 9725.678 | 33455.0764 | 0.29071 | 1.1862 | 0.85028 | 2.004 | 5.1768 | 36685.6583 | 18125 | 3 | 4 | 21156.4193 | 29624.4798 | 29665.4798 | 166189.4193 | 14.0375
355 | C-SOK-TOU-CC-ET-HC-R10 | 8668.6359 | 977.0974 | 9645.7334 | 33421.5621 | 0.28861 | 1.1828 | 0.85034 | 2.0121 | 5.1786 | 36303.0395 | 20125 | 3 | 4 | 21206.3205 | 29594.3513 | 29635.3513 | 182239.3206 | 15.8209
356 | C-SOK-TOU-CC-ET-HC-R10 | 9846.0086 | 970.437 | 10816.4457 | 33479.9916 | 0.32307 | 1.2429 | 0.85029 | 2.3207 | 5.1798 | 41001.4295 | 21000 | 3 | 4 | 20203.2555 | 29646.9254 | 29687.9254 | 188236.2555 | 14.6581
357 | C-SOK-TOU-CC-ET-HC-R10 | 10351.0336 | 966.8978 | 11317.9314 | 33488.9231 | 0.33796 | 1.2708 | 0.85027 | 2.5502 | 5.1791 | 43015.6308 | 21875 | 3 | 4 | 19758.913 | 29654.9819 | 29695.9819 | 194791.913 | 14.5871
358 | C-SOK-TOU-CC-ET-HC-R10 | 9907.1544 | 981.0536 | 10888.2079 | 33455.6994 | 0.32545 | 1.2473 | 0.85031 | 2.2753 | 5.1794 | 41263.7067 | 23575 | 3 | 4 | 20120.0006 | 29625.0717 | 29666.0717 | 208753.0006 | 16.4478
359 | C-SOK-TOU-CC-ET-HC-R10 | 11183.0217 | 979.4008 | 12162.4226 | 33500.4216 | 0.36305 | 1.3209 | 0.85025 | 2.8213 | 5.1785 | 46364.4217 | 24600 | 3 | 4 | 19012.9111 | 29665.2711 | 29706.2711 | 215845.9111 | 15.3045
360 | C-SOK-TOU-CC-ET-HC-R10 | 11818.8486 | 974.2774 | 12793.126 | 33508.4001 | 0.38179 | 1.3609 | 0.85025 | 3.2988 | 5.1796 | 48899.1901 | 25625 | 3 | 4 | 18450.954 | 29672.4841 | 29713.4841 | 223483.954 | 15.1465
361 | C-SOK-TOU-CC-ET-HC-R600 | 2196.2144 | 1228.3863 | 3424.6007 | 24649.6219 | 0.13893 | 1.011 | 0.88185 | 1.0912 | 5.2455 | 10832.1682 | 9488 | 3 | 4 | 18889.8551 | 21603.4799 | 21644.4799 | 94826.8552 | 21.3696
362 | C-SOK-TOU-CC-ET-HC-R600 | 2815.816 | 1218.506 | 4034.322 | 24766.1954 | 0.1629 | 1.0395 | 0.88145 | 1.1103 | 5.2433 | 13294.1075 | 9900 | 3 | 4 | 18443.0666 | 21708.4046 | 21749.4046 | 97676.0667 | 18.8202
363 | C-SOK-TOU-CC-ET-HC-R600 | 3068.9413 | 1213.1807 | 4282.122 | 24797.9816 | 0.17268 | 1.0518 | 0.88137 | 1.1357 | 5.2439 | 14297.7329 | 10313 | 3 | 4 | 18247.0494 | 21737.005 | 21778.005 | 100784.0494 | 18.4502
364 | C-SOK-TOU-CC-ET-HC-R600 | 4013.4804 | 1256.1783 | 5269.6587 | 24765.7669 | 0.21278 | 1.1055 | 0.88151 | 1.32 | 5.246 | 18147.552 | 12938 | 3 | 4 | 17342.2238 | 21708.0632 | 21749.0632 | 120879.2239 | 18.8115
365 | C-SOK-TOU-CC-ET-HC-R600 | 4794.4071 | 1247.3463 | 6041.7534 | 24856.451 | 0.24307 | 1.1495 | 0.88128 | 1.4237 | 5.2473 | 21256.5389 | 13500 | 3 | 4 | 16726.2936 | 21789.6678 | 21830.6678 | 124759.2936 | 17.0362
366 | C-SOK-TOU-CC-ET-HC-R600 | 5151.3364 | 1246.5477 | 6397.884 | 24878.6199 | 0.25716 | 1.1712 | 0.88118 | 1.4997 | 5.2459 | 22682.9249 | 14063 | 3 | 4 | 16425.4742 | 21809.6055 | 21850.6055 | 128962.4742 | 16.7418
367 | C-SOK-TOU-CC-ET-HC-R600 | 5458.9113 | 1264.8235 | 6723.7348 | 24837.5321 | 0.27071 | 1.1931 | 0.88133 | 1.512 | 5.2471 | 23943.6844 | 16675 | 3 | 4 | 16100.7399 | 21772.6542 | 21813.6542 | 149533.74 | 18.9954
368 | C-SOK-TOU-CC-ET-HC-R600 | 6453.7252 | 1263.2144 | 7716.9397 | 24904.8027 | 0.30986 | 1.2605 | 0.88113 | 1.7379 | 5.2468 | 27920.2583 | 17400 | 3 | 4 | 15266.8849 | 21833.1663 | 21874.1663 | 154499.8849 | 17.1863
369 | C-SOK-TOU-CC-ET-HC-R600 | 6914.8147 | 1256.8762 | 8171.6908 | 24924.5359 | 0.32786 | 1.2943 | 0.88109 | 1.8834 | 5.2477 | 29754.0523 | 18125 | 3 | 4 | 14873.4535 | 21850.9124 | 21891.9124 | 159906.4535 | 16.8893
370 | C-SOK-TOU-CC-ET-HC-R60 | 6783.5417 | 1283.9977 | 8067.5394 | 24879.9459 | 0.32426 | 1.2875 | 0.88121 | 1.8108 | 5.2471 | 29274.1629 | 20125 | 3 | 4 | 14935.2144 | 21810.8005 | 21851.8005 | 175968.2145 | 19.1033
371 | C-SOK-TOU-CC-ET-HC-R60 | 7868.683 | 1281.1403 | 9149.8234 | 24939.5993 | 0.36688 | 1.374 | 0.88108 | 2.1547 | 5.2487 | 33609.9661 | 21000 | 3 | 4 | 14013.9599 | 21864.4589 | 21905.4589 | 182046.9599 | 17.5021
372 | C-SOK-TOU-CC-ET-HC-R60 | 8397.4679 | 1276.6481 | 9674.1159 | 24955.6171 | 0.38765 | 1.4205 | 0.88102 | 2.438 | 5.2483 | 35717.6183 | 21875 | 3 | 4 | 13555.1778 | 21878.8878 | 21919.8878 | 188588.1778 | 17.2283
373 | C-SOK-TOU-CC-ET-HC-R60 | 7852.805 | 1291.0022 | 9143.8072 | 24915.0267 | 0.367 | 1.3744 | 0.88115 | 2.0555 | 5.2489 | 33562.8902 | 23575 | 3 | 4 | 14000.205 | 21842.3308 | 21883.3308 | 202633.205 | 19.7675
374 | C-SOK-TOU-CC-ET-HC-R60 | 9074.3325 | 1289.606 | 10363.9385 | 24971.6955 | 0.41503 | 1.487 | 0.88102 | 2.5974 | 5.2501 | 38446.6735 | 24600 | 3 | 4 | 12952.6924 | 21893.3553 | 21934.3553 | 209785.6924 | 18.1255
375 | C-SOK-TOU-CC-ET-HC-R60 | 9638.0465 | 1285.9237 | 10923.9702 | 24989.2793 | 0.43715 | 1.5453 | 0.88093 | 2.9917 | 5.2489 | 40695.3921 | 25625 | 3 | 4 | 12463.4107 | 21909.2068 | 21950.2068 | 217496.4107 | 17.9007
376 | C-SOK-TOU-CC-FP-HC-R100 | 2227.0317 | 902.3268 | 3129.3585 | 33194.1607 | 0.094274 | 0.92909 | 0.85051 | 0.96207 | 5.1705 | 10412.0047 | 6188 | 3 | 4 | 26843.9868 | 29389.7114 | 29430.7114 | 76380.9869 | 15.0032
377 | C-SOK-TOU-CC-FP-HC-R100 | 2988.3199 | 897.9107 | 3886.2306 | 33250.6594 | 0.11688 | 0.95279 | 0.85042 | 0.96258 | 5.169 | 13449.7975 | 6600 | 3 | 4 | 26212.3501 | 29440.5844 | 29481.5844 | 79045.3502 | 12.7537
378 | C-SOK-TOU-CC-FP-HC-R100 | 3321.6069 | 897.0496 | 4218.6566 | 33268.7178 | 0.12681 | 0.96361 | 0.8504 | 0.97081 | 5.169 | 14781.5105 | 7013 | 3 | 4 | 25929.1307 | 29456.8067 | 29497.8067 | 82066.1307 | 12.4609
379 | C-SOK-TOU-CC-FP-HC-R100 | 3940.201 | 917.5145 | 4857.7156 | 33275.6343 | 0.14598 | 0.98528 | 0.85043 | 1.089 | 5.1717 | 17289.9949 | 8438 | 3 | 4 | 25366.3086 | 29462.9983 | 29503.9983 | 92903.3087 | 13.0513
380 | C-SOK-TOU-CC-FP-HC-R100 | 4911.2654 | 913.5699 | 5824.8353 | 33328.023 | 0.17477 | 1.0196 | 0.85034 | 1.1174 | 5.1699 | 21167.678 | 9000 | 3 | 4 | 24541.8931 | 29510.1739 | 29551.1739 | 96574.8931 | 11.5065
381 | C-SOK-TOU-CC-FP-HC-R100 | 5296.9837 | 914.6244 | 6211.608 | 33337.2852 | 0.18633 | 1.0341 | 0.85037 | 1.1417 | 5.1727 | 22712.3086 | 9563 | 3 | 4 | 24202.4412 | 29518.5011 | 29559.5011 | 100739.4412 | 11.4592
382 | C-SOK-TOU-CC-FP-HC-R100 | 5473.672 | 924.8164 | 6398.4884 | 33335.98 | 0.19194 | 1.0413 | 0.85036 | 1.2099 | 5.1727 | 23436.0487 | 10875 | 3 | 4 | 24036.1697 | 29517.3644 | 29558.3644 | 111069.1698 | 12.7391
383 | C-SOK-TOU-CC-FP-HC-R100 | 6557.8993 | 921.0405 | 7478.9398 | 33380.0522 | 0.22405 | 1.0843 | 0.85033 | 1.2648 | 5.1738 | 27766.6647 | 11600 | 3 | 4 | 23102.2446 | 29556.9783 | 29597.9783 | 115935.2446 | 11.5441
384 | C-SOK-TOU-CC-FP-HC-R100 | 7055.8828 | 921.2683 | 7977.1511 | 33385.5419 | 0.23894 | 1.1055 | 0.8503 | 1.3117 | 5.1726 | 29758.9784 | 12325 | 3 | 4 | 22658.894 | 29561.9495 | 29602.9495 | 121291.894 | 11.4939
385 | C-SOK-TOU-CC-FP-HC-R10 | 6761.3695 | 927.5289 | 7688.8984 | 33374.54 | 0.23038 | 1.0933 | 0.85036 | 1.3425 | 5.1759 | 28591.3596 | 13125 | 3 | 4 | 22910.311 | 29552.0609 | 29593.0609 | 127943.3111 | 12.7912
386 | C-SOK-TOU-CC-FP-HC-R10 | 7937.2843 | 927.5987 | 8864.883 | 33419.6389 | 0.26526 | 1.1451 | 0.85029 | 1.4381 | 5.1748 | 33295.135 | 14000 | 3 | 4 | 21892.4918 | 29592.6069 | 29633.6069 | 133925.4918 | 11.7646
387 | C-SOK-TOU-CC-FP-HC-R10 | 8529.056 | 925.7668 | 9454.8228 | 33426.4874 | 0.28285 | 1.1732 | 0.85027 | 1.5105 | 5.1741 | 35659.1685 | 14875 | 3 | 4 | 21367.1942 | 29598.8047 | 29639.8047 | 140400.1942 | 11.7147
388 | C-SOK-TOU-CC-FP-HC-R10 | 7811.404 | 925.1832 | 8736.5872 | 33404.9717 | 0.26154 | 1.1394 | 0.85036 | 1.4391 | 5.178 | 32787.5881 | 15375 | 3 | 4 | 21994.02 | 29579.3936 | 29620.3936 | 145027.02 | 13.2096
389 | C-SOK-TOU-CC-FP-HC-R10 | 9105.631 | 926.9847 | 10032.6157 | 33448.783 | 0.29994 | 1.2019 | 0.85031 | 1.5953 | 5.1789 | 37967.4985 | 16400 | 3 | 4 | 20867.5875 | 29618.8462 | 29659.8462 | 152100.5875 | 12.2043
390 | C-SOK-TOU-CC-FP-HC-R10 | 9709.8982 | 925.7502 | 10635.6483 | 33458.9343 | 0.31787 | 1.2334 | 0.85029 | 1.6612 | 5.1784 | 40382.5096 | 17425 | 3 | 4 | 20333.6744 | 29628.0328 | 29669.0328 | 159766.6744 | 12.2322
391 | C-SOK-TOU-CC-FP-HC-R600 | 999.1072 | 1208.239 | 2207.3463 | 24552.9832 | 0.089901 | 0.95679 | 0.88212 | 0.95011 | 5.2452 | 6010.1606 | 6188 | 3 | 4 | 19892.3842 | 21516.5241 | 21557.5241 | 69429.3843 | 21.6875
392 | C-SOK-TOU-CC-FP-HC-R600 | 1649.9829 | 1204.2173 | 2854.2002 | 24642.2138 | 0.11583 | 0.98451 | 0.88179 | 0.94618 | 5.2421 | 8606.9603 | 6600 | 3 | 4 | 19389.3073 | 21596.8223 | 21637.8223 | 72222.3074 | 17.7228
393 | C-SOK-TOU-CC-FP-HC-R600 | 1873.4722 | 1200.8879 | 3074.3601 | 24670.4795 | 0.12462 | 0.9943 | 0.88169 | 0.94614 | 5.2417 | 9495.3686 | 7013 | 3 | 4 | 19215.6074 | 21622.2651 | 21663.2651 | 75352.6074 | 17.4636
394 | C-SOK-TOU-CC-FP-HC-R600 | 2530.3329 | 1224.1692 | 3754.5021 | 24668.8166 | 0.1522 | 1.0267 | 0.88175 | 1.0627 | 5.244 | 12161.6136 | 8438 | 3 | 4 | 18608.9641 | 21620.7653 | 21661.7653 | 86145.9642 | 17.1752
395 | C-SOK-TOU-CC-FP-HC-R600 | 3314.3123 | 1220.4414 | 4534.7536 | 24758.3923 | 0.18316 | 1.0654 | 0.88151 | 1.0909 | 5.2449 | 15291.318 | 9000 | 3 | 4 | 17986.2698 | 21701.4156 | 21742.4156 | 90019.2698 | 15.0564
396 | C-SOK-TOU-CC-FP-HC-R600 | 3633.8581 | 1221.7094 | 4855.5675 | 24782.3111 | 0.19593 | 1.0823 | 0.88145 | 1.108 | 5.2458 | 16571.6147 | 9563 | 3 | 4 | 17719.4775 | 21722.9754 | 21763.9754 | 94256.4775 | 14.9298
397 | C-SOK-TOU-CC-FP-HC-R600 | 3773.9395 | 1229.7078 | 5003.6473 | 24755.4086 | 0.20212 | 1.0907 | 0.88151 | 1.1578 | 5.2445 | 17145.2711 | 10875 | 3 | 4 | 17564.3398 | 21698.71 | 21739.71 | 104597.3399 | 16.5594
398 | C-SOK-TOU-CC-FP-HC-R600 | 4746.9839 | 1228.4723 | 5975.4562 | 24835.0329 | 0.24061 | 1.1458 | 0.88129 | 1.2489 | 5.2452 | 21035.3894 | 11600 | 3 | 4 | 16761 | 21770.3689 | 21811.3689 | 109594 | 14.6905
399 | C-SOK-TOU-CC-FP-HC-R600 | 5176.4517 | 1229.1828 | 6405.6345 | 24855.1696 | 0.25772 | 1.1721 | 0.88124 | 1.281 | 5.2453 | 22754.4447 | 12325 | 3 | 4 | 16392.1466 | 21788.4628 | 21829.4628 | 115025.1466 | 14.549
400 | C-SOK-TOU-CC-FP-HC-R60 | 4827.3485 | 1236.2552 | 6063.6037 | 24810.5763 | 0.2444 | 1.1516 | 0.88142 | 1.2754 | 5.2471 | 21369.8193 | 13125 | 3 | 4 | 16661.9639 | 21748.3307 | 21789.3307 | 121694.964 | 16.4763
401 | C-SOK-TOU-CC-FP-HC-R60 | 5853.4113 | 1235.1925 | 7088.6038 | 24880.922 | 0.2849 | 1.2166 | 0.88121 | 1.3858 | 5.2472 | 25472.2993 | 14000 | 3 | 4 | 15802.4874 | 21811.6731 | 21852.6731 | 127835.4874 | 14.9512
402 | C-SOK-TOU-CC-FP-HC-R60 | 6381.9463 | 1234.7018 | 7616.6481 | 24903.5235 | 0.30585 | 1.2533 | 0.88116 | 1.4625 | 5.2477 | 27585.6214 | 14875 | 3 | 4 | 15347.4174 | 21831.9901 | 21872.9901 | 134380.4174 | 14.7713
403 | C-SOK-TOU-CC-FP-HC-R60 | 5697.7313 | 1233.3117 | 6931.043 | 24852.9727 | 0.27888 | 1.2066 | 0.88131 | 1.3724 | 5.2478 | 24846.4448 | 15375 | 3 | 4 | 15918.5085 | 21786.4537 | 21827.4537 | 138951.5085 | 16.8985
404 | C-SOK-TOU-CC-FP-HC-R60 | 6854.8513 | 1234.9756 | 8089.8269 | 24913.268 | 0.32472 | 1.2883 | 0.88116 | 1.5416 | 5.2487 | 29477.6979 | 16400 | 3 | 4 | 14930.3777 | 21840.7293 | 21881.7293 | 146163.3777 | 15.3627
405 | C-SOK-TOU-CC-FP-HC-R60 | 7453.6178 | 1235.9925 | 8689.6103 | 24931.7828 | 0.34854 | 1.3353 | 0.88108 | 1.6655 | 5.2479 | 31874.4587 | 17425 | 3 | 4 | 14407.6088 | 21857.4603 | 21898.4603 | 153840.6088 | 15.1839
406 | C-SOK-TOU-FC-ET-HC-OFF0 | -3702.4051 | 1705.8182 | -1996.5869 | 5752.9474 | -0.34705 | 0.83279 | 1.1747 | 1.1221 | 4.6712 | -11966.5899 | 6613 | 3 | 4 | 6718.9885 | 4410.3148 | 4451.3148 | 59655.9885 | -27.6495
407 | C-SOK-TOU-FC-ET-HC-OFF0 | -3448.2621 | 1712.1078 | -1736.1542 | 5753.5371 | -0.30175 | 0.86155 | 1.1744 | 1.1489 | 4.6688 | -10939.5352 | 6900 | 3 | 4 | 6486.8398 | 4410.6687 | 4451.6687 | 61719.8399 | -32.9856
408 | C-SOK-TOU-FC-ET-HC-OFF0 | -3295.8174 | 1713.3087 | -1582.5087 | 5753.7492 | -0.27504 | 0.87959 | 1.1744 | 1.1676 | 4.6685 | -10327.755 | 7188 | 3 | 4 | 6349.0464 | 4410.796 | 4451.796 | 63886.0465 | -37.557
409 | C-SOK-TOU-FC-ET-HC-OFF0 | -2159.4243 | 1758.7288 | -400.6955 | 5753.1261 | -0.069648 | 1.0487 | 1.1747 | 1.4913 | 4.6708 | -5706.4824 | 8913 | 3 | 4 | 5298.6667 | 4410.4221 | 4451.4221 | 76635.6667 | -180.1474
410 | C-SOK-TOU-FC-ET-HC-OFF0 | -1710.9281 | 1762.3541 | 51.4259 | 5753.0897 | 0.0089388 | 1.1318 | 1.1746 | 1.6063 | 4.6704 | -3906.4558 | 9300 | 3 | 4 | 4892.8232 | 4410.4003 | 4451.4003 | 79325.8233 | 1455.9668
411 | C-SOK-TOU-FC-ET-HC-OFF0 | -1548.9251 | 1761.1305 | 212.2055 | 5752.7768 | 0.036887 | 1.1647 | 1.1746 | 1.6634 | 4.6706 | -3260.4827 | 9688 | 3 | 4 | 4747.5667 | 4410.2125 | 4451.2125 | 82284.5667 | 366.783
412 | C-SOK-TOU-FC-ET-HC-OFF0 | -896.8313 | 1810.6567 | 913.8253 | 5752.5322 | 0.15886 | 1.3336 | 1.1746 | 2.0218 | 4.671 | -569.5642 | 11500 | 3 | 4 | 4130.8199 | 4410.0657 | 4451.0657 | 96163.82 | 100.3614
413 | C-SOK-TOU-FC-ET-HC-OFF0 | -369.779 | 1815.8164 | 1446.0374 | 5753.1111 | 0.25135 | 1.4984 | 1.1746 | 2.3105 | 4.6707 | 1547.2447 | 12000 | 3 | 4 | 3653.7243 | 4410.4131 | 4451.4131 | 99686.7243 | 65.8595
414 | C-SOK-TOU-FC-ET-HC-OFF0 | -114.3115 | 1820.8309 | 1706.5194 | 5752.8818 | 0.29664 | 1.5949 | 1.1747 | 2.4985 | 4.6713 | 2577.4722 | 12500 | 3 | 4 | 3420.6573 | 4410.2755 | 4451.2755 | 103453.6573 | 58.0142
415 | C-SOK-TOU-FC-ET-HC-OFF | -199.0939 | 1836.598 | 1637.5042 | 5752.7923 | 0.28465 | 1.5683 | 1.1748 | 2.4157 | 4.6716 | 2264.6213 | 13800 | 3 | 4 | 3487.4475 | 4410.2218 | 4451.2218 | 113920.4476 | 66.8513
416 | C-SOK-TOU-FC-ET-HC-OFF | 409.5112 | 1844.4917 | 2254.0029 | 5752.4599 | 0.39183 | 1.8446 | 1.1747 | 2.9587 | 4.6717 | 4712.1977 | 14400 | 3 | 4 | 2934.7673 | 4410.0224 | 4451.0224 | 118167.7673 | 50.451
417 | C-SOK-TOU-FC-ET-HC-OFF | 702.083 | 1852.6195 | 2554.7025 | 5752.2538 | 0.44412 | 2.0183 | 1.1748 | 3.3605 | 4.6726 | 5896.0312 | 15000 | 3 | 4 | 2666.4523 | 4409.8987 | 4450.8987 | 122699.4523 | 46.2866
418 | C-SOK-TOU-FC-ET-HC-OFF | 499.6894 | 1857.7537 | 2357.4431 | 5753.0226 | 0.40977 | 1.9007 | 1.1747 | 2.9922 | 4.6712 | 5095.0139 | 16388 | 3 | 4 | 2845.9873 | 4410.36 | 4451.36 | 133982.9874 | 54.9458
419 | C-SOK-TOU-FC-ET-HC-OFF | 1153.4814 | 1871.4389 | 3024.9203 | 5751.925 | 0.5259 | 2.3662 | 1.1747 | 3.9455 | 4.672 | 7732.9905 | 17100 | 3 | 4 | 2248.7048 | 4409.7014 | 4450.7014 | 139081.7048 | 44.5073
420 | C-SOK-TOU-FC-ET-HC-OFF | 1454.6604 | 1885.9715 | 3340.632 | 5752.7105 | 0.58071 | 2.6756 | 1.1748 | 4.6388 | 4.6718 | 8961.9276 | 17813 | 3 | 4 | 1969.3954 | 4410.1727 | 4451.1727 | 144506.3954 | 41.9248
421 | C-SOK-TOU-FC-ET-HC-R100 | 1318.6306 | 648.8804 | 1967.5111 | 22678.6008 | 0.086756 | 0.91629 | 0.84997 | 0.8627 | 4.6835 | 6355.9899 | 6613 | 3 | 4 | 18423.6208 | 19999.7167 | 20040.7167 | 71360.6209 | 26.0837
422 | C-SOK-TOU-FC-ET-HC-R100 | 1800.3093 | 646.7955 | 2447.1048 | 22708.5777 | 0.10776 | 0.93788 | 0.84997 | 0.87301 | 4.688 | 8279.2298 | 6900 | 3 | 4 | 18018.5284 | 20026.8841 | 20067.8841 | 73251.5285 | 21.7333
423 | C-SOK-TOU-FC-ET-HC-R100 | 2025.1448 | 647.4691 | 2672.6138 | 22713.7961 | 0.11766 | 0.94835 | 0.84991 | 0.89848 | 4.6839 | 9179.6942 | 7188 | 3 | 4 | 17820.2983 | 20031.41 | 20072.41 | 75357.2984 | 20.6857
424 | C-SOK-TOU-FC-ET-HC-R100 | 2772.9254 | 686.0834 | 3459.0087 | 22715.8463 | 0.15227 | 0.98706 | 0.84991 | 1.0368 | 4.6852 | 12235.1738 | 8913 | 3 | 4 | 17126.1336 | 20033.4165 | 20074.4165 | 88463.1336 | 19.7712
425 | C-SOK-TOU-FC-ET-HC-R100 | 3414.6779 | 683.1667 | 4097.8446 | 22742.8039 | 0.18018 | 1.0206 | 0.84986 | 1.0988 | 4.6834 | 14797.3228 | 9300 | 3 | 4 | 16574.3729 | 20057.483 | 20098.483 | 91007.373 | 17.3039
426 | C-SOK-TOU-FC-ET-HC-R100 | 3722.1171 | 680.0715 | 4402.1886 | 22744.1822 | 0.19355 | 1.0376 | 0.8499 | 1.1694 | 4.6865 | 16021.9211 | 9688 | 3 | 4 | 16300.7987 | 20058.747 | 20099.747 | 93837.7987 | 16.7503
427 | C-SOK-TOU-FC-ET-HC-R100 | 4139.3264 | 719.9793 | 4859.3057 | 22739.6095 | 0.21369 | 1.0642 | 0.8499 | 1.2537 | 4.6868 | 17757.2713 | 11500 | 3 | 4 | 15897.3783 | 20054.7597 | 20095.7597 | 107930.3784 | 18.0755
428 | C-SOK-TOU-FC-ET-HC-R100 | 4919.5283 | 716.4306 | 5635.9588 | 22770.1333 | 0.24752 | 1.1119 | 0.84984 | 1.3931 | 4.6869 | 20872.1641 | 12000 | 3 | 4 | 15224.8551 | 20082.2889 | 20123.2889 | 111257.8551 | 16.1702
429 | C-SOK-TOU-FC-ET-HC-R100 | 5258.0349 | 717.0855 | 5975.1204 | 22775.01 | 0.26235 | 1.1343 | 0.84982 | 1.4853 | 4.6858 | 22227.2822 | 12500 | 3 | 4 | 14924.1137 | 20086.5965 | 20127.5965 | 114957.1137 | 15.8707
430 | C-SOK-TOU-FC-ET-HC-R10 | 5112.0906 | 736.8719 | 5848.9625 | 22758.7068 | 0.257 | 1.1262 | 0.84987 | 1.4054 | 4.6863 | 21676.4823 | 13800 | 3 | 4 | 15028.8249 | 20071.8296 | 20112.8296 | 125461.8249 | 18.0116
431 | C-SOK-TOU-FC-ET-HC-R10 | 5952.2064 | 733.554 | 6685.7604 | 22789.3777 | 0.29337 | 1.1841 | 0.84981 | 1.6065 | 4.6862 | 25031.4156 | 14400 | 3 | 4 | 14302.3232 | 20099.4413 | 20140.4413 | 129535.3232 | 16.3624
432 | C-SOK-TOU-FC-ET-HC-R10 | 6356.7132 | 734.6908 | 7091.404 | 22793.0317 | 0.31112 | 1.2146 | 0.84979 | 1.7667 | 4.6862 | 26651.3374 | 15000 | 3 | 4 | 13940.9747 | 20102.8311 | 20143.8311 | 133973.9747 | 16.0518
433 | C-SOK-TOU-FC-ET-HC-R10 | 6073.9035 | 743.9367 | 6817.8402 | 22776.4379 | 0.29934 | 1.1942 | 0.84984 | 1.5595 | 4.6862 | 25535.5086 | 16388 | 3 | 4 | 14174.936 | 20087.8111 | 20128.8111 | 145311.936 | 18.3611
434 | C-SOK-TOU-FC-ET-HC-R10 | 6955.3255 | 745.0626 | 7700.3881 | 22800.9815 | 0.33772 | 1.2633 | 0.84977 | 1.849 | 4.6848 | 29063.0731 | 17100 | 3 | 4 | 13403.0711 | 20109.9016 | 20150.9016 | 150236.0711 | 16.8933
435 | C-SOK-TOU-FC-ET-HC-R10 | 7414.1676 | 747.6826 | 8161.8502 | 22803.514 | 0.35792 | 1.3031 | 0.84977 | 2.0694 | 4.6863 | 30902.808 | 17813 | 3 | 4 | 12990.9558 | 20112.3162 | 20153.3162 | 155527.9558 | 16.5863
436 | C-SOK-TOU-FC-ET-HC-R600 | 584.1626 | 830.8111 | 1414.9737 | 16577.7108 | 0.085354 | 0.94158 | 0.87795 | 0.85579 | 4.7364 | 3721.3355 | 6613 | 3 | 4 | 13430.5547 | 14454.7877 | 14495.7877 | 66367.5548 | 36.6592
437 | C-SOK-TOU-FC-ET-HC-R600 | 1019.7014 | 829.1249 | 1848.8263 | 16638.5165 | 0.11112 | 0.96869 | 0.87772 | 0.86504 | 4.7376 | 5460.6804 | 6900 | 3 | 4 | 13094.35 | 14509.5562 | 14550.5562 | 68327.3501 | 29.087
438 | C-SOK-TOU-FC-ET-HC-R600 | 1160.5873 | 826.4826 | 1987.0699 | 16656.5916 | 0.1193 | 0.97762 | 0.87764 | 0.87322 | 4.7376 | 6019.8201 | 7188 | 3 | 4 | 12985.4166 | 14525.8347 | 14566.8347 | 70522.4167 | 28.1598
439 | C-SOK-TOU-FC-ET-HC-R600 | 1925.8346 | 869.2742 | 2795.1088 | 16646.605 | 0.16791 | 1.0348 | 0.87774 | 1.0161 | 4.7402 | 9152.1286 | 8913 | 3 | 4 | 12262.1405 | 14516.9562 | 14557.9562 | 83599.1406 | 24.7007
440 | C-SOK-TOU-FC-ET-HC-R600 | 2434.8539 | 865.9501 | 3300.804 | 16701.0028 | 0.19764 | 1.073 | 0.87752 | 1.0734 | 4.7402 | 11182.6657 | 9300 | 3 | 4 | 11854.9085 | 14565.847 | 14606.847 | 86287.9086 | 21.7162
441 | C-SOK-TOU-FC-ET-HC-R600 | 2684.0589 | 863.6315 | 3547.6903 | 16710.2605 | 0.21231 | 1.0929 | 0.87745 | 1.1215 | 4.7391 | 12175.6213 | 9688 | 3 | 4 | 11640.3805 | 14574.2124 | 14615.2124 | 89177.3805 | 21.0171
442 | C-SOK-TOU-FC-ET-HC-R600 | 3102.1401 | 906.19 | 4008.3301 | 16690.9247 | 0.24015 | 1.133 | 0.87754 | 1.2124 | 4.7392 | 13918.8772 | 11500 | 3 | 4 | 11221.1406 | 14556.7807 | 14597.7807 | 103254.1407 | 22.118
443 | C-SOK-TOU-FC-ET-HC-R600 | 3751.8118 | 903.9604 | 4655.7723 | 16729.6044 | 0.2783 | 1.1927 | 0.87736 | 1.3554 | 4.7385 | 16513.848 | 12000 | 3 | 4 | 10672.5776 | 14591.5845 | 14632.5845 | 106705.5776 | 19.7761
444 | C-SOK-TOU-FC-ET-HC-R600 | 4074.7906 | 900.6188 | 4975.4094 | 16739.5801 | 0.29722 | 1.2248 | 0.87733 | 1.4493 | 4.7386 | 17800.1939 | 12500 | 3 | 4 | 10392.8165 | 14600.4994 | 14641.4994 | 110425.8165 | 19.2515
445 | C-SOK-TOU-FC-ET-HC-R60 | 3927.7864 | 921.4396 | 4849.226 | 16715.6815 | 0.2901 | 1.2126 | 0.87744 | 1.3573 | 4.7396 | 17246.8782 | 13800 | 3 | 4 | 10491.2238 | 14579.0954 | 14620.0954 | 120924.2239 | 21.9219
446 | C-SOK-TOU-FC-ET-HC-R60 | 4680.9362 | 919.232 | 5600.1682 | 16746.5944 | 0.33441 | 1.2932 | 0.87732 | 1.5773 | 4.7398 | 20255.798 | 14400 | 3 | 4 | 9842.5437 | 14606.9255 | 14647.9255 | 125075.5437 | 19.7186
447 | C-SOK-TOU-FC-ET-HC-R60 | 5055.8454 | 916.3618 | 5972.2072 | 16756.9014 | 0.3564 | 1.3374 | 0.8773 | 1.7556 | 4.7412 | 21750.6513 | 15000 | 3 | 4 | 9516.1844 | 14616.2623 | 14657.2623 | 129549.1844 | 19.2378
448 | C-SOK-TOU-FC-ET-HC-R60 | 4708.8446 | 925.178 | 5634.0226 | 16736.8352 | 0.33662 | 1.2976 | 0.87737 | 1.4903 | 4.7403 | 20377.3416 | 16388 | 3 | 4 | 9805.0568 | 14598.1237 | 14639.1237 | 140942.0569 | 22.4179
449 | C-SOK-TOU-FC-ET-HC-R60 | 5581.0867 | 927.1395 | 6508.2262 | 16764.8748 | 0.38821 | 1.4069 | 0.87724 | 1.8377 | 4.7399 | 23869.5793 | 17100 | 3 | 4 | 9044.1303 | 14623.392 | 14664.392 | 145877.1303 | 20.1611
450 | C-SOK-TOU-FC-ET-HC-R60 | 5984.5138 | 929.985 | 6914.4988 | 16775.534 | 0.41218 | 1.4642 | 0.87723 | 2.0466 | 4.7415 | 25488.0302 | 17813 | 3 | 4 | 8688.9778 | 14633.0312 | 14674.0312 | 151225.9778 | 19.7486
451 | C-SOK-TOU-FC-FP-HC-OFF0 | -5315.7295 | 1709.8928 | -3605.8367 | 5753.3397 | -0.62674 | 0.68944 | 1.1744 | 0.87382 | 4.669 | -18413.0965 | 4313 | 3 | 4 | 8168.7711 | 4410.5503 | 4451.5503 | 42705.7711 | -10.609
452 | C-SOK-TOU-FC-FP-HC-OFF0 | -5138.4405 | 1720.8414 | -3417.5992 | 5753.7216 | -0.59398 | 0.7037 | 1.1746 | 0.87206 | 4.6698 | -17685.6931 | 4600 | 3 | 4 | 8002.871 | 4410.7794 | 4451.7794 | 44835.8711 | -11.8165
453 | C-SOK-TOU-FC-FP-HC-OFF0 | -5026.5123 | 1723.9992 | -3302.5131 | 5753.8991 | -0.57396 | 0.7126 | 1.1745 | 0.8738 | 4.6691 | -17232.7173 | 4888 | 3 | 4 | 7900.3475 | 4410.8859 | 4451.8859 | 47037.3476 | -12.8949
454 | C-SOK-TOU-FC-FP-HC-OFF0 | -4223.2757 | 1744.7923 | -2478.4834 | 5753.1042 | -0.43081 | 0.784 | 1.1746 | 1.0044 | 4.6707 | -13985.1155 | 5813 | 3 | 4 | 7164.4817 | 4410.4089 | 4451.4089 | 53701.4817 | -19.8711
455 | C-SOK-TOU-FC-FP-HC-OFF0 | -3870.7256 | 1753.4616 | -2117.264 | 5753.6021 | -0.36799 | 0.81981 | 1.1744 | 1.0274 | 4.6685 | -12560.4664 | 6200 | 3 | 4 | 6842.2838 | 4410.7077 | 4451.7077 | 56475.2839 | -24.5711
456 | C-SOK-TOU-FC-FP-HC-OFF0 | -3706.5752 | 1753.3606 | -1953.2146 | 5752.9391 | -0.33952 | 0.83739 | 1.1746 | 1.0391 | 4.6704 | -11904.0332 | 6588 | 3 | 4 | 6694.2112 | 4410.3099 | 4451.3099 | 59431.2112 | -28.1484
457 | C-SOK-TOU-FC-FP-HC-OFF0 | -3216.6012 | 1774.1616 | -1442.4396 | 5752.8294 | -0.25074 | 0.89693 | 1.1747 | 1.166 | 4.6713 | -9909.4689 | 7500 | 3 | 4 | 6240.6882 | 4410.2441 | 4451.2441 | 66273.6883 | -42.8596
458 | C-SOK-TOU-FC-FP-HC-OFF0 | -2728.1469 | 1780.9184 | -947.2285 | 5752.7345 | -0.16466 | 0.96314 | 1.1746 | 1.2259 | 4.6708 | -7944.3903 | 8000 | 3 | 4 | 5796.9683 | 4410.1871 | 4451.1871 | 69829.9683 | -69.0211
459 | C-SOK-TOU-FC-FP-HC-OFF0 | -2448.7017 | 1781.4645 | -667.2372 | 5753.1677 | -0.11598 | 1.0052 | 1.1747 | 1.2748 | 4.6709 | -6825.6994 | 8500 | 3 | 4 | 5545.3999 | 4410.447 | 4451.447 | 73578.3999 | -103.6018
460 | C-SOK-TOU-FC-FP-HC-OFF | -2613.9449 | 1792.317 | -821.6279 | 5752.2567 | -0.14284 | 0.98173 | 1.1749 | 1.2799 | 4.6726 | -7468.5845 | 9000 | 3 | 4 | 5687.0607 | 4409.9005 | 4450.9005 | 77720.0607 | -89.1756
461 | C-SOK-TOU-FC-FP-HC-OFF | -1912.7702 | 1803.1629 | -109.6074 | 5752.7296 | -0.019053 | 1.1009 | 1.1748 | 1.4188 | 4.6718 | -4645.8095 | 9600 | 3 | 4 | 5049.7797 | 4410.1842 | 4451.1842 | 81882.7797 | -706.4452
462 | C-SOK-TOU-FC-FP-HC-OFF | -2306.7762 | 1797.5433 | -509.2328 | 5753.5233 | -0.088508 | 1.0305 | 1.1746 | 1.3315 | 4.67 | -6231.1991 | 9200 | 3 | 4 | 5408.233 | 4410.6604 | 4451.6604 | 79041.2331 | -146.4744
463 | C-SOK-TOU-FC-FP-HC-OFF | -2035.148 | 1801.0557 | -234.0923 | 5753.1223 | -0.04069 | 1.0779 | 1.1747 | 1.4004 | 4.671 | -5138.8325 | 10688 | 3 | 4 | 5161.4196 | 4410.4198 | 4451.4198 | 90698.4197 | -368.4315
464 | C-SOK-TOU-FC-FP-HC-OFF | -1235.0399 | 1813.185 | 578.1452 | 5752.4934 | 0.1005 | 1.2473 | 1.1748 | 1.6072 | 4.6721 | -1918.1844 | 11400 | 3 | 4 | 4433.6673 | 4410.0425 | 4451.0425 | 95666.6673 | 157.7729
465 | C-SOK-TOU-FC-FP-HC-OFF | -874.2522 | 1819.5205 | 945.2682 | 5752.7705 | 0.16432 | 1.3424 | 1.1747 | 1.7297 | 4.6713 | -464.4748 | 12113 | 3 | 4 | 4105.3235 | 4410.2087 | 4451.2087 | 101042.3235 | 102.1838
466 | C-SOK-TOU-FC-FP-HC-R100 | 595.9797 | 634.587 | 1230.5666 | 22646.7146 | 0.054338 | 0.88498 | 0.85008 | 0.77136 | 4.6869 | 3441.5636 | 4313 | 3 | 4 | 19053.892 | 19971.0259 | 20012.0259 | 53590.892 | 27.2873
467 | C-SOK-TOU-FC-FP-HC-R100 | 1094.1193 | 638.3942 | 1732.5136 | 22674.5513 | 0.076408 | 0.906 | 0.84995 | 0.76532 | 4.6822 | 5440.4676 | 4600 | 3 | 4 | 18628.3764 | 19996.1203 | 20037.1203 | 55461.3764 | 20.4467
468 | C-SOK-TOU-FC-FP-HC-R100 | 1312.7786 | 640.0258 | 1952.8044 | 22681.6956 | 0.086096 | 0.91561 | 0.84995 | 0.77035 | 4.6824 | 6317.8242 | 4888 | 3 | 4 | 18436.9957 | 20002.5119 | 20043.5119 | 57573.9958 | 19.2188
469 | C-SOK-TOU-FC-FP-HC-R100 | 1853.4252 | 659.9921 | 2513.4173 | 22687.3502 | 0.11078 | 0.94106 | 0.84997 | 0.86911 | 4.6855 | 8513.6876 | 5813 | 3 | 4 | 17943.6568 | 20007.7347 | 20048.7347 | 64480.6568 | 17.6779
470 | C-SOK-TOU-FC-FP-HC-R100 | 2477.1286 | 661.8801 | 3139.0087 | 22710.9654 | 0.13822 | 0.97097 | 0.84992 | 0.88239 | 4.6845 | 11011.648 | 6200 | 3 | 4 | 17402.3834 | 20028.9272 | 20069.9272 | 67035.3835 | 14.9619
471 | C-SOK-TOU-FC-FP-HC-R100 | 2693.9409 | 664.8142 | 3358.7551 | 22716.7484 | 0.14785 | 0.98195 | 0.84991 | 0.88706 | 4.685 | 11883.7874 | 6588 | 3 | 4 | 17210.7597 | 20034.195 | 20075.195 | 69947.7597 | 14.8485
472 | C-SOK-TOU-FC-FP-HC-R100 | 2978.1773 | 683.3805 | 3661.5578 | 22717.806 | 0.16118 | 0.99756 | 0.84992 | 0.96377 | 4.6856 | 13051.6767 | 7500 | 3 | 4 | 16944.6917 | 20035.0796 | 20076.0796 | 76977.6917 | 15.5403
473 | C-SOK-TOU-FC-FP-HC-R100 | 3722.2136 | 682.8032 | 4405.0168 | 22738.1762 | 0.19373 | 1.0378 | 0.84989 | 1.0095 | 4.6858 | 16026.8598 | 8000 | 3 | 4 | 16293.7802 | 20053.4544 | 20094.4544 | 80326.7802 | 13.6736
474 | C-SOK-TOU-FC-FP-HC-R100 | 4072.4563 | 688.0232 | 4760.4795 | 22741.8615 | 0.20933 | 1.0582 | 0.84983 | 1.0481 | 4.6816 | 17436.5307 | 8500 | 3 | 4 | 15978.595 | 20056.6196 | 20097.6196 | 84011.595 | 13.426
475 | C-SOK-TOU-FC-FP-HC-R10 | 3770.7932 | 694.5316 | 4465.3248 | 22736.5894 | 0.19639 | 1.0412 | 0.84989 | 1.0261 | 4.686 | 16240.7253 | 9000 | 3 | 4 | 16241.6397 | 20052.0725 | 20093.0725 | 88274.6398 | 15.2691
476 | C-SOK-TOU-FC-FP-HC-R10 | 4621.2134 | 697.2743 | 5318.4877 | 22758.7653 | 0.23369 | 1.0919 | 0.84988 | 1.1006 | 4.6876 | 19646.9775 | 9600 | 3 | 4 | 15494.4954 | 20071.9521 | 20112.9521 | 92327.4954 | 13.578
477 | C-SOK-TOU-FC-FP-HC-R10 | 5075.896 | 704.3809 | 5780.2769 | 22762.9608 | 0.25393 | 1.1215 | 0.84982 | 1.1696 | 4.6835 | 21477.5523 | 10200 | 3 | 4 | 15084.6845 | 20075.6194 | 20116.6194 | 96717.6845 | 13.2521
478 | C-SOK-TOU-FC-FP-HC-R10 | 4645.6252 | 704.5639 | 5350.189 | 22751.5556 | 0.23516 | 1.0941 | 0.8499 | 1.1261 | 4.6884 | 19756.7738 | 10688 | 3 | 4 | 15461.7075 | 20065.5084 | 20106.5084 | 100998.7075 | 15.1195
479 | C-SOK-TOU-FC-FP-HC-R10 | 5522.2689 | 703.8377 | 6226.1066 | 22775.5915 | 0.27337 | 1.1515 | 0.84984 | 1.1948 | 4.6878 | 23262.1383 | 11400 | 3 | 4 | 14694.8933 | 20087.2379 | 20128.2379 | 105927.8933 | 13.7806
480 | C-SOK-TOU-FC-FP-HC-R10 | 6003.8046 | 706.8526 | 6710.6572 | 22779.3619 | 0.29459 | 1.1861 | 0.84982 | 1.2795 | 4.6869 | 25193.3061 | 12113 | 3 | 4 | 14263.0464 | 20090.5821 | 20131.5821 | 111200.0464 | 13.5707
481 | C-SOK-TOU-FC-FP-HC-R600 | -159.0457 | 816.3472 | 657.3015 | 16528.0604 | 0.039769 | 0.89706 | 0.87818 | 0.77745 | 4.7377 | 724.3958 | 4313 | 3 | 4 | 14063.4992 | 14410.1664 | 14451.1664 | 48600.4993 | 51.9538
482 | C-SOK-TOU-FC-FP-HC-R600 | 270.0098 | 819.7709 | 1089.7807 | 16574.4164 | 0.065751 | 0.92182 | 0.87795 | 0.76788 | 4.7359 | 2446.3239 | 4600 | 3 | 4 | 13716.9622 | 14451.8335 | 14492.8335 | 50549.9623 | 33.0866
483 | C-SOK-TOU-FC-FP-HC-R600 | 414.3233 | 820.6809 | 1235.0042 | 16590.7373 | 0.074439 | 0.9304 | 0.87786 | 0.76663 | 4.7354 | 3025.0948 | 4888 | 3 | 4 | 13601.2313 | 14466.5308 | 14507.5308 | 52738.2314 | 30.9559
484 | C-SOK-TOU-FC-FP-HC-R600 | 950.1319 | 843.9254 | 1794.0573 | 16594.211 | 0.10811 | 0.96564 | 0.87796 | 0.86226 | 4.7399 | 5207.0701 | 5813 | 3 | 4 | 13108.2629 | 14469.7369 | 14510.7369 | 59645.263 | 25.1578
485 | C-SOK-TOU-FC-FP-HC-R600 | 1456.0619 | 844.0032 | 2300.0651 | 16640.422 | 0.13822 | 0.99911 | 0.87768 | 0.87338 | 4.7363 | 7230.9195 | 6200 | 3 | 4 | 12694.388 | 14511.2457 | 14552.2457 | 62327.3881 | 20.7712
486 | C-SOK-TOU-FC-FP-HC-R600 | 1655.178 | 845.5546 | 2500.7326 | 16656.4668 | 0.15014 | 1.013 | 0.87759 | 0.88102 | 4.7354 | 8029.9697 | 6588 | 3 | 4 | 12528.6833 | 14525.6762 | 14566.6762 | 65265.6833 | 20.2737
487 | C-SOK-TOU-FC-FP-HC-R600 | 1927.2037 | 865.1548 | 2792.3585 | 16641.1661 | 0.1678 | 1.0347 | 0.87775 | 0.95469 | 4.7395 | 9150.7395 | 7500 | 3 | 4 | 12258.4028 | 14511.979 | 14552.979 | 72291.4028 | 20.6773
488 | C-SOK-TOU-FC-FP-HC-R600 | 2551.5172 | 865.3724 | 3416.8895 | 16688.5116 | 0.20475 | 1.0825 | 0.87752 | 0.99941 | 4.738 | 11648.3559 | 8000 | 3 | 4 | 11739.0161 | 14554.605 | 14595.605 | 75772.0161 | 17.9041
489 | C-SOK-TOU-FC-FP-HC-R600 | 2767.9876 | 868.4669 | 3636.4545 | 16699.6419 | 0.21776 | 1.1005 | 0.87745 | 1.0121 | 4.7375 | 12519.3953 | 8500 | 3 | 4 | 11552.3908 | 14564.6598 | 14605.6598 | 79585.3908 | 17.869
490 | C-SOK-TOU-FC-FP-HC-R60 | 2608.1737 | 877.7042 | 3485.8779 | 16671.698 | 0.20909 | 1.0886 | 0.8776 | 1.0234 | 4.7388 | 11895.5351 | 9000 | 3 | 4 | 11665.5474 | 14539.5263 | 14580.5263 | 83698.5475 | 19.828
491 | C-SOK-TOU-FC-FP-HC-R60 | 3327.5673 | 881.8524 | 4209.4197 | 16716.0244 | 0.25182 | 1.1506 | 0.87745 | 1.0975 | 4.7396 | 14780.0232 | 9600 | 3 | 4 | 11055.3965 | 14579.3185 | 14620.3185 | 87888.3965 | 17.4057
492 | C-SOK-TOU-FC-FP-HC-R60 | 3649.881 | 883.1856 | 4533.0666 | 16726.846 | 0.27101 | 1.1808 | 0.8774 | 1.1487 | 4.7393 | 16071.5 | 10200 | 3 | 4 | 10774.2568 | 14589.0611 | 14630.0611 | 92407.2568 | 17.1577
493 | C-SOK-TOU-FC-FP-HC-R60 | 3300.9251 | 884.2879 | 4185.213 | 16701.1339 | 0.25059 | 1.1487 | 0.87747 | 1.1082 | 4.7379 | 14677.5136 | 10688 | 3 | 4 | 11064.5247 | 14565.9301 | 14606.9301 | 96601.5248 | 19.5915
494 | C-SOK-TOU-FC-FP-HC-R60 | 4072.6641 | 889.8929 | 4962.557 | 16735.9698 | 0.29652 | 1.2236 | 0.87734 | 1.2015 | 4.7389 | 17773.8112 | 11400 | 3 | 4 | 10398.0068 | 14597.3402 | 14638.3402 | 101631.0068 | 17.5298
495 | C-SOK-TOU-FC-FP-HC-R60 | 4471.7761 | 884.4527 | 5356.2288 | 16745.2439 | 0.31987 | 1.2656 | 0.87735 | 1.2733 | 4.7409 | 19361.1922 | 12113 | 3 | 4 | 10050.4669 | 14605.737 | 14646.737 | 106987.4669 | 17.2399
496 | C-SOK-TOU-FC-FP-WC-OFF0 | -8264.1693 | 2672.909 | -5591.2604 | 9017.7936 | -0.62003 | 0.69916 | 1.1662 | 0.84731 | 4.5919 | -28601.8291 | 6750 | 3 | 4 | 12782.4285 | 6928.2611 | 6969.2611 | 66815.4286 | -10.7035
497 | C-SOK-TOU-FC-FP-WC-OFF0 | -7992.5658 | 2679.3719 | -5313.1939 | 9017.9787 | -0.58918 | 0.71272 | 1.1661 | 0.84592 | 4.5917 | -27504.6433 | 7200 | 3 | 4 | 12534.2225 | 6928.3721 | 6969.3721 | 70167.2226 | -11.8945
498 | C-SOK-TOU-FC-FP-WC-OFF0 | -7840.9971 | 2681.8937 | -5159.1034 | 9017.9924 | -0.57209 | 0.72047 | 1.1661 | 0.84668 | 4.5916 | -26894.1656 | 7650 | 3 | 4 | 12396.3128 | 6928.3804 | 6969.3804 | 73629.3128 | -12.9208
499 | C-SOK-TOU-FC-FP-WC-OFF0 | -6728.9127 | 2683.2038 | -4045.7089 | 9017.7841 | -0.44864 | 0.78188 | 1.1662 | 0.95068 | 4.5918 | -22443.6446 | 9175 | 3 | 4 | 11394.5622 | 6928.2553 | 6969.2553 | 84827.5623 | -19.2447
500 | C-SOK-TOU-FC-FP-WC-OFF0 | -6265.5426 | 2689.7345 | -3575.8081 | 9017.8674 | -0.39652 | 0.81099 | 1.1661 | 0.96193 | 4.5912 | -20579.2797 | 9825 | 3 | 4 | 10973.6679 | 6928.3053 | 6969.3053 | 89606.6679 | -23.1101
501 | C-SOK-TOU-FC-FP-WC-OFF0 | -6040.6738 | 2691.6661 | -3349.0077 | 9017.1248 | -0.37141 | 0.82605 | 1.1664 | 0.96928 | 4.5934 | -19676.5851 | 10425 | 3 | 4 | 10769.6931 | 6927.8598 | 6968.8598 | 94202.6931 | -26.0477
502 | C-SOK-TOU-FC-FP-WC-OFF0 | -5431.942 | 2698.0157 | -2733.9263 | 9018.3333 | -0.30315 | 0.86915 | 1.1661 | 1.0595 | 4.5915 | -17231.0753 | 11650 | 3 | 4 | 10218.7204 | 6928.5849 | 6969.5849 | 103451.7205 | -35.2907
503 | C-SOK-TOU-FC-FP-WC-OFF0 | -4823.8785 | 2702.4886 | -2121.3899 | 9018.3338 | -0.23523 | 0.91694 | 1.1661 | 1.0897 | 4.5915 | -14791.3662 | 12400 | 3 | 4 | 9668.7946 | 6928.5852 | 6969.5852 | 108901.7946 | -48.0497
504 | C-SOK-TOU-FC-FP-WC-OFF0 | -4505.0461 | 2705.4324 | -1799.6136 | 9018.1416 | -0.19955 | 0.94422 | 1.1661 | 1.1121 | 4.5916 | -13511.1302 | 13200 | 3 | 4 | 9379.9764 | 6928.4698 | 6969.4698 | 115012.9764 | -60.0371
505 | C-SOK-TOU-FC-FP-WC-OFF | -4428.1308 | 2699.8922 | -1728.2386 | 9018.5467 | -0.19163 | 0.95034 | 1.1659 | 1.1611 | 4.5902 | -13212.7028 | 14250 | 3 | 4 | 9314.3079 | 6928.7129 | 6969.7129 | 123347.308 | -67.3388
506 | C-SOK-TOU-FC-FP-WC-OFF | -3481.1634 | 2704.6663 | -776.4971 | 9017.9335 | -0.086106 | 1.0427 | 1.166 | 1.2416 | 4.5907 | -9416.8764 | 15200 | 3 | 4 | 8458.821 | 6928.345 | 6969.345 | 130091.821 | -158.5614
507 | C-SOK-TOU-FC-FP-WC-OFF | -3103.3489 | 2705.2712 | -398.0777 | 9017.772 | -0.044144 | 1.0847 | 1.1661 | 1.2857 | 4.5913 | -7904.6103 | 16150 | 3 | 4 | 8118.338 | 6928.2481 | 6969.2481 | 137351.338 | -327.5292
508 | C-SOK-TOU-FC-FP-WC-OFF | -3532.7392 | 2702.5402 | -830.1991 | 9018.3695 | -0.092056 | 1.0372 | 1.1662 | 1.2643 | 4.5916 | -9626.7234 | 16675 | 3 | 4 | 8506.7615 | 6928.6066 | 6969.6066 | 141939.7615 | -162.5757
509 | C-SOK-TOU-FC-FP-WC-OFF | -2307.5982 | 2704.848 | 397.2497 | 9017.0622 | 0.044055 | 1.1848 | 1.1661 | 1.4198 | 4.592 | -4722.313 | 17825 | 3 | 4 | 7401.983 | 6927.8222 | 6968.8222 | 150034.983 | 360.1416
510 | C-SOK-TOU-FC-FP-WC-OFF | -1892.6472 | 2706.8357 | 814.1885 | 9017.5591 | 0.090289 | 1.245 | 1.1661 | 1.4825 | 4.5916 | -3059.1961 | 18925 | 3 | 4 | 7027.6637 | 6928.1203 | 6969.1203 | 158460.6637 | 186.0645
511 | C-SOK-TOU-FC-FP-WC-R100 | 931.9114 | 1025.5265 | 1957.4378 | 35013.6162 | 0.055905 | 0.89137 | 0.85007 | 0.71277 | 4.6038 | 5436.8563 | 6750 | 3 | 4 | 29470.164 | 30915.0738 | 30956.0738 | 83503.1641 | 26.8448
512 | C-SOK-TOU-FC-FP-WC-R100 | 1739.5002 | 1022.1023 | 2761.6025 | 35067.8302 | 0.07875 | 0.91344 | 0.85003 | 0.71317 | 4.6051 | 8661.5045 | 7200 | 3 | 4 | 28794.2574 | 30963.9437 | 31004.9437 | 86427.2575 | 20.0689
513 | C-SOK-TOU-FC-FP-WC-R100 | 2099.2316 | 1021.8945 | 3121.1261 | 35083.0763 | 0.088964 | 0.92367 | 0.85001 | 0.71771 | 4.6052 | 10100.0839 | 7650 | 3 | 4 | 28484.3191 | 30977.635 | 31018.635 | 89717.3191 | 18.8069
514 | C-SOK-TOU-FC-FP-WC-R100 | 2773.5639 | 1033.144 | 3806.7079 | 35089.9034 | 0.10848 | 0.9439 | 0.85001 | 0.78393 | 4.6056 | 12816.1622 | 9175 | 3 | 4 | 27876.8065 | 30983.7691 | 31024.7691 | 101309.8066 | 18.4635
515 | C-SOK-TOU-FC-FP-WC-R100 | 3809.2738 | 1032.9088 | 4842.1826 | 35142.3381 | 0.13779 | 0.97591 | 0.84994 | 0.79465 | 4.6048 | 16958.6098 | 9825 | 3 | 4 | 26992.0049 | 31030.9675 | 31071.9675 | 105625.0049 | 15.3966
516 | C-SOK-TOU-FC-FP-WC-R100 | 4206.7013 | 1033.6883 | 5240.3896 | 35149.0346 | 0.14909 | 0.98888 | 0.84995 | 0.80277 | 4.6055 | 18549.619 | 10425 | 3 | 4 | 26639.8463 | 31036.95 | 31077.95 | 110072.8463 | 15.0742
517 | C-SOK-TOU-FC-FP-WC-R100 | 4476.6291 | 1042.4575 | 5519.0866 | 35150.0086 | 0.15702 | 0.99819 | 0.84995 | 0.85971 | 4.6065 | 19643.9456 | 11650 | 3 | 4 | 26392.5654 | 31037.9162 | 31078.9162 | 119625.5654 | 16.0437
518 | C-SOK-TOU-FC-FP-WC-R100 | 5565.287 | 1045.661 | 6610.948 | 35187.9414 | 0.18788 | 1.0361 | 0.84991 | 0.88871 | 4.6062 | 24003.9165 | 12400 | 3 | 4 | 25444.9511 | 31072.0252 | 31113.0252 | 124677.9511 | 14.153
519 | C-SOK-TOU-FC-FP-WC-R100 | 6131.8309 | 1048.087 | 7179.9179 | 35197.2954 | 0.20399 | 1.0571 | 0.84991 | 0.91466 | 4.6064 | 26274.1353 | 13200 | 3 | 4 | 24941.9052 | 31080.3085 | 31121.3085 | 130574.9052 | 13.8516
520 | C-SOK-TOU-FC-FP-WC-R10 | 5847.869 | 1040.3593 | 6888.2283 | 35188.2139 | 0.19575 | 1.0463 | 0.84993 | 0.92003 | 4.6074 | 25125.4083 | 14250 | 3 | 4 | 25194.0439 | 31072.2394 | 31113.2394 | 139227.044 | 15.6954
521 | C-SOK-TOU-FC-FP-WC-R10 | 7223.7366 | 1045.7048 | 8269.4414 | 35234.4118 | 0.2347 | 1.0994 | 0.84988 | 0.98472 | 4.6071 | 30637.7877 | 15200 | 3 | 4 | 23994.0795 | 31113.7666 | 31154.7666 | 145627.0795 | 13.8428
522 | C-SOK-TOU-FC-FP-WC-R10 | 7892.5113 | 1047.1499 | 8939.6612 | 35243.3872 | 0.25365 | 1.1274 | 0.84987 | 1.0207 | 4.607 | 33315.2951 | 16150 | 3 | 4 | 23399.3907 | 31121.8413 | 31162.8413 | 152632.3907 | 13.5877
523 | C-SOK-TOU-FC-FP-WC-R10 | 7030.221 | 1036.3632 | 8066.5841 | 35216.8413 | 0.22905 | 1.0914 | 0.84989 | 0.9876 | 4.6069 | 29848.1558 | 16675 | 3 | 4 | 24158.1523 | 31098.0603 | 31139.0603 | 157591.1523 | 15.676
524 | C-SOK-TOU-FC-FP-WC-R10 | 8570.3121 | 1044.6204 | 9614.9325 | 35265.049 | 0.27265 | 1.1567 | 0.84982 | 1.0829 | 4.606 | 36022.2824 | 17825 | 3 | 4 | 22810.4758 | 31141.4305 | 31182.4305 | 165443.4758 | 13.9638
525 | C-SOK-TOU-FC-FP-WC-R10 | 9298.9489 | 1049.0119 | 10347.9608 | 35276.0572 | 0.29334 | 1.1906 | 0.84982 | 1.1582 | 4.6066 | 38944.1489 | 18925 | 3 | 4 | 22161.9269 | 31151.2992 | 31192.2992 | 173594.9269 | 13.7614
526 | C-SOK-TOU-FC-FP-WC-R600 | -598.6889 | 1275.0317 | 676.3428 | 25222.0543 | 0.026816 | 0.8921 | 0.87919 | 0.70435 | 4.6615 | -269.7027 | 6750 | 3 | 4 | 21794.4546 | 22009.5431 | 22050.5431 | 75827.4546 | 79.5113
527 | C-SOK-TOU-FC-FP-WC-R600 | 24.7767 | 1271.9864 | 1296.7631 | 25310.3691 | 0.051234 | 0.91484 | 0.87894 | 0.70014 | 4.6613 | 2219.084 | 7200 | 3 | 4 | 21314.6276 | 22089.0048 | 22130.0048 | 78947.6277 | 43.815
528 | C-SOK-TOU-FC-FP-WC-R600 | 254.5235 | 1272.1471 | 1526.6706 | 25336.7874 | 0.060255 | 0.92356 | 0.87887 | 0.70115 | 4.661 | 3138.3393 | 7650 | 3 | 4 | 21131.4666 | 22112.7139 | 22153.7139 | 82364.4666 | 39.4393
529 | C-SOK-TOU-FC-FP-WC-R600 | 969.8283 | 1283.0462 | 2252.8745 | 25330.3065 | 0.08894 | 0.95269 | 0.87893 | 0.76547 | 4.6624 | 6017.7234 | 9175 | 3 | 4 | 20475.3236 | 22106.8821 | 22147.8821 | 93908.3236 | 31.8528
530 | C-SOK-TOU-FC-FP-WC-R600 | 1784.6537 | 1282.4987 | 3067.1524 | 25417.8286 | 0.12067 | 0.98681 | 0.87866 | 0.77783 | 4.6617 | 9276.1126 | 9825 | 3 | 4 | 19821.1487 | 22185.7204 | 22226.7204 | 98454.1487 | 24.8528
531 | C-SOK-TOU-FC-FP-WC-R600 | 2096.9654 | 1284.409 | 3381.3745 | 25439.8352 | 0.13292 | 1.0007 | 0.87862 | 0.78193 | 4.6627 | 10528.5435 | 10425 | 3 | 4 | 19558.7525 | 22205.5442 | 22246.5442 | 102991.7525 | 23.8794
532 | C-SOK-TOU-FC-FP-WC-R600 | 2327.5917 | 1291.3783 | 3618.97 | 25414.9832 | 0.1424 | 1.0116 | 0.87849 | 0.82265 | 4.6554 | 11462.6639 | 11650 | 3 | 4 | 19324.5005 | 22183.0887 | 22224.0887 | 112557.5006 | 24.9611
533 | C-SOK-TOU-FC-FP-WC-R600 | 3254.1687 | 1296.5855 | 4550.7542 | 25484.414 | 0.17857 | 1.0562 | 0.87851 | 0.86096 | 4.6625 | 15177.6507 | 12400 | 3 | 4 | 18549.9512 | 22245.569 | 22286.569 | 117782.9512 | 20.9847
534 | C-SOK-TOU-FC-FP-WC-R600 | 3725.0122 | 1297.317 | 5022.3292 | 25502.8682 | 0.19693 | 1.0802 | 0.87839 | 0.88211 | 4.66 | 17062.2439 | 13200 | 3 | 4 | 18142.3447 | 22262.1649 | 22303.1649 | 123775.3447 | 20.2042
535 | C-SOK-TOU-FC-FP-WC-R60 | 3539.9153 | 1293.8494 | 4833.7647 | 25466.28 | 0.18981 | 1.0709 | 0.87857 | 0.89691 | 4.6631 | 16316.0769 | 14250 | 3 | 4 | 18278.1517 | 22229.3025 | 22270.3025 | 132311.1518 | 22.765
536 | C-SOK-TOU-FC-FP-WC-R60 | 4626.1366 | 1297.9911 | 5924.1277 | 25528.6956 | 0.23206 | 1.1297 | 0.87839 | 0.95195 | 4.6627 | 20667.8647 | 15200 | 3 | 4 | 17354.1886 | 22285.4106 | 22326.4106 | 138987.1886 | 19.6925
537 | C-SOK-TOU-FC-FP-WC-R60 | 5210.0087 | 1302.3351 | 6512.3437 | 25547.7288 | 0.25491 | 1.1642 | 0.87833 | 0.99306 | 4.6625 | 23010.5931 | 16150 | 3 | 4 | 16843.26 | 22302.5808 | 22343.5808 | 146076.26 | 18.9997
538 | C-SOK-TOU-FC-FP-WC-R60 | 4497.9523 | 1290.9304 | 5788.8826 | 25505.8859 | 0.22696 | 1.1223 | 0.87846 | 0.95524 | 4.6626 | 20143.3596 | 16675 | 3 | 4 | 17453.257 | 22264.8782 | 22305.8782 | 150886.257 | 22.2116
539 | C-SOK-TOU-FC-FP-WC-R60 | 5829.9408 | 1297.6548 | 7127.5956 | 25559.2819 | 0.27887 | 1.2029 | 0.87831 | 1.0522 | 4.6627 | 25482.5212 | 17825 | 3 | 4 | 16298.507 | 22312.9544 | 22353.9544 | 158931.507 | 19.1618
540 | C-SOK-TOU-FC-FP-WC-R60 | 6490.4495 | 1301.1086 | 7791.5581 | 25575.7746 | 0.30465 | 1.2474 | 0.87826 | 1.1106 | 4.6622 | 28130.3123 | 18925 | 3 | 4 | 15716.7842 | 22327.7606 | 22368.7606 | 167149.7842 | 18.5818
541 | C-SOK-TOU-CC-FP-WC-R600 | 1337.0118 | 1652.3902 | 2989.4019 | 33735.4968 | 0.088613 | 0.96032 | 0.8835 | 0.93531 | 5.1936 | 8102.0307 | 8650 | 3 | 4 | 27389.705 | 29571.7553 | 29612.7553 | 96622.7051 | 22.4158
542 | C-SOK-TOU-CC-FP-WC-R600 | 2084.6711 | 1648.3154 | 3732.9865 | 33843.6897 | 0.1103 | 0.98352 | 0.88329 | 0.93089 | 5.1944 | 11085.8769 | 9200 | 3 | 4 | 26816.5849 | 29669.0852 | 29710.0852 | 100449.5849 | 18.9498
543 | C-SOK-TOU-CC-FP-WC-R600 | 2398.2431 | 1647.4815 | 4045.7245 | 33878.0178 | 0.11942 | 0.99364 | 0.88322 | 0.93299 | 5.1949 | 12338.7747 | 9800 | 3 | 4 | 26565.8174 | 29700.0211 | 29741.0211 | 104998.8174 | 18.6018
544 | C-SOK-TOU-CC-FP-WC-R600 | 3301.2128 | 1652.1737 | 4953.3865 | 33884.5356 | 0.14618 | 1.0246 | 0.88306 | 1.0228 | 5.1895 | 15958.4741 | 12000 | 3 | 4 | 25756.2642 | 29705.9603 | 29746.9603 | 121789.2643 | 18.5817
545 | C-SOK-TOU-CC-FP-WC-R600 | 4356.5612 | 1652.3284 | 6008.8896 | 33991.3699 | 0.17678 | 1.0626 | 0.88296 | 1.0641 | 5.1942 | 20180.1254 | 12800 | 3 | 4 | 24902.4244 | 29802.0208 | 29843.0208 | 127335.4244 | 16.2247
546 | C-SOK-TOU-CC-FP-WC-R600 | 4876.9915 | 1652.3326 | 6529.3241 | 34012.2471 | 0.19197 | 1.0825 | 0.88288 | 1.0871 | 5.193 | 22261.8536 | 13600 | 3 | 4 | 24452.8761 | 29820.8601 | 29861.8601 | 133285.8761 | 15.8399
547 | C-SOK-TOU-CC-FP-WC-R600 | 4954.2362 | 1650.6382 | 6604.8744 | 33970.4528 | 0.19443 | 1.0859 | 0.88297 | 1.1324 | 5.1928 | 22568.0085 | 15175 | 3 | 4 | 24346.7243 | 29783.2116 | 29824.2116 | 145779.7243 | 17.5561
548 | C-SOK-TOU-CC-FP-WC-R600 | 6227.1726 | 1650.8907 | 7878.0633 | 34067.8711 | 0.23125 | 1.1377 | 0.88278 | 1.2006 | 5.194 | 27660.1748 | 16225 | 3 | 4 | 23288.6516 | 29870.914 | 29911.914 | 153121.6516 | 15.6396
549 | C-SOK-TOU-CC-FP-WC-R600 | 6943.6465 | 1650.2873 | 8593.9338 | 34087.6368 | 0.25211 | 1.1693 | 0.88272 | 1.2572 | 5.1933 | 30525.0648 | 17225 | 3 | 4 | 22661.9735 | 29888.6898 | 29929.6898 | 160494.9735 | 15.1927
550 | C-SOK-TOU-CC-FP-WC-R60 | 6475.7337 | 1644.2768 | 8120.0105 | 34042.7954 | 0.23852 | 1.1487 | 0.88291 | 1.255 | 5.1967 | 28643.3962 | 18400 | 3 | 4 | 23046.2602 | 29848.2519 | 29889.2519 | 170279.2602 | 17.2894
551 | C-SOK-TOU-CC-FP-WC-R60 | 7933.3707 | 1643.3472 | 9576.7179 | 34111.1434 | 0.28075 | 1.2159 | 0.88271 | 1.3857 | 5.1949 | 34472.3948 | 19600 | 3 | 4 | 21796.562 | 29909.8549 | 29950.8549 | 178629.562 | 15.525
552 | C-SOK-TOU-CC-FP-WC-R60 | 8825.066 | 1644.0027 | 10469.0686 | 34132.6467 | 0.30672 | 1.2614 | 0.8827 | 1.4876 | 5.1961 | 38040.2683 | 20850 | 3 | 4 | 21012.9634 | 29929.1417 | 29970.1417 | 187845.9634 | 15.0802
553 | C-SOK-TOU-CC-FP-WC-R60 | 7701.2838 | 1629.8231 | 9331.1069 | 34088.8219 | 0.27373 | 1.2043 | 0.88281 | 1.3591 | 5.1965 | 33521.5071 | 21750 | 3 | 4 | 21993.384 | 29889.6789 | 29930.6789 | 196026.384 | 17.8002
554 | C-SOK-TOU-CC-FP-WC-R60 | 9419.0076 | 1628.9604 | 11047.968 | 34150.6697 | 0.32351 | 1.2927 | 0.8827 | 1.5515 | 5.1974 | 40390.9643 | 23200 | 3 | 4 | 20503.6701 | 29945.3563 | 29986.3563 | 206136.6701 | 15.9441
555 | C-SOK-TOU-CC-FP-WC-R60 | 10418.5954 | 1627.1716 | 12045.767 | 34165.8356 | 0.35257 | 1.3506 | 0.88258 | 1.7065 | 5.1942 | 44386.3341 | 24650 | 3 | 4 | 19618.8487 | 29959.0708 | 30000.0708 | 216851.8487 | 15.5118
556 | C-SOK-TOU-FC-ET-WC-OFF0 | -6264.0921 | 2646.8421 | -3617.25 | 9018.1879 | -0.40111 | 0.80844 | 1.1662 | 1.0176 | 4.5921 | -20644.9648 | 10350 | 3 | 4 | 10998.3018 | 6928.4976 | 6969.4976 | 93831.3019 | -24.0132
557 | C-SOK-TOU-FC-ET-WC-OFF0 | -5961.296 | 2646.8601 | -3314.4359 | 9017.6458 | -0.36755 | 0.82829 | 1.1662 | 1.0255 | 4.5924 | -19433.7506 | 10800 | 3 | 4 | 10725.4628 | 6928.1723 | 6969.1723 | 97158.4629 | -27.2111
558 | C-SOK-TOU-FC-ET-WC-OFF0 | -5776.5088 | 2646.7015 | -3129.8073 | 9017.392 | -0.34709 | 0.84088 | 1.1662 | 1.0357 | 4.5925 | -18694.8661 | 11250 | 3 | 4 | 10559.0998 | 6928.0201 | 6969.0201 | 100592.0998 | -29.9134
559 | C-SOK-TOU-FC-ET-WC-OFF0 | -4309.1709 | 2658.759 | -1650.4119 | 9017.6233 | -0.18302 | 0.95752 | 1.1663 | 1.2287 | 4.5927 | -12805.4185 | 14075 | 3 | 4 | 9231.4451 | 6928.1589 | 6969.1589 | 121864.4452 | -69.6161
560 | C-SOK-TOU-FC-ET-WC-OFF0 | -3671.346 | 2661.263 | -1010.083 | 9018.028 | -0.11201 | 1.0186 | 1.1662 | 1.2913 | 4.5923 | -10249.9458 | 14725 | 3 | 4 | 8656.1692 | 6928.4017 | 6969.4017 | 126489.1692 | -118.3267
561 | C-SOK-TOU-FC-ET-WC-OFF0 | -3485.0357 | 2660.3171 | -824.7186 | 9018.2561 | -0.09145 | 1.0377 | 1.1661 | 1.316 | 4.5915 | -9506.281 | 15325 | 3 | 4 | 8489.2006 | 6928.5385 | 6969.5385 | 131122.2006 | -150.5394
562 | C-SOK-TOU-FC-ET-WC-OFF0 | -2609.9788 | 2675.904 | 65.9252 | 9017.9031 | 0.0073105 | 1.1411 | 1.1662 | 1.4919 | 4.5922 | -5980.0751 | 17850 | 3 | 4 | 7692.0354 | 6928.3267 | 6969.3267 | 150525.0355 | 2177.5529
563 | C-SOK-TOU-FC-ET-WC-OFF0 | -1952.7654 | 2675.8673 | 723.102 | 9017.8826 | 0.080185 | 1.2315 | 1.1663 | 1.6035 | 4.5925 | -3351.2826 | 18600 | 3 | 4 | 7100.592 | 6928.3145 | 6969.3145 | 155933.592 | 206.0073
564 | C-SOK-TOU-FC-ET-WC-OFF0 | -1475.42 | 2676.9116 | 1201.4916 | 9017.7675 | 0.13324 | 1.3067 | 1.1661 | 1.7185 | 4.5917 | -1440.1607 | 19400 | 3 | 4 | 6670.2863 | 6928.2454 | 6969.2454 | 161903.2863 | 128.9514
565 | C-SOK-TOU-FC-ET-WC-OFF | -1167.2492 | 2690.9757 | 1523.7265 | 9017.5011 | 0.16897 | 1.363 | 1.1662 | 1.8265 | 4.5922 | -184.0372 | 21850 | 3 | 4 | 6384.2614 | 6928.0855 | 6969.0855 | 181217.2615 | 114.3566
566 | C-SOK-TOU-FC-ET-WC-OFF | -278.5844 | 2690.0417 | 2411.4573 | 9018.1986 | 0.2674 | 1.5461 | 1.1662 | 2.0861 | 4.592 | 3369.0652 | 22800 | 3 | 4 | 5585.4851 | 6928.5041 | 6969.5041 | 188018.4851 | 75.0787
567 | C-SOK-TOU-FC-ET-WC-OFF | 304.3522 | 2687.9228 | 2992.2749 | 9017.4339 | 0.33183 | 1.6954 | 1.1663 | 2.3481 | 4.593 | 5697.28 | 23750 | 3 | 4 | 5061.6861 | 6928.0452 | 6969.0452 | 195094.6861 | 62.8704
568 | C-SOK-TOU-FC-ET-WC-OFF | -79.2744 | 2698.8024 | 2619.528 | 9016.9455 | 0.29051 | 1.5966 | 1.1663 | 2.1727 | 4.5931 | 4180.9063 | 25575 | 3 | 4 | 5400.0483 | 6927.7522 | 6968.7522 | 210033.0483 | 77.5194
569 | C-SOK-TOU-FC-ET-WC-OFF | 1069.5429 | 2696.9791 | 3766.522 | 9017.5126 | 0.41769 | 1.9452 | 1.1662 | 2.7188 | 4.5922 | 8773.1369 | 26725 | 3 | 4 | 4367.6044 | 6928.0924 | 6969.0924 | 218200.6044 | 56.0813
570 | C-SOK-TOU-FC-ET-WC-OFF | 1518.2313 | 2699.1815 | 4217.4128 | 9017.5847 | 0.46769 | 2.1276 | 1.1661 | 3.0003 | 4.5914 | 10571.5609 | 27825 | 3 | 4 | 3962.4891 | 6928.1357 | 6969.1357 | 226595.4891 | 52.0761
571 | C-SOK-TOU-FC-ET-WC-R100 | 868.3922 | 1006.4123 | 1874.8044 | 35044.5502 | 0.053498 | 0.88907 | 0.85003 | 0.73357 | 4.6037 | 5150.9225 | 10350 | 3 | 4 | 29566.6693 | 30942.9483 | 30983.9483 | 112399.6694 | 43.4262
572 | C-SOK-TOU-FC-ET-WC-R100 | 1469.1567 | 998.855 | 2468.0117 | 35090.815 | 0.070332 | 0.90513 | 0.84998 | 0.742 | 4.6039 | 7541.3853 | 10800 | 3 | 4 | 29072.1859 | 30984.6162 | 31025.6162 | 115505.186 | 34.2298
573 | C-SOK-TOU-FC-ET-WC-R100 | 1705.7899 | 995.4249 | 2701.2148 | 35107.1248 | 0.076942 | 0.91162 | 0.84998 | 0.74695 | 4.605 | 8482.2011 | 11250 | 3 | 4 | 28875.9345 | 30999.2641 | 31040.2641 | 118908.9345 | 32.5293
574 | C-SOK-TOU-FC-ET-WC-R100 | 2886.998 | 1016.4207 | 3903.4187 | 35123.528 | 0.11113 | 0.94668 | 0.84997 | 0.84311 | 4.6058 | 13242.0267 | 14075 | 3 | 4 | 27815.0764 | 31014.0912 | 31055.0912 | 140448.0765 | 28.0249
575 | C-SOK-TOU-FC-ET-WC-R100 | 3683.5814 | 1009.2966 | 4692.878 | 35164.6835 | 0.13345 | 0.97101 | 0.84992 | 0.87214 | 4.605 | 16416.4865 | 14725 | 3 | 4 | 27139.37 | 31051.0284 | 31092.0284 | 144972.37 | 24.2666
576 | C-SOK-TOU-FC-ET-WC-R100 | 4022.7459 | 1005.2754 | 5028.0213 | 35165.9802 | 0.14298 | 0.98181 | 0.84993 | 0.8991 | 4.6056 | 17766.4427 | 15325 | 3 | 4 | 26837.7597 | 31052.2414 | 31093.2414 | 149470.7597 | 23.5436
577 | C-SOK-TOU-FC-ET-WC-R100 | 4698.6944 | 1026.0761 | 5724.7705 | 35180.2034 | 0.16273 | 1.0049 | 0.84989 | 0.96146 | 4.605 | 20504.9044 | 17850 | 3 | 4 | 26229.7484 | 31065.1133 | 31106.1133 | 169062.7485 | 24.0982
578 | C-SOK-TOU-FC-ET-WC-R100 | 5540.1785 | 1020.805 | 6560.9835 | 35211.4447 | 0.18633 | 1.0341 | 0.84989 | 1.0166 | 4.6066 | 23862.0558 | 18600 | 3 | 4 | 25503.6364 | 31093.167 | 31134.167 | 174336.6364 | 21.8264
579 | C-SOK-TOU-FC-ET-WC-R100 | 5961.0323 | 1018.1192 | 6979.1515 | 35223.1084 | 0.19814 | 1.0493 | 0.84987 | 1.045 | 4.6057 | 25540.9945 | 19400 | 3 | 4 | 25136.8917 | 31103.5632 | 31144.5632 | 180369.8917 | 21.3816
580 | C-SOK-TOU-FC-ET-WC-R10 | 6206.9385 | 1030.662 | 7237.6005 | 35215.6783 | 0.20552 | 1.0591 | 0.84991 | 1.076 | 4.6081 | 26545.5239 | 21850 | 3 | 4 | 24901.4395 | 31096.9679 | 31137.9679 | 199734.4396 | 23.2945
581 | C-SOK-TOU-FC-ET-WC-R10 | 7266.7027 | 1024.3386 | 8291.0413 | 35260.341 | 0.23514 | 1.1001 | 0.84986 | 1.1778 | 4.6081 | 30774.0417 | 22800 | 3 | 4 | 23991.6785 | 31137.1993 | 31178.1993 | 206424.6785 | 21.1368
582 | C-SOK-TOU-FC-ET-WC-R10 | 7816.0232 | 1021.9221 | 8837.9453 | 35270.4218 | 0.25058 | 1.1227 | 0.84983 | 1.2624 | 4.6071 | 32967.2963 | 23750 | 3 | 4 | 23507.726 | 31146.1848 | 31187.1848 | 213540.726 | 20.633
583 | C-SOK-TOU-FC-ET-WC-R10 | 7424.017 | 1029.0146 | 8453.0316 | 35244.1139 | 0.23984 | 1.1069 | 0.84989 | 1.1787 | 4.6094 | 31411.0922 | 25575 | 3 | 4 | 23832.752 | 31122.662 | 31163.662 | 228465.752 | 23.341
584 | C-SOK-TOU-FC-ET-WC-R10 | 8679.0105 | 1024.2654 | 9703.2759 | 35291.3712 | 0.27495 | 1.1604 | 0.84984 | 1.3486 | 4.6092 | 36423.151 | 26725 | 3 | 4 | 22748.5396 | 31165.0933 | 31206.0933 | 236581.5396 | 21.1656
585 | C-SOK-TOU-FC-ET-WC-R10 | 9234.8674 | 1022.2646 | 10257.132 | 35296.4228 | 0.2906 | 1.1861 | 0.84985 | 1.4587 | 4.6101 | 38643.2439 | 27825 | 3 | 4 | 22254.068 | 31169.6894 | 31210.6894 | 244887.068 | 20.832
586 | C-SOK-STR-FC-FP-WC-OFF0 | -7505.6315 | 2025.3737 | -5480.2578 | 14963.6012 | -0.36624 | 0.70462 | 0.98314 | 0.77357 | 4.7367 | -26646.9031 | 6750 | 3 | 4 | 18079.0953 | 12523.7127 | 12564.7127 | 72112.0953 | -10.8658
587 | C-SOK-STR-FC-FP-WC-OFF0 | -7356.2288 | 2028.3512 | -5327.8776 | 14963.4762 | -0.35606 | 0.7099 | 0.98312 | 0.77308 | 4.7366 | -26044.3299 | 7200 | 3 | 4 | 17942.7731 | 12523.6377 | 12564.6377 | 75575.7732 | -11.8267
588 | C-SOK-STR-FC-FP-WC-OFF0 | -7298.0668 | 2027.7038 | -5270.3629 | 14963.3132 | -0.35222 | 0.7119 | 0.98309 | 0.77153 | 4.7362 | -25812.7606 | 7650 | 3 | 4 | 17890.7295 | 12523.5399 | 12564.5399 | 79123.7295 | -12.629
589 | C-SOK-STR-FC-FP-WC-OFF0 | -6297.7068 | 2027.7364 | -4269.9704 | 14963.4089 | -0.28536 | 0.74894 | 0.98311 | 0.84769 | 4.7364 | -21811.2666 | 9175 | 3 | 4 | 16990.477 | 12523.5973 | 12564.5973 | 90423.4771 | -18.2341
590 | C-SOK-STR-FC-FP-WC-OFF0 | -6038.0472 | 2032.1118 | -4005.9353 | 14963.5575 | -0.26771 | 0.75936 | 0.9831 | 0.85324 | 4.7363 | -20765.3357 | 9825 | 3 | 4 | 16754.2483 | 12523.6865 | 12564.6865 | 95387.2483 | -20.675
591 | C-SOK-STR-FC-FP-WC-OFF0 | -5827.7337 | 2032.429 | -3795.3047 | 14963.5262 | -0.25364 | 0.76789 | 0.98311 | 0.86 | 4.7363 | -19923.5533 | 10425 | 3 | 4 | 16564.7765 | 12523.6677 | 12564.6677 | 99997.7765 | -23.0372
592 | C-SOK-STR-FC-FP-WC-OFF0 | -5319.3557 | 2035.8052 | -3283.5505 | 14963.7564 | -0.21943 | 0.78942 | 0.98309 | 0.9118 | 4.736 | -17884.4142 | 11650 | 3 | 4 | 16105.326 | 12523.8058 | 12564.8058 | 109338.326 | -29.4722
593 | C-SOK-STR-FC-FP-WC-OFF0 | -4915.4593 | 2037.8635 | -2877.5958 | 14963.234 | -0.19231 | 0.80739 | 0.98311 | 0.93284 | 4.7365 | -16265.3979 | 12400 | 3 | 4 | 15740.2874 | 12523.4924 | 12564.4924 | 114973.2874 | -35.5883
594 | C-SOK-STR-FC-FP-WC-OFF0 | -4606.7631 | 2038.5402 | -2568.2229 | 14963.1057 | -0.17164 | 0.82165 | 0.98313 | 0.94888 | 4.7369 | -15029.4855 | 13200 | 3 | 4 | 15461.9852 | 12523.4154 | 12564.4154 | 121094.9852 | -42.259
595 | C-SOK-STR-FC-FP-WC-OFF | -4428.2932 | 2037.1968 | -2391.0964 | 14963.3747 | -0.1598 | 0.83007 | 0.98316 | 0.98004 | 4.7372 | -14317.845 | 14250 | 3 | 4 | 15302.3199 | 12523.5768 | 12564.5768 | 129335.32 | -48.8356
596 | C-SOK-STR-FC-FP-WC-OFF | -3757.4584 | 2040.5923 | -1716.866 | 14963.3285 | -0.11474 | 0.86358 | 0.98311 | 1.0273 | 4.7366 | -11628.8463 | 15200 | 3 | 4 | 14696.5012 | 12523.5491 | 12564.5491 | 136329.5012 | -72.0877
597 | C-SOK-STR-FC-FP-WC-OFF | -3296.8751 | 2041.1016 | -1255.7735 | 14963.1774 | -0.083924 | 0.88814 | 0.98312 | 1.07 | 4.7368 | -9785.6645 | 16150 | 3 | 4 | 14281.5958 | 12523.4584 | 12564.4584 | 143514.5958 | -104.2785
598 | C-SOK-STR-FC-FP-WC-OFF | -3613.1667 | 2037.6151 | -1575.5516 | 14963.2724 | -0.10529 | 0.87098 | 0.98314 | 1.0574 | 4.737 | -11056.6417 | 16675 | 3 | 4 | 14568.3915 | 12523.5154 | 12564.5154 | 148001.3915 | -85.9616
599 | C-SOK-STR-FC-FP-WC-OFF | -2692.337 | 2038.9646 | -653.3723 | 14963.2075 | -0.043665 | 0.92241 | 0.98314 | 1.1416 | 4.7371 | -7371.0735 | 17825 | 3 | 4 | 13738.8135 | 12523.4765 | 12564.4765 | 156371.8135 | -220.1001
600 | C-SOK-STR-FC-FP-WC-OFF | -2305.2171 | 2039.7505 | -265.4665 | 14963.3058 | -0.017741 | 0.94591 | 0.98314 | 1.1832 | 4.7369 | -5821.284 | 18925 | 3 | 4 | 13390.0184 | 12523.5355 | 12564.5355 | 164823.0184 | -573.5505
601 | C-SOK-TOU-CC-ET-WC-R100 | 3210.1506 | 1229.574 | 4439.7246 | 46116.2334 | 0.096272 | 0.93436 | 0.85089 | 0.99808 | 5.1228 | 14889.8924 | 13250 | 3 | 4 | 37239.3732 | 40856.3691 | 40897.3691 | 143272.3733 | 23.0589
602 | C-SOK-TOU-CC-ET-WC-R100 | 3985.8868 | 1220.0646 | 5205.9514 | 46168.088 | 0.11276 | 0.95169 | 0.85085 | 1.0214 | 5.1236 | 17976.9882 | 13800 | 3 | 4 | 36593.6125 | 40903.0503 | 40944.0503 | 147026.6125 | 20.3772
603 | C-SOK-TOU-CC-ET-WC-R100 | 4288.8073 | 1216.2426 | 5505.0499 | 46185.4728 | 0.11919 | 0.95865 | 0.85085 | 1.0301 | 5.1246 | 19182.3001 | 14400 | 3 | 4 | 36338.8988 | 40918.663 | 40959.663 | 151571.8988 | 20.0929
604 | C-SOK-TOU-CC-ET-WC-R100 | 5777.9012 | 1234.0203 | 7011.9215 | 46218.0353 | 0.15171 | 0.99527 | 0.85075 | 1.1774 | 5.1193 | 25168.3054 | 18400 | 3 | 4 | 35017.4154 | 40948.0434 | 40989.0434 | 182250.4155 | 20.1459
605 | C-SOK-TOU-CC-ET-WC-R100 | 6757.482 | 1223.7962 | 7981.2782 | 46268.1741 | 0.1725 | 1.0202 | 0.85071 | 1.2315 | 5.12 | 29069.5882 | 19200 | 3 | 4 | 34187.0245 | 40993.13 | 41034.13 | 187820.0245 | 18.3913
606 | C-SOK-TOU-CC-ET-WC-R100 | 7239.8442 | 1220.0098 | 8459.854 | 46264.0157 | 0.18286 | 1.0331 | 0.85068 | 1.2829 | 5.1178 | 30992.7266 | 20000 | 3 | 4 | 33751.4677 | 40989.4234 | 41030.4234 | 193784.4677 | 18.0563
607 | C-SOK-TOU-CC-ET-WC-R100 | 7897.0038 | 1233.0983 | 9130.1021 | 46277.8297 | 0.19729 | 1.0519 | 0.8508 | 1.3825 | 5.1268 | 33643.179 | 23275 | 3 | 4 | 33164.5179 | 41001.7642 | 41042.7642 | 219397.5179 | 19.5348
608 | C-SOK-TOU-CC-ET-WC-R100 | 9141.4294 | 1221.1413 | 10362.5707 | 46325.1048 | 0.22369 | 1.0875 | 0.85072 | 1.5078 | 5.1236 | 38600.9532 | 24325 | 3 | 4 | 32094.3075 | 41044.3481 | 41085.3481 | 226727.3075 | 17.9147
609 | C-SOK-TOU-CC-ET-WC-R100 | 9720.4589 | 1214.953 | 10935.4119 | 46334.2966 | 0.23601 | 1.105 | 0.85069 | 1.6007 | 5.1227 | 40906.7571 | 25325 | 3 | 4 | 31585.1837 | 41052.6284 | 41093.6284 | 234218.1837 | 17.6605
610 | C-SOK-TOU-CC-ET-WC-R10 | 9794.5576 | 1227.0252 | 11021.5828 | 46327.5607 | 0.23791 | 1.1079 | 0.85075 | 1.5997 | 5.1257 | 41223.2725 | 28200 | 3 | 4 | 31505.118 | 41046.5065 | 41087.5065 | 257138.118 | 19.6025
611 | C-SOK-TOU-CC-ET-WC-R10 | 11179.1328 | 1213.1376 | 12392.2704 | 46382.3937 | 0.26718 | 1.1521 | 0.85072 | 1.8297 | 5.1272 | 46738.4272 | 29400 | 3 | 4 | 30316.6604 | 41095.8064 | 41136.8064 | 265549.6604 | 18.1091
612 | C-SOK-TOU-CC-ET-WC-R10 | 11781.6788 | 1205.5891 | 12987.2679 | 46393.5265 | 0.27994 | 1.1725 | 0.85068 | 2.0208 | 5.1253 | 49136.0302 | 30650 | 3 | 4 | 29788.9782 | 41105.874 | 41146.874 | 275021.9782 | 18.008
613 | C-SOK-TOU-CC-ET-WC-R10 | 11430.0552 | 1212.6753 | 12642.7305 | 46365.4056 | 0.27268 | 1.1609 | 0.85076 | 1.8396 | 5.1288 | 47741.3463 | 33350 | 3 | 4 | 30075.8126 | 41080.5111 | 41121.5111 | 296908.8126 | 20.232
614 | C-SOK-TOU-CC-ET-WC-R10 | 12930.4861 | 1197.5271 | 14128.0132 | 46418.628 | 0.30436 | 1.2136 | 0.85069 | 2.1881 | 5.1272 | 53717.8229 | 34800 | 3 | 4 | 28782.4895 | 41128.4647 | 41169.4647 | 307215.4895 | 18.8311
615 | C-SOK-TOU-CC-ET-WC-R10 | 13585.322 | 1190.3746 | 14775.6965 | 46429.3582 | 0.31824 | 1.2384 | 0.8507 | 2.4891 | 5.1289 | 56325.2456 | 36250 | 3 | 4 | 28207.0787 | 41138.0942 | 41179.0942 | 318240.0787 | 18.7511
616 | C-SOK-TOU-CC-FP-WC-R100 | 3283.9476 | 1249.7566 | 4533.7042 | 46069.3881 | 0.09841 | 0.93663 | 0.85094 | 0.95617 | 5.1235 | 15218.718 | 8650 | 3 | 4 | 37118.6436 | 40814.1651 | 40855.1651 | 106351.6437 | 14.4466
617 | C-SOK-TOU-CC-FP-WC-R100 | 4275.5862 | 1245.7415 | 5521.3277 | 46131.8586 | 0.11969 | 0.9592 | 0.85088 | 0.96117 | 5.1228 | 19178.5805 | 9200 | 3 | 4 | 36284.8228 | 40870.4114 | 40911.4114 | 109917.8228 | 12.4982
618 | C-SOK-TOU-CC-FP-WC-R100 | 4756.8065 | 1245.0347 | 6001.8412 | 46151.1058 | 0.13005 | 0.97062 | 0.85087 | 0.96955 | 5.1232 | 21102.2838 | 9800 | 3 | 4 | 35869.4412 | 40887.6985 | 40928.6985 | 114302.4412 | 12.2252
619 | C-SOK-TOU-CC-FP-WC-R100 | 5573.9542 | 1250.387 | 6824.3412 | 46175.1892 | 0.14779 | 0.99075 | 0.8508 | 1.0638 | 5.1201 | 24379.7953 | 12000 | 3 | 4 | 35152.4867 | 40909.3946 | 40950.3946 | 131185.4867 | 13.2225
620 | C-SOK-TOU-CC-FP-WC-R100 | 6993.7556 | 1248.9431 | 8242.6988 | 46237.1249 | 0.17827 | 1.0274 | 0.85074 | 1.1104 | 5.1198 | 30056.5943 | 12800 | 3 | 4 | 33931.351 | 40965.2108 | 41006.2108 | 136364.351 | 11.5688
621 | C-SOK-TOU-CC-FP-WC-R100 | 7568.3656 | 1247.8669 | 8816.2324 | 46237.7413 | 0.19067 | 1.0432 | 0.85076 | 1.1371 | 5.1209 | 32353.2404 | 13600 | 3 | 4 | 33415.3441 | 40965.6987 | 41006.6987 | 142248.3441 | 11.4835
622 | C-SOK-TOU-CC-FP-WC-R100 | 7556.5034 | 1246.5246 | 8803.028 | 46240.5149 | 0.19037 | 1.0427 | 0.85064 | 1.1859 | 5.1133 | 32303.5546 | 15175 | 3 | 4 | 33429.3867 | 40968.285 | 41009.285 | 154862.3867 | 12.9334
623 | C-SOK-TOU-CC-FP-WC-R100 | 9201.7051 | 1244.357 | 10446.0621 | 46294.16 | 0.22565 | 1.0903 | 0.85076 | 1.2653 | 5.1249 | 38880.7486 | 16225 | 3 | 4 | 31998.2013 | 41016.4435 | 41057.4435 | 161831.2013 | 11.5617
624 | C-SOK-TOU-CC-FP-WC-R100 | 9918.7387 | 1244.3151 | 11163.0539 | 46301.7534 | 0.24109 | 1.1125 | 0.8507 | 1.3059 | 5.1211 | 41748.8135 | 17225 | 3 | 4 | 31359.7668 | 41023.3054 | 41064.3054 | 169192.7668 | 11.4779
625 | C-SOK-TOU-CC-FP-WC-R10 | 9450.7656 | 1236.3676 | 10687.1332 | 46288.904 | 0.23088 | 1.0978 | 0.85081 | 1.3305 | 5.1277 | 39863.6749 | 18400 | 3 | 4 | 31774.0997 | 41011.6992 | 41052.6992 | 179007.0997 | 12.9085
626 | C-SOK-TOU-CC-FP-WC-R10 | 11149.8608 | 1236.6896 | 12386.5503 | 46343.3444 | 0.26728 | 1.1523 | 0.85078 | 1.4527 | 5.1287 | 46660.5924 | 19600 | 3 | 4 | 30293.7523 | 41060.7081 | 41101.7081 | 187126.7523 | 11.789
627 | C-SOK-TOU-CC-FP-WC-R10 | 12042.0648 | 1234.3332 | 13276.398 | 46355.1851 | 0.28641 | 1.1832 | 0.85074 | 1.5586 | 5.1271 | 50225.4811 | 20850 | 3 | 4 | 29502.8385 | 41071.3466 | 41112.3466 | 196335.8385 | 11.6917
628 | C-SOK-TOU-CC-FP-WC-R10 | 10967.0666 | 1220.7891 | 12187.8558 | 46323.775 | 0.2631 | 1.1458 | 0.85076 | 1.445 | 5.1263 | 45902.9151 | 21750 | 3 | 4 | 30450.1827 | 41043.0941 | 41084.0941 | 204483.1827 | 13.4067
629 | C-SOK-TOU-CC-FP-WC-R10 | 12883.4103 | 1221.1028 | 14104.5131 | 46384.7239 | 0.30408 | 1.2131 | 0.8507 | 1.6259 | 5.1262 | 53568.8125 | 23200 | 3 | 4 | 28780.2136 | 41097.999 | 41138.999 | 214413.2136 | 12.285
630 | C-SOK-TOU-CC-FP-WC-R10 | 13889.5741 | 1219.5823 | 15109.1565 | 46396.3913 | 0.32565 | 1.252 | 0.85073 | 1.808 | 5.1286 | 57590.9337 | 24650 | 3 | 4 | 27886.0459 | 41108.441 | 41149.441 | 225119.0459 | 12.176
631 | C-SOK-TOU-CC-ET-WC-R600 | 2507.8292 | 1653.0681 | 4160.8972 | 33847.4095 | 0.12293 | 0.99769 | 0.88329 | 1.0323 | 5.195 | 12786.4301 | 13250 | 3 | 4 | 26436.2683 | 29672.4485 | 29713.4485 | 132469.2684 | 24.6956
632 | C-SOK-TOU-CC-ET-WC-R600 | 3290.8392 | 1644.0472 | 4934.8865 | 33967.3712 | 0.14528 | 1.0235 | 0.88298 | 1.0609 | 5.1931 | 15903.4357 | 13800 | 3 | 4 | 25844.9808 | 29780.4493 | 29821.4493 | 136277.9808 | 21.5722
633 | C-SOK-TOU-CC-ET-WC-R600 | 3588.9318 | 1639.0673 | 5227.9991 | 33995.0111 | 0.15379 | 1.0337 | 0.88295 | 1.0751 | 5.1943 | 17087.5061 | 14400 | 3 | 4 | 25604.5378 | 29805.2874 | 29846.2874 | 140837.5378 | 21.2302
634 | C-SOK-TOU-CC-ET-WC-R600 | 4811.6858 | 1662.0146 | 6473.7004 | 33982.5236 | 0.1905 | 1.0806 | 0.88297 | 1.2021 | 5.1937 | 22016.7676 | 18400 | 3 | 4 | 24479.0407 | 29794.037 | 29835.037 | 171712.0408 | 21.9159
635 | C-SOK-TOU-CC-ET-WC-R600 | 5852.3837 | 1653.7471 | 7506.1308 | 34072.0354 | 0.2203 | 1.1217 | 0.88277 | 1.2845 | 5.1938 | 26165.7799 | 19200 | 3 | 4 | 23627.9868 | 29874.6321 | 29915.6321 | 177260.9868 | 19.63
636 | C-SOK-TOU-CC-ET-WC-R600 | 6372.5478 | 1649.6737 | 8022.2215 | 34090.7732 | 0.23532 | 1.1437 | 0.88276 | 1.3489 | 5.1951 | 28239.6474 | 20000 | 3 | 4 | 23179.1634 | 29891.4956 | 29932.4956 | 183212.1634 | 19.1069
637 | C-SOK-TOU-CC-ET-WC-R600 | 6705.891 | 1668.1338 | 8374.0248 | 34057.7791 | 0.24588 | 1.1595 | 0.88262 | 1.3833 | 5.1868 | 29603.787 | 23275 | 3 | 4 | 22838.4019 | 29861.8524 | 29902.8524 | 209071.4019 | 21.3958
638 | C-SOK-TOU-CC-ET-WC-R600 | 8046.6126 | 1659.7402 | 9706.3528 | 34125.5102 | 0.28443 | 1.222 | 0.88257 | 1.5578 | 5.1905 | 34952.6841 | 24325 | 3 | 4 | 21697.7556 | 29922.7873 | 29963.7873 | 216330.7556 | 19.2005
639 | C-SOK-TOU-CC-ET-WC-R600 | 8703.1369 | 1652.3781 | 10355.515 | 34139.3963 | 0.30333 | 1.2553 | 0.88271 | 1.6805 | 5.1972 | 37566.5111 | 25325 | 3 | 4 | 21123.7879 | 29935.2393 | 29976.2393 | 223756.7879 | 18.7128
640 | C-SOK-TOU-CC-ET-WC-R60 | 8475.7355 | 1665.7351 | 10141.4706 | 34117.7462 | 0.29725 | 1.2445 | 0.88277 | 1.5988 | 5.1975 | 36679.167 | 28200 | 3 | 4 | 21300.9163 | 29915.7404 | 29956.7404 | 246933.9163 | 21.395
641 | C-SOK-TOU-CC-ET-WC-R60 | 9898.3729 | 1656.7909 | 11555.1638 | 34166.4036 | 0.3382 | 1.3213 | 0.88263 | 1.8677 | 5.1961 | 42354.8096 | 29400 | 3 | 4 | 20069.7409 | 29959.5501 | 30000.5501 | 255302.7409 | 19.498
642 | C-SOK-TOU-CC-ET-WC-R60 | 10680.0544 | 1649.5533 | 12329.6077 | 34183.1545 | 0.36069 | 1.3678 | 0.88263 | 2.0922 | 5.1976 | 45469.473 | 30650 | 3 | 4 | 19385.6666 | 29974.6065 | 30015.6065 | 264618.6666 | 19.0276
643 | C-SOK-TOU-CC-ET-WC-R60 | 9960.8105 | 1657.9884 | 11618.7989 | 34159.7808 | 0.34013 | 1.3253 | 0.88268 | 1.7961 | 5.1973 | 42606.5558 | 33350 | 3 | 4 | 20006.8006 | 29953.5253 | 29994.5253 | 286839.8006 | 22.106
644 | C-SOK-TOU-CC-ET-WC-R60 | 11652.6392 | 1645.8487 | 13298.4879 | 34207.8675 | 0.38876 | 1.4305 | 0.88255 | 2.2344 | 5.1965 | 49353.6379 | 34800 | 3 | 4 | 18534.7955 | 29996.8425 | 30037.8425 | 296967.7955 | 20.0722
645 | C-SOK-TOU-CC-ET-WC-R60 | 12494.8241 | 1638.1492 | 14132.9734 | 34228.3365 | 0.4129 | 1.4893 | 0.88253 | 2.5643 | 5.1974 | 52709.5452 | 36250 | 3 | 4 | 17799.8837 | 30015.2331 | 30056.2331 | 307832.8837 | 19.6545
646 | C-SOK-TOU-FC-ET-WC-R600 | 316.0757 | 1275.7787 | 1591.8544 | 25303.3228 | 0.062911 | 0.92625 | 0.87896 | 0.76071 | 4.661 | 3390.6007 | 10350 | 3 | 4 | 21043.8006 | 22082.6204 | 22123.6204 | 103876.8006 | 51.3572
647 | C-SOK-TOU-FC-ET-WC-R600 | 934.4229 | 1267.2197 | 2201.6426 | 25403.3591 | 0.086667 | 0.95009 | 0.87868 | 0.77167 | 4.6608 | 5849.7244 | 10800 | 3 | 4 | 20582.4212 | 22172.6168 | 22213.6168 | 107015.4213 | 38.5175
648 | C-SOK-TOU-FC-ET-WC-R600 | 1183.0006 | 1263.8147 | 2446.8153 | 25425.2083 | 0.096236 | 0.96011 | 0.87863 | 0.78109 | 4.6613 | 6838.3603 | 11250 | 3 | 4 | 20380.4296 | 22192.294 | 22233.294 | 110413.4296 | 36.0387
649 | C-SOK-TOU-FC-ET-WC-R600 | 2156.5835 | 1291.0066 | 3447.5902 | 25410.0379 | 0.13568 | 1.004 | 0.87872 | 0.8647 | 4.663 | 10778.0119 | 14075 | 3 | 4 | 19474.2958 | 22178.7024 | 22219.7024 | 132107.2959 | 31.8737
650 | C-SOK-TOU-FC-ET-WC-R600 | 2943.3844 | 1285.4406 | 4228.825 | 25492.1426 | 0.16589 | 1.0401 | 0.87847 | 0.90264 | 4.6615 | 13915.9385 | 14725 | 3 | 4 | 18843.2734 | 22252.4567 | 22293.4567 | 136676.2734 | 27.0484
651 | C-SOK-TOU-FC-ET-WC-R600 | 3306.3704 | 1283.7726 | 4590.143 | 25505.1548 | 0.17997 | 1.0579 | 0.87843 | 0.92846 | 4.6618 | 15365.1024 | 15325 | 3 | 4 | 18529.3503 | 22264.2234 | 22305.2234 | 141162.3503 | 25.894
652 | C-SOK-TOU-FC-ET-WC-R600 | 3764.5224 | 1307.0266 | 5071.549 | 25484.4792 | 0.19901 | 1.0831 | 0.87848 | 0.97271 | 4.6616 | 17236.4673 | 17850 | 3 | 4 | 18084.4514 | 22245.6658 | 22286.6658 | 160917.4515 | 27.335
653 | C-SOK-TOU-FC-ET-WC-R600 | 4676.3249 | 1302.1761 | 5978.5009 | 25533.5237 | 0.23414 | 1.1328 | 0.8784 | 1.0436 | 4.6636 | 20875.593 | 18600 | 3 | 4 | 17310.9263 | 22289.8167 | 22330.8167 | 166143.9263 | 24.055
654 | C-SOK-TOU-FC-ET-WC-R600 | 5179.8434 | 1300.4884 | 6480.3318 | 25548.3101 | 0.25365 | 1.1623 | 0.87836 | 1.0994 | 4.6638 | 22886.8544 | 19400 | 3 | 4 | 16872.0882 | 22303.1415 | 22344.1415 | 172105.0882 | 23.1101
655 | C-SOK-TOU-FC-ET-WC-R60 | 5202.339 | 1317.4816 | 6519.8205 | 25527.9771 | 0.2554 | 1.1651 | 0.87844 | 1.1005 | 4.6646 | 23005.1586 | 21850 | 3 | 4 | 16823.3227 | 22284.849 | 22325.849 | 191656.3228 | 25.9716
656 | C-SOK-TOU-FC-ET-WC-R60 | 6338.5037 | 1314.8705 | 7653.3742 | 25569.4608 | 0.29932 | 1.238 | 0.87832 | 1.2217 | 4.6644 | 27545.4655 | 22800 | 3 | 4 | 15839.6787 | 22322.1827 | 22363.1827 | 198272.6787 | 22.9846
657 | C-SOK-TOU-FC-ET-WC-R60 | 6945.2867 | 1311.8746 | 8257.1614 | 25585.1463 | 0.32273 | 1.2808 | 0.87828 | 1.3309 | 4.6641 | 29967.6047 | 23750 | 3 | 4 | 15309.4279 | 22336.2118 | 22377.2118 | 205342.4279 | 22.1584
658 | C-SOK-TOU-FC-ET-WC-R60 | 6299.5018 | 1321.551 | 7621.0528 | 25562.2181 | 0.29814 | 1.236 | 0.87834 | 1.1912 | 4.6639 | 27400.5921 | 25575 | 3 | 4 | 15864.1675 | 22315.5807 | 22356.5807 | 220497.1675 | 25.9991
659 | C-SOK-TOU-FC-ET-WC-R60 | 7642.026 | 1318.5798 | 8960.6058 | 25602.9269 | 0.34998 | 1.3344 | 0.87821 | 1.3857 | 4.6636 | 32765.7371 | 26725 | 3 | 4 | 14694.364 | 22352.2745 | 22393.2745 | 228527.364 | 23.0045
660 | C-SOK-TOU-FC-ET-WC-R60 | 8327.9265 | 1316.3576 | 9644.2841 | 25619.8233 | 0.37644 | 1.391 | 0.87818 | 1.5367 | 4.6641 | 35505.6355 | 27825 | 3 | 4 | 14093.6266 | 22367.4917 | 22408.4917 | 236726.6266 | 22.2223

## Energetic Results
Code | Code | A_coll | V_store | q_coll | eta_coll | COP_th | SF_cooling | SF_heating | SF_DHW | totalcoolingtime | solarcoolingtime | coolingdemandtime | stagnationtime | waterconsumption wet cooling tower | Q_aux_total | P_el_SC+_total | P_el_ref_total | thermal_COP_el_cooling | thermal_COP_el_heating | Total_elec_eff | relBoilerconsumption | ref_COP_el | P_heat, fossil, ref | Efficiency_storage | Q_loss_storage
|  | [m²] | [m³] | [kWh/m²] | [-] | [-] | [-] | [-] | [-] | [h] | [h] | [h] | [h] | [m³] | [kWh] | [kWh] | [kWh] | [-] | [-] | [-] | [-] | [-] | [kWh] | [-] | [kWh]
1 | C-SOK-NAP-CC-ET-HC-R100 | 16.5 | 0.413 | 726.9439 | 0.42261 | 0.72557 | 0.32727 | 0.16693 | 0.73701 | 684.35 | 252.65 | 1854.725 | 2091 | 0 | 14159.5526 | 553.7276 | 2219.1453 | 18.3624 | 93.7915 | 30.9807 | 1.2572 | 3.092 | 12875.1304 | 0.61796 | -4844.9768
2 | #REF! | 16.5 | 0.825 | 763.6245 | 0.44394 | 0.72518 | 0.33443 | 0.19454 | 0.76551 | 687.5 | 255.875 | 1854.725 | 1996.95 | 0 | 13754.4794 | 556.5571 | 2219.1679 | 18.4189 | 92.3458 | 30.9232 | 1.2813 | 3.0927 | 12925.4623 | 0.62497 | -4691.7768
3 | #REF! | 16.5 | 1.238 | 778.3425 | 0.45249 | 0.72501 | 0.34291 | 0.20625 | 0.76696 | 688.75 | 258.6 | 1854.725 | 1957.775 | 0 | 13576.7705 | 558.3762 | 2219.1652 | 18.4028 | 91.5737 | 30.8493 | 1.2894 | 3.0925 | 12936.042 | 0.62792 | -4655.6558
4 | C-SOK-NAP-CC-ET-HC-R100 | 22.5 | 0.563 | 640.1263 | 0.37214 | 0.72461 | 0.44034 | 0.24347 | 0.77816 | 666.1 | 320.7 | 1854.725 | 2318 | 0 | 12362.1641 | 522.5277 | 2219.2384 | 19.6195 | 91.4566 | 32.7277 | 1.3359 | 3.0931 | 12933.3801 | 0.64452 | -4260.1424
5 | C-SOK-NAP-CC-ET-HC-R100 | 22.5 | 1.125 | 677.6065 | 0.39393 | 0.72418 | 0.47217 | 0.28077 | 0.8033 | 666.35 | 334.5 | 1854.725 | 2219.15 | 0 | 11663.9089 | 526.3087 | 2219.1614 | 19.5741 | 89.5403 | 32.5761 | 1.373 | 3.0929 | 12967.8655 | 0.65722 | -4120.4285
6 | C-SOK-NAP-CC-ET-HC-R100 | 22.5 | 1.688 | 692.827 | 0.40278 | 0.7239 | 0.49522 | 0.29815 | 0.80068 | 666.825 | 345.625 | 1854.725 | 2180.825 | 0 | 11327.6171 | 528.6011 | 2219.2781 | 19.5154 | 88.335 | 32.4597 | 1.3855 | 3.0933 | 12972.2638 | 0.66495 | -4144.353
7 | C-SOK-NAP-CC-ET-HC-R100 | 29 | 0.725 | 539.018 | 0.31336 | 0.72523 | 0.48951 | 0.31593 | 0.80764 | 656.475 | 347.95 | 1854.725 | 2566.55 | 0 | 11186.5864 | 512.2578 | 2219.2589 | 19.6313 | 91.2905 | 33.379 | 1.3999 | 3.0942 | 12971.1371 | 0.67121 | -4195.2795
8 | C-SOK-NAP-CC-ET-HC-R100 | 29 | 1.45 | 577.9142 | 0.33597 | 0.7243 | 0.55534 | 0.36607 | 0.8283 | 652.425 | 379.05 | 1854.725 | 2461.65 | 0 | 10100.526 | 511.6356 | 2219.2676 | 19.851 | 88.3157 | 33.4604 | 1.4535 | 3.0945 | 12996.7174 | 0.69309 | -4156.024
9 | C-SOK-NAP-CC-ET-HC-R100 | 29 | 2.175 | 600.6345 | 0.34918 | 0.72393 | 0.6004 | 0.39337 | 0.82282 | 652.825 | 401.675 | 1854.725 | 2406.2 | 0 | 9498.1138 | 518.2711 | 2219.3249 | 19.5892 | 86.6247 | 33.0788 | 1.4838 | 3.0953 | 12994.1186 | 0.70171 | -4122.2593
10 | C-SOK-NAP-CC-ET-HC-R10 | 35 | 0.875 | 468.5892 | 0.27242 | 0.72453 | 0.5518 | 0.37771 | 0.82651 | 641.225 | 371.75 | 1854.725 | 2752.575 | 0 | 10039.0206 | 498.9136 | 2219.372 | 19.9504 | 90.2633 | 34.2163 | 1.4603 | 3.096 | 12994.3973 | 0.71196 | -4578.6287
11 | C-SOK-NAP-CC-ET-HC-R10 | 35 | 1.75 | 514.0759 | 0.29886 | 0.72392 | 0.6254 | 0.43405 | 0.84643 | 639.075 | 410.025 | 1854.725 | 2634.625 | 0 | 8830.4457 | 503.5808 | 2219.3863 | 20.0244 | 87.338 | 33.9782 | 1.5271 | 3.0961 | 13018.2599 | 0.7179 | -4190.5761
12 | C-SOK-NAP-CC-ET-HC-R10 | 35 | 2.625 | 541.5221 | 0.31482 | 0.72344 | 0.68616 | 0.46806 | 0.84937 | 639.2 | 441.475 | 1854.725 | 2568.275 | 0 | 7994.76 | 510.8472 | 2219.3976 | 19.8132 | 84.7944 | 33.5436 | 1.5703 | 3.0961 | 13014.6628 | 0.72572 | -4047.3068
13 | C-SOK-NAP-CC-ET-HC-R10 | 41 | 1.025 | 420.9028 | 0.24469 | 0.72436 | 0.59122 | 0.43036 | 0.84474 | 633.625 | 388.65 | 1854.725 | 2889.325 | 0 | 9164.8875 | 498.6664 | 2219.3502 | 19.755 | 89.9086 | 34.2644 | 1.514 | 3.096 | 13013.0955 | 0.72849 | -4577.2412
14 | C-SOK-NAP-CC-ET-HC-R10 | 41 | 2.05 | 465.0663 | 0.27037 | 0.72367 | 0.68143 | 0.49049 | 0.86367 | 632.025 | 437.4 | 1854.725 | 2771.875 | 0 | 7782.5345 | 502.8535 | 2219.4563 | 19.9395 | 86.1713 | 34.0629 | 1.5888 | 3.0961 | 13041.5235 | 0.73378 | -4163.1563
15 | C-SOK-NAP-CC-ET-HC-R10 | 41 | 3.075 | 492.7808 | 0.28648 | 0.72288 | 0.75158 | 0.53596 | 0.86596 | 630.2 | 474.55 | 1854.725 | 2700.475 | 0 | 6769.1625 | 505.6296 | 2219.3615 | 20.0823 | 82.9467 | 33.8929 | 1.6412 | 3.0961 | 13039.3037 | 0.743 | -4032.2711
16 | C-SOK-NAP-CC-ET-HC-R600 | 16.5 | 0.413 | 734.2809 | 0.42688 | 0.72906 | 0.30649 | 0.16556 | 0.79604 | 751.975 | 262.975 | 2104.7 | 2069.075 | 0 | 11365.2283 | 561.5715 | 2420.1897 | 18.4536 | 86.0181 | 25.9296 | 1.2211 | 3.1165 | 9201.4976 | 0.62058 | -8279.606
17 | C-SOK-NAP-CC-ET-HC-R600 | 16.5 | 0.825 | 771.4107 | 0.44846 | 0.72877 | 0.31124 | 0.20325 | 0.82455 | 755.3 | 264.675 | 2104.7 | 1976.55 | 0 | 11033.115 | 564.023 | 2420.241 | 18.5299 | 84.6966 | 25.9589 | 1.2435 | 3.1161 | 9284.1697 | 0.62353 | -8167.1307
18 | C-SOK-NAP-CC-ET-HC-R600 | 16.5 | 1.238 | 788.3463 | 0.45831 | 0.72862 | 0.32194 | 0.22836 | 0.82326 | 756.1 | 268.975 | 2104.7 | 1931.175 | 0 | 10828.8632 | 565.7382 | 2420.2382 | 18.5097 | 83.8385 | 25.9098 | 1.2574 | 3.116 | 9298.0221 | 0.62703 | -8150.5187
19 | C-SOK-NAP-CC-ET-HC-R600 | 22.5 | 0.563 | 641.7 | 0.37305 | 0.72829 | 0.41353 | 0.25836 | 0.83503 | 731.9 | 333.825 | 2104.7 | 2306.8 | 0 | 9753.3379 | 531.1757 | 2420.2709 | 19.4909 | 82.9134 | 27.4001 | 1.2944 | 3.1158 | 9291.9864 | 0.63925 | -7719.893
20 | C-SOK-NAP-CC-ET-HC-R600 | 22.5 | 1.125 | 680.7433 | 0.39575 | 0.72784 | 0.44817 | 0.31196 | 0.85859 | 732.825 | 352.025 | 2104.7 | 2205.7 | 0 | 9078.6002 | 535.0745 | 2420.1806 | 19.4227 | 81.1194 | 27.3199 | 1.3355 | 3.1162 | 9350.0302 | 0.65088 | -7617.813
21 | C-SOK-NAP-CC-ET-HC-R600 | 22.5 | 1.688 | 701.2187 | 0.40766 | 0.72763 | 0.47643 | 0.35032 | 0.85994 | 732.2 | 365.55 | 2104.7 | 2151.25 | 0 | 8632.0738 | 537.4302 | 2420.317 | 19.3475 | 79.797 | 27.2219 | 1.3593 | 3.1166 | 9354.0355 | 0.66072 | -7615.9744
22 | C-SOK-NAP-CC-ET-HC-R600 | 29 | 0.725 | 535.0081 | 0.31103 | 0.72862 | 0.464 | 0.34133 | 0.86395 | 722.825 | 366.775 | 2104.7 | 2574.025 | 0 | 8765.5439 | 520.2768 | 2420.3023 | 19.4755 | 83.0793 | 28.0126 | 1.3561 | 3.1172 | 9348.9081 | 0.66222 | -7694.9826
23 | C-SOK-NAP-CC-ET-HC-R600 | 29 | 1.45 | 576.5744 | 0.33519 | 0.72783 | 0.53298 | 0.40951 | 0.88049 | 718.25 | 402.425 | 2104.7 | 2460.875 | 0 | 7726.0256 | 519.9888 | 2420.2274 | 19.645 | 80.2181 | 28.1081 | 1.4143 | 3.1174 | 9396.5221 | 0.68015 | -7629.3891
24 | C-SOK-NAP-CC-ET-HC-R600 | 29 | 2.175 | 601.571 | 0.34973 | 0.7275 | 0.57771 | 0.45913 | 0.88408 | 718.3 | 427.875 | 2104.7 | 2399.825 | 0 | 7058.6073 | 525.0247 | 2420.2932 | 19.4518 | 78.551 | 27.8779 | 1.4519 | 3.1177 | 9401.4085 | 0.69072 | -7576.7504
25 | C-SOK-NAP-CC-ET-HC-R60 | 35 | 0.875 | 460.9548 | 0.26798 | 0.72805 | 0.52876 | 0.41123 | 0.88209 | 705.825 | 393.525 | 2104.7 | 2773.175 | 0 | 7750.4852 | 506.3738 | 2420.3574 | 19.7258 | 81.9582 | 28.7596 | 1.412 | 3.1187 | 9383.169 | 0.70265 | -8137.5568
26 | C-SOK-NAP-CC-ET-HC-R60 | 35 | 1.75 | 506.3703 | 0.29438 | 0.72731 | 0.60695 | 0.48932 | 0.89797 | 702.725 | 438.65 | 2104.7 | 2650.925 | 0 | 6576.8716 | 508.2995 | 2420.3633 | 19.8985 | 78.9909 | 28.7285 | 1.4799 | 3.1187 | 9420.6041 | 0.70853 | -7786.6254
27 | C-SOK-NAP-CC-ET-HC-R60 | 35 | 2.625 | 536.0327 | 0.31162 | 0.72689 | 0.66817 | 0.54087 | 0.90456 | 702.3 | 474.4 | 2104.7 | 2576.775 | 0 | 5724.8091 | 516.7952 | 2420.2939 | 19.6145 | 76.3938 | 28.3207 | 1.5285 | 3.1189 | 9427.1409 | 0.71539 | -7596.37
28 | C-SOK-NAP-CC-ET-HC-R60 | 41 | 1.025 | 411.658 | 0.23932 | 0.72796 | 0.56584 | 0.47038 | 0.8986 | 699.075 | 412.4 | 2104.7 | 2912.525 | 0 | 7051.5194 | 508.3749 | 2420.3918 | 19.4254 | 81.9573 | 28.71 | 1.4574 | 3.1185 | 9412.5459 | 0.71486 | -8115.7107
29 | C-SOK-NAP-CC-ET-HC-R60 | 41 | 2.05 | 453.7953 | 0.26382 | 0.72704 | 0.65916 | 0.56206 | 0.91291 | 695.425 | 466.8 | 2104.7 | 2800.775 | 0 | 5677.5158 | 507.6899 | 2420.3588 | 19.7171 | 78.524 | 28.7915 | 1.5355 | 3.1187 | 9439.3921 | 0.72445 | -7798.6434
30 | C-SOK-NAP-CC-ET-HC-R60 | 41 | 3.075 | 483.6835 | 0.28119 | 0.72641 | 0.73184 | 0.61298 | 0.92197 | 693.375 | 508.95 | 2104.7 | 2726.025 | 0 | 4705.296 | 512.4146 | 2420.463 | 19.7186 | 74.8233 | 28.5812 | 1.588 | 3.119 | 9452.7404 | 0.72988 | -7557.205
31 | C-SOK-NAP-CC-ET-WC-R100 | 23 | 0.6 | 653.0369 | 0.37965 | 0.70813 | 0.33199 | 0.17903 | 0.74557 | 1076.025 | 364.025 | 1854.725 | 2111.95 | 25.8465 | 19857.4242 | 893.1647 | 3098.8506 | 13.2329 | 119.5549 | 27.8095 | 1.1932 | 3.0583 | 17729.3152 | 0.69807 | -14445.6119
32 | C-SOK-NAP-CC-ET-WC-R100 | 23 | 1.15 | 681.9118 | 0.39643 | 0.70786 | 0.34444 | 0.20537 | 0.76652 | 1077.275 | 387.075 | 1854.725 | 2033.65 | 25.8594 | 19279.1289 | 899.0006 | 3098.8431 | 13.169 | 117.474 | 27.6983 | 1.2202 | 3.0583 | 17784.4031 | 0.7092 | -14492.7524
33 | C-SOK-NAP-CC-ET-WC-R100 | 23 | 1.75 | 693.6847 | 0.40328 | 0.70688 | 0.34965 | 0.21833 | 0.76674 | 1080.125 | 401.5 | 1854.725 | 2000.95 | 25.8815 | 19068.3925 | 902.0669 | 3098.8267 | 13.1341 | 116.4566 | 27.6245 | 1.2295 | 3.0583 | 17797.9008 | 0.71231 | -14508.5749
34 | C-SOK-NAP-CC-ET-WC-R100 | 32 | 0.8 | 546.9511 | 0.31797 | 0.70353 | 0.42772 | 0.25365 | 0.78172 | 1071.575 | 462.175 | 1854.725 | 2380.1 | 25.8966 | 17604.1339 | 878.6379 | 3098.9064 | 13.3391 | 115.9573 | 28.3237 | 1.2671 | 3.0582 | 17810.8917 | 0.73716 | -14458.916
35 | C-SOK-NAP-CC-ET-WC-R100 | 32 | 1.6 | 581.053 | 0.3378 | 0.70229 | 0.4597 | 0.29489 | 0.80285 | 1073.65 | 512.475 | 1854.725 | 2286.25 | 25.9437 | 16600.1347 | 887.3351 | 3099.0733 | 13.2254 | 113.2027 | 28.1126 | 1.3103 | 3.0598 | 17850.9711 | 0.75165 | -14458.9021
36 | C-SOK-NAP-CC-ET-WC-R100 | 32 | 2.4 | 598.1923 | 0.34776 | 0.70165 | 0.48507 | 0.31135 | 0.80026 | 1075.5 | 552.125 | 1854.725 | 2241.6 | 25.9712 | 16097.971 | 890.6874 | 3099.0387 | 13.1874 | 111.8281 | 28.0179 | 1.3304 | 3.0601 | 17853.7542 | 0.75716 | -14452.2778
37 | C-SOK-NAP-CC-ET-WC-R100 | 40.5 | 1 | 470.8797 | 0.27375 | 0.70018 | 0.48917 | 0.31792 | 0.80648 | 1063.875 | 520.45 | 1854.725 | 2584.575 | 25.934 | 15943.6429 | 866.6328 | 3099.049 | 13.4929 | 113.0592 | 28.7415 | 1.327 | 3.0598 | 17855.1283 | 0.7695 | -14674.6299
38 | C-SOK-NAP-CC-ET-WC-R100 | 40.5 | 2.05 | 509.3537 | 0.29611 | 0.69819 | 0.54188 | 0.36923 | 0.82654 | 1068.075 | 602.65 | 1854.725 | 2475.475 | 25.989 | 14553.6588 | 877.8102 | 3099.1055 | 13.3416 | 109.7582 | 28.4389 | 1.3872 | 3.0597 | 17891.2005 | 0.78225 | -14586.607
39 | C-SOK-NAP-CC-ET-WC-R100 | 40.5 | 3.05 | 530.703 | 0.30853 | 0.69755 | 0.58421 | 0.39279 | 0.82157 | 1068.325 | 657.65 | 1854.725 | 2421.75 | 26.0425 | 13758.5939 | 881.5242 | 3099.1413 | 13.3059 | 108.1652 | 28.3256 | 1.4279 | 3.061 | 17885.5277 | 0.78833 | -14538.0685
40 | C-SOK-NAP-CC-ET-WC-R10 | 49 | 1.25 | 418.9909 | 0.24358 | 0.69777 | 0.53479 | 0.37885 | 0.82704 | 1059.125 | 570.55 | 1854.725 | 2728.725 | 25.9723 | 14530.3382 | 862.277 | 3099.2014 | 13.5931 | 110.327 | 28.9216 | 1.387 | 3.0606 | 17894.1015 | 0.78787 | -14730.2171
41 | C-SOK-NAP-CC-ET-WC-R10 | 49 | 2.45 | 455.9974 | 0.2651 | 0.69575 | 0.6015 | 0.43499 | 0.84141 | 1063.075 | 665.8 | 1854.725 | 2625.475 | 26.034 | 12927.0837 | 871.9993 | 3099.2384 | 13.4794 | 106.8707 | 28.649 | 1.4607 | 3.0605 | 17919.97 | 0.79849 | -14587.9539
42 | C-SOK-NAP-CC-ET-WC-R10 | 49 | 3.7 | 480.2129 | 0.27917 | 0.69392 | 0.65689 | 0.46643 | 0.84569 | 1067.875 | 734.425 | 1854.725 | 2559.65 | 26.1007 | 11817.7851 | 879.12 | 3099.2141 | 13.3914 | 104.3277 | 28.4262 | 1.5136 | 3.0608 | 17912.8254 | 0.80655 | -14490.2019
43 | C-SOK-NAP-CC-ET-WC-R10 | 58 | 1.45 | 375.6825 | 0.2184 | 0.69577 | 0.56791 | 0.43025 | 0.84396 | 1058.475 | 608.625 | 1854.725 | 2861.15 | 26.0101 | 13402.0958 | 863.3733 | 3099.2056 | 13.6416 | 107.609 | 28.9166 | 1.438 | 3.0606 | 17921.2421 | 0.79706 | -14658.1059
44 | C-SOK-NAP-CC-ET-WC-R10 | 58 | 2.9 | 412.7038 | 0.23993 | 0.69312 | 0.65129 | 0.49206 | 0.86154 | 1063.75 | 720.175 | 1854.725 | 2753.625 | 26.0882 | 11497.3977 | 874.811 | 3099.3247 | 13.515 | 103.5052 | 28.5985 | 1.5279 | 3.0609 | 17951.6507 | 0.80853 | -14497.6651
45 | C-SOK-NAP-CC-ET-WC-R10 | 58 | 4.35 | 438.0502 | 0.25466 | 0.69026 | 0.71846 | 0.53292 | 0.86593 | 1072.325 | 799.125 | 1854.725 | 2680.6 | 26.1765 | 10120.9804 | 885.0498 | 3099.1647 | 13.3956 | 99.8439 | 28.2879 | 1.5845 | 3.0609 | 17949.8962 | 0.81791 | -14423.682
46 | C-SOK-NAP-CC-ET-WC-R600 | 23 | 0.6 | 657.984 | 0.38252 | 0.70696 | 0.3125 | 0.1829 | 0.80769 | 1213.625 | 386.8 | 2104.7 | 2089.5 | 28.8204 | 15995.4446 | 942.1522 | 3395.5262 | 13.1984 | 108.4616 | 22.2503 | 1.1358 | 3.0836 | 12429.299 | 0.69829 | -20950.0413
47 | C-SOK-NAP-CC-ET-WC-R600 | 23 | 1.15 | 685.3215 | 0.39841 | 0.70683 | 0.32197 | 0.22399 | 0.82535 | 1213.5 | 407.975 | 2104.7 | 2013.025 | 28.8263 | 15510.9115 | 949.052 | 3395.5546 | 13.122 | 106.275 | 22.1783 | 1.1618 | 3.0831 | 12511.2559 | 0.7064 | -21114.0473
48 | C-SOK-NAP-CC-ET-WC-R600 | 23 | 1.75 | 699.3193 | 0.40655 | 0.70599 | 0.32994 | 0.25099 | 0.82323 | 1216.45 | 429.075 | 2104.7 | 1973.8 | 28.8506 | 15256.8277 | 952.2542 | 3395.5548 | 13.0828 | 105.2028 | 22.1168 | 1.18 | 3.0833 | 12519.0857 | 0.70965 | -21117.2593
49 | C-SOK-NAP-CC-ET-WC-R600 | 32 | 0.8 | 543.7332 | 0.3161 | 0.70244 | 0.40128 | 0.27574 | 0.83898 | 1208.925 | 490.575 | 2104.7 | 2373.725 | 28.8617 | 14038.1616 | 927.312 | 3395.5728 | 13.2689 | 104.6026 | 22.6918 | 1.2055 | 3.0824 | 12540.9634 | 0.7312 | -21100.424
50 | C-SOK-NAP-CC-ET-WC-R600 | 32 | 1.6 | 578.0164 | 0.33603 | 0.70122 | 0.43811 | 0.33197 | 0.85843 | 1209.9 | 551.55 | 2104.7 | 2275.425 | 28.9114 | 13066.8736 | 936.288 | 3395.6235 | 13.1518 | 101.7992 | 22.5527 | 1.2503 | 3.0835 | 12601.6864 | 0.74524 | -21188.9119
51 | C-SOK-NAP-CC-ET-WC-R600 | 32 | 2.4 | 600.0414 | 0.34884 | 0.7011 | 0.46369 | 0.3684 | 0.8622 | 1209.05 | 593.6 | 2104.7 | 2217.525 | 28.937 | 12454.3682 | 939.8332 | 3395.6386 | 13.1153 | 100.3079 | 22.4753 | 1.2827 | 3.084 | 12602.1116 | 0.75006 | -21079.5884
52 | C-SOK-NAP-CC-ET-WC-R600 | 40.5 | 1 | 463.4601 | 0.26943 | 0.69924 | 0.46515 | 0.3466 | 0.86236 | 1199.9 | 559.275 | 2104.7 | 2591.15 | 28.9037 | 12587.6262 | 914.317 | 3395.6403 | 13.3925 | 102.0064 | 23.0614 | 1.2633 | 3.0835 | 12604.4246 | 0.76222 | -21423.9314
53 | C-SOK-NAP-CC-ET-WC-R600 | 40.5 | 2.05 | 501.4015 | 0.29149 | 0.69765 | 0.51935 | 0.4208 | 0.87857 | 1202.225 | 650.25 | 2104.7 | 2479.075 | 28.9592 | 11270.4424 | 925.051 | 3395.7408 | 13.2511 | 99.0539 | 22.8661 | 1.3311 | 3.0836 | 12657.9589 | 0.77369 | -21404.3294
54 | C-SOK-NAP-CC-ET-WC-R600 | 40.5 | 3.05 | 527.9308 | 0.30691 | 0.69693 | 0.56268 | 0.47042 | 0.88205 | 1203 | 714.075 | 2104.7 | 2407.95 | 29.0072 | 10326.5352 | 930.2015 | 3395.7125 | 13.1954 | 97.0116 | 22.7502 | 1.3802 | 3.0843 | 12658.0407 | 0.77981 | -21269.991
55 | C-SOK-NAP-CC-ET-WC-R60 | 49 | 1.25 | 408.0868 | 0.23724 | 0.69631 | 0.5118 | 0.41463 | 0.88086 | 1198.2 | 618.975 | 2104.7 | 2746.75 | 28.958 | 11416.0936 | 910.842 | 3395.7864 | 13.4368 | 99.7092 | 23.1976 | 1.3156 | 3.0838 | 12655.923 | 0.77975 | -21572.9128
56 | C-SOK-NAP-CC-ET-WC-R60 | 49 | 2.45 | 445.0933 | 0.25876 | 0.69501 | 0.57947 | 0.49518 | 0.89449 | 1198.3 | 724.525 | 2104.7 | 2637.05 | 29.0073 | 9871.3486 | 919.0212 | 3395.6365 | 13.3503 | 96.5306 | 23.0405 | 1.3965 | 3.0842 | 12690.0078 | 0.78861 | -21416.1932
57 | C-SOK-NAP-CC-ET-WC-R60 | 49 | 3.7 | 471.7837 | 0.27427 | 0.69295 | 0.6391 | 0.54473 | 0.90213 | 1204.375 | 806.775 | 2104.7 | 2562.375 | 29.0863 | 8672.1636 | 927.9647 | 3395.7102 | 13.2292 | 93.6274 | 22.8402 | 1.4568 | 3.0842 | 12697.1151 | 0.79802 | -21336.4342
58 | C-SOK-NAP-CC-ET-WC-R60 | 58 | 1.45 | 363.5358 | 0.21134 | 0.69454 | 0.54675 | 0.47451 | 0.89532 | 1196.15 | 664.125 | 2104.7 | 2885.6 | 29.002 | 10470.4872 | 910.2316 | 3395.7345 | 13.4895 | 97.626 | 23.25 | 1.364 | 3.0846 | 12690.5166 | 0.78786 | -21550.3513
59 | C-SOK-NAP-CC-ET-WC-R60 | 58 | 2.9 | 400.4964 | 0.23283 | 0.6923 | 0.63162 | 0.56639 | 0.91119 | 1199.525 | 788.925 | 2104.7 | 2769.175 | 29.0781 | 8594.1251 | 922.0083 | 3395.7694 | 13.3482 | 93.5057 | 22.9973 | 1.4563 | 3.0846 | 12714.5323 | 0.79899 | -21347.6814
60 | C-SOK-NAP-CC-ET-WC-R60 | 58 | 4.35 | 426.5382 | 0.24797 | 0.68945 | 0.7015 | 0.61545 | 0.91943 | 1208.8 | 879.9 | 2104.7 | 2696.4 | 29.175 | 7245.2826 | 932.155 | 3395.7485 | 13.2223 | 89.8922 | 22.7805 | 1.5193 | 3.0845 | 12732.1471 | 0.80782 | -21279.5709
61 | C-SOK-NAP-CC-FP-HC-R100 | 16.5 | 0.413 | 623.7341 | 0.36261 | 0.72576 | 0.24134 | 0.14347 | 0.71828 | 695.7 | 198.625 | 1854.725 | 2212.125 | 0 | 15178.6016 | 565.5719 | 2219.1964 | 18.0073 | 94.7704 | 30.3513 | 1.2234 | 3.0918 | 12844.9337 | 0.61803 | -5508.0378
62 | C-SOK-NAP-CC-FP-HC-R100 | 16.5 | 0.825 | 654.969 | 0.38077 | 0.72552 | 0.24204 | 0.1769 | 0.75234 | 696.925 | 195.675 | 1854.725 | 2180.825 | 0 | 14755.0929 | 565.79 | 2219.1745 | 18.0804 | 92.8971 | 30.4232 | 1.2497 | 3.0916 | 12897.515 | 0.6328 | -5443.6271
63 | C-SOK-NAP-CC-FP-HC-R100 | 16.5 | 1.238 | 668.2069 | 0.38846 | 0.72542 | 0.24568 | 0.19306 | 0.75863 | 698.05 | 196.6 | 1854.725 | 2181.25 | 0 | 14560.6939 | 565.134 | 2219.1941 | 18.1123 | 92.1007 | 30.4718 | 1.2614 | 3.0916 | 12908.1088 | 0.63899 | -5428.1578
64 | C-SOK-NAP-CC-FP-HC-R100 | 22.5 | 0.563 | 544.9317 | 0.3168 | 0.72501 | 0.33737 | 0.21021 | 0.7604 | 681.65 | 259.45 | 1854.725 | 2387.075 | 0 | 13611.58 | 542.824 | 2219.1917 | 18.8472 | 91.4912 | 31.5863 | 1.2869 | 3.0926 | 12904.3748 | 0.65231 | -5129.5831
65 | C-SOK-NAP-CC-FP-HC-R100 | 22.5 | 1.125 | 576.7745 | 0.33531 | 0.72474 | 0.35707 | 0.25163 | 0.79098 | 681.45 | 265.675 | 1854.725 | 2370.725 | 0 | 12961.0137 | 542.8664 | 2219.2482 | 18.8303 | 90.0112 | 31.6433 | 1.3273 | 3.0921 | 12941.1017 | 0.66943 | -5051.8727
66 | C-SOK-NAP-CC-FP-HC-R100 | 22.5 | 1.688 | 591.7854 | 0.34404 | 0.7244 | 0.37491 | 0.27268 | 0.79504 | 682.075 | 273.3 | 1854.725 | 2371.15 | 0 | 12611.3453 | 541.6327 | 2219.2343 | 18.8622 | 89.1506 | 31.7199 | 1.346 | 3.0928 | 12947.2743 | 0.67962 | -5071.7837
67 | C-SOK-NAP-CC-FP-HC-R100 | 29 | 0.725 | 463.1005 | 0.26922 | 0.72526 | 0.39236 | 0.27412 | 0.79226 | 674.075 | 293.775 | 1854.725 | 2578.4 | 0 | 12453.17 | 537.2511 | 2219.2162 | 18.7927 | 89.7124 | 31.947 | 1.3463 | 3.0936 | 12943.6203 | 0.68472 | -5107.5207
68 | C-SOK-NAP-CC-FP-HC-R100 | 29 | 1.45 | 496.3806 | 0.28857 | 0.72469 | 0.4397 | 0.32253 | 0.82015 | 671.675 | 314.5 | 1854.725 | 2564.3 | 0 | 11513.0715 | 535.7545 | 2219.2394 | 18.8191 | 87.8992 | 32.0792 | 1.3981 | 3.0941 | 12974.2161 | 0.70682 | -5066.832
69 | C-SOK-NAP-CC-FP-HC-R100 | 29 | 2.175 | 515.1541 | 0.29949 | 0.72436 | 0.46981 | 0.3532 | 0.81921 | 671.675 | 328.575 | 1854.725 | 2549.75 | 0 | 10992.533 | 538.7311 | 2219.1934 | 18.6554 | 86.6796 | 31.9257 | 1.4216 | 3.0941 | 12976.9794 | 0.71635 | -5059.6006
70 | C-SOK-NAP-CC-FP-HC-R10 | 35 | 0.875 | 407.7846 | 0.23707 | 0.72478 | 0.44794 | 0.32275 | 0.81272 | 663.825 | 320.1 | 1854.725 | 2738.8 | 0 | 11471.5759 | 529.6229 | 2219.3584 | 18.9609 | 88.0711 | 32.405 | 1.3949 | 3.0949 | 12969.3499 | 0.71558 | -5249.5188
71 | C-SOK-NAP-CC-FP-HC-R10 | 35 | 1.75 | 446.2241 | 0.25941 | 0.72418 | 0.51573 | 0.38203 | 0.83726 | 661.525 | 354.175 | 1854.725 | 2694.25 | 0 | 10271.4441 | 529.5694 | 2219.3257 | 19.0183 | 85.7071 | 32.4564 | 1.4579 | 3.0956 | 12996.8946 | 0.73313 | -5093.0067
72 | C-SOK-NAP-CC-FP-HC-R10 | 35 | 2.625 | 469.4577 | 0.27292 | 0.72381 | 0.56434 | 0.41985 | 0.83763 | 660.975 | 377.325 | 1854.725 | 2674.45 | 0 | 9519.0178 | 533.164 | 2219.3007 | 18.8137 | 84.4789 | 32.2527 | 1.503 | 3.0944 | 12994.0843 | 0.74252 | -5022.8844
73 | C-SOK-NAP-CC-FP-HC-R10 | 41 | 1.025 | 368.6686 | 0.21433 | 0.72461 | 0.48459 | 0.36715 | 0.82926 | 657.375 | 338.775 | 1854.725 | 2852.275 | 0 | 10702.8023 | 528.6331 | 2219.389 | 19.0005 | 86.8053 | 32.4973 | 1.438 | 3.0957 | 12990.4943 | 0.72821 | -5174.0884
74 | C-SOK-NAP-CC-FP-HC-R10 | 41 | 2.05 | 407.7004 | 0.23702 | 0.72376 | 0.57622 | 0.43232 | 0.8523 | 653.925 | 385.8 | 1854.725 | 2801.075 | 0 | 9248.6281 | 527.0169 | 2219.4225 | 19.1773 | 83.8735 | 32.6257 | 1.5147 | 3.0956 | 13014.0574 | 0.74751 | -5011.1685
75 | C-SOK-NAP-CC-FP-HC-R10 | 41 | 3.075 | 430.9753 | 0.25055 | 0.72309 | 0.63759 | 0.47261 | 0.85738 | 653.55 | 416.475 | 1854.725 | 2788.3 | 0 | 8344.6426 | 527.1887 | 2219.3788 | 19.1903 | 82.083 | 32.6075 | 1.5619 | 3.0953 | 13009.5452 | 0.75845 | -4931.7814
76 | C-SOK-NAP-CC-FP-HC-R600 | 16.5 | 0.413 | 625.5277 | 0.36365 | 0.72932 | 0.22323 | 0.13211 | 0.77148 | 763.925 | 205 | 2104.7 | 2192.125 | 0 | 12420.6446 | 574.3922 | 2420.2181 | 18.1294 | 88.4726 | 25.3272 | 1.1854 | 3.1158 | 9149.7488 | 0.62069 | -8939.5947
77 | C-SOK-NAP-CC-FP-HC-R600 | 16.5 | 0.825 | 655.0826 | 0.38083 | 0.72907 | 0.22336 | 0.16809 | 0.81286 | 765.6 | 201.3 | 2104.7 | 2165.975 | 0 | 12081.4637 | 574.7758 | 2420.1845 | 18.1997 | 86.5744 | 25.4394 | 1.2055 | 3.1155 | 9232.2947 | 0.63189 | -8898.9685
78 | C-SOK-NAP-CC-FP-HC-R600 | 16.5 | 1.238 | 666.9041 | 0.38771 | 0.72901 | 0.22728 | 0.19467 | 0.81525 | 766.125 | 202.15 | 2104.7 | 2179.2 | 0 | 11918.8293 | 574.4024 | 2420.1524 | 18.1891 | 85.766 | 25.4815 | 1.221 | 3.1155 | 9249.837 | 0.63712 | -8919.9212
79 | C-SOK-NAP-CC-FP-HC-R600 | 22.5 | 0.563 | 542.1666 | 0.31519 | 0.72871 | 0.31547 | 0.20503 | 0.81802 | 748.925 | 269.525 | 2104.7 | 2378.55 | 0 | 11009.3144 | 553.8743 | 2420.2115 | 18.7361 | 84.1467 | 26.3155 | 1.2407 | 3.1163 | 9241.2293 | 0.64913 | -8596.5565
80 | C-SOK-NAP-CC-FP-HC-R600 | 22.5 | 1.125 | 572.6541 | 0.33291 | 0.72842 | 0.33677 | 0.25897 | 0.84591 | 748.575 | 277.525 | 2104.7 | 2362.625 | 0 | 10443.7593 | 553.9716 | 2420.2352 | 18.7202 | 82.6271 | 26.4185 | 1.2804 | 3.1165 | 9307.0557 | 0.66393 | -8584.7437
81 | C-SOK-NAP-CC-FP-HC-R600 | 22.5 | 1.688 | 587.7321 | 0.34168 | 0.72818 | 0.35355 | 0.29717 | 0.84944 | 748.875 | 285.1 | 2104.7 | 2362.25 | 0 | 10098.554 | 553.7206 | 2420.2678 | 18.6844 | 81.4812 | 26.441 | 1.2989 | 3.1162 | 9314.9936 | 0.67379 | -8604.5614
82 | C-SOK-NAP-CC-FP-HC-R600 | 29 | 0.725 | 455.4312 | 0.26477 | 0.72895 | 0.36543 | 0.27536 | 0.84625 | 741.3 | 305.3 | 2104.7 | 2585.65 | 0 | 10087.2162 | 548.4821 | 2420.2331 | 18.6534 | 82.4227 | 26.6504 | 1.2917 | 3.1164 | 9304.7875 | 0.67396 | -8601.1179
83 | C-SOK-NAP-CC-FP-HC-R600 | 29 | 1.45 | 487.7906 | 0.28358 | 0.72833 | 0.41829 | 0.33949 | 0.86953 | 737.8 | 331.125 | 2104.7 | 2562.85 | 0 | 9192.1848 | 547.3273 | 2420.2672 | 18.648 | 80.2811 | 26.7852 | 1.346 | 3.1174 | 9354.1903 | 0.69683 | -8633.3176
84 | C-SOK-NAP-CC-FP-HC-R600 | 29 | 2.175 | 509.4872 | 0.29619 | 0.72804 | 0.447 | 0.39864 | 0.87322 | 738.425 | 345.775 | 2104.7 | 2545.3 | 0 | 8636.5008 | 550.8361 | 2420.1325 | 18.4416 | 79.2978 | 26.6354 | 1.3809 | 3.1168 | 9357.5912 | 0.70509 | -8555.1431
85 | C-SOK-NAP-CC-FP-HC-R60 | 35 | 0.875 | 397.9237 | 0.23133 | 0.72843 | 0.42366 | 0.3304 | 0.86422 | 729.8 | 336.925 | 2104.7 | 2740.5 | 0 | 9204.8126 | 538.0265 | 2420.3611 | 18.9138 | 80.4099 | 27.1834 | 1.3387 | 3.1175 | 9344.8115 | 0.70615 | -8831.1863
86 | C-SOK-NAP-CC-FP-HC-R60 | 35 | 1.75 | 434.5945 | 0.25265 | 0.72788 | 0.49134 | 0.4092 | 0.88275 | 727.25 | 373.925 | 2104.7 | 2716.85 | 0 | 8120.2056 | 540.005 | 2420.2844 | 18.7936 | 78.2478 | 27.1657 | 1.4023 | 3.1184 | 9386.0136 | 0.72123 | -8698.6309
87 | C-SOK-NAP-CC-FP-HC-R60 | 35 | 2.625 | 459.2436 | 0.26698 | 0.72743 | 0.54023 | 0.47095 | 0.88892 | 727.05 | 400.55 | 2104.7 | 2687.975 | 0 | 7345.6145 | 542.84 | 2420.3383 | 18.6374 | 76.8651 | 27.0383 | 1.4492 | 3.118 | 9386.3581 | 0.73103 | -8585.8542
88 | C-SOK-NAP-CC-FP-HC-R60 | 41 | 1.025 | 357.636 | 0.20791 | 0.7284 | 0.46266 | 0.37732 | 0.8767 | 722.375 | 357.15 | 2104.7 | 2866.75 | 0 | 8563.1676 | 541.1628 | 2420.2888 | 18.7078 | 79.219 | 27.0922 | 1.3767 | 3.1182 | 9373.4552 | 0.71658 | -8780.5749
89 | C-SOK-NAP-CC-FP-HC-R60 | 41 | 2.05 | 394.3754 | 0.22927 | 0.72742 | 0.54921 | 0.46603 | 0.89489 | 719.45 | 407.425 | 2104.7 | 2835.175 | 0 | 7253.6355 | 537.3414 | 2420.3744 | 18.892 | 76.3989 | 27.323 | 1.4472 | 3.1188 | 9407.5015 | 0.73386 | -8630.5912
90 | C-SOK-NAP-CC-FP-HC-R60 | 41 | 3.075 | 419.4206 | 0.24383 | 0.72674 | 0.61373 | 0.53419 | 0.90353 | 717.925 | 443.375 | 2104.7 | 2803.7 | 0 | 6287.6926 | 538.1555 | 2420.4188 | 18.8332 | 74.6055 | 27.2951 | 1.5083 | 3.1185 | 9413.4318 | 0.74704 | -8555.9078
91 | C-SOK-NAP-CC-FP-WC-R100 | 23 | 0.6 | 590.5968 | 0.34335 | 0.70932 | 0.2752 | 0.16263 | 0.73369 | 1077.325 | 302.325 | 1854.725 | 2282.475 | 25.8283 | 20816.9242 | 891.5636 | 3099.0181 | 13.2864 | 120.6438 | 27.8211 | 1.1677 | 3.0588 | 17693.9187 | 0.69728 | -14811.6851
92 | C-SOK-NAP-CC-FP-WC-R100 | 23 | 1.15 | 618.9351 | 0.35982 | 0.70916 | 0.27761 | 0.19531 | 0.76111 | 1077.2 | 311.175 | 1854.725 | 2260.625 | 25.8347 | 20254.4421 | 895.6148 | 3098.9597 | 13.2341 | 118.3056 | 27.7704 | 1.1935 | 3.0588 | 17758.037 | 0.70956 | -14858.7896
93 | C-SOK-NAP-CC-FP-WC-R100 | 23 | 1.75 | 631.1007 | 0.36689 | 0.70879 | 0.2797 | 0.21461 | 0.76457 | 1077.7 | 318.275 | 1854.725 | 2258.55 | 25.8477 | 19983.0158 | 894.7948 | 3098.9803 | 13.2476 | 117.2757 | 27.81 | 1.2095 | 3.0595 | 17771.1763 | 0.71614 | -14898.8339
94 | C-SOK-NAP-CC-FP-WC-R100 | 32 | 0.8 | 491.6878 | 0.28584 | 0.70602 | 0.35485 | 0.23336 | 0.76971 | 1074.1 | 385.575 | 1854.725 | 2508.8 | 25.8604 | 18808.4692 | 884.4049 | 3098.9924 | 13.3045 | 115.9624 | 28.1137 | 1.231 | 3.0588 | 17772.7109 | 0.73838 | -14879.5221
95 | C-SOK-NAP-CC-FP-WC-R100 | 32 | 1.6 | 524.8879 | 0.30515 | 0.70531 | 0.37927 | 0.27642 | 0.79787 | 1073.825 | 425.925 | 1854.725 | 2488.725 | 25.8903 | 17836.7196 | 887.5991 | 3099.1098 | 13.2418 | 113.9477 | 28.0734 | 1.2754 | 3.0594 | 17821.9107 | 0.7534 | -14864.2376
96 | C-SOK-NAP-CC-FP-WC-R100 | 32 | 2.4 | 542.6216 | 0.31545 | 0.70498 | 0.39737 | 0.29788 | 0.80147 | 1074.875 | 453.525 | 1854.725 | 2478.825 | 25.9149 | 17332.2635 | 888.028 | 3099.0469 | 13.2332 | 113.0661 | 28.0718 | 1.2991 | 3.0603 | 17830.0948 | 0.75884 | -14826.2921
97 | C-SOK-NAP-CC-FP-WC-R100 | 40.5 | 1 | 426.4727 | 0.24793 | 0.70369 | 0.41196 | 0.29004 | 0.79574 | 1067.55 | 442.075 | 1854.725 | 2678.025 | 25.8903 | 17286.7821 | 880.0005 | 3099.164 | 13.3675 | 112.4005 | 28.2999 | 1.2839 | 3.0601 | 17820.5351 | 0.76628 | -14976.6316
98 | C-SOK-NAP-CC-FP-WC-R100 | 40.5 | 2.05 | 462.859 | 0.26908 | 0.70241 | 0.4569 | 0.34312 | 0.8229 | 1069.075 | 513.15 | 1854.725 | 2651.275 | 25.9318 | 15935.8799 | 884.047 | 3099.2019 | 13.2799 | 110.2575 | 28.2266 | 1.3461 | 3.06 | 17865.541 | 0.78173 | -14921.1854
99 | C-SOK-NAP-CC-FP-WC-R100 | 40.5 | 3.05 | 485.3068 | 0.28213 | 0.70105 | 0.4934 | 0.37367 | 0.82152 | 1072.6 | 562.975 | 1854.725 | 2638.675 | 25.9817 | 15118.5766 | 885.5284 | 3099.1832 | 13.2415 | 109.0983 | 28.1831 | 1.3821 | 3.0601 | 17865.8565 | 0.78844 | -14863.5037
100 | C-SOK-NAP-CC-FP-WC-R10 | 49 | 1.25 | 378.8024 | 0.22022 | 0.70191 | 0.45216 | 0.34166 | 0.81667 | 1061.5 | 485.425 | 1854.725 | 2830.7 | 25.9065 | 16053.5795 | 878.1118 | 3099.1582 | 13.4336 | 109.3834 | 28.4001 | 1.3343 | 3.0602 | 17861.3562 | 0.78345 | -15014.4131
101 | C-SOK-NAP-CC-FP-WC-R10 | 49 | 2.45 | 416.1188 | 0.24191 | 0.69932 | 0.51662 | 0.39914 | 0.84009 | 1068.075 | 580.775 | 1854.725 | 2783.075 | 25.9818 | 14427.3802 | 884.7756 | 3099.1031 | 13.3117 | 106.9141 | 28.2418 | 1.4086 | 3.0603 | 17900.2241 | 0.79717 | -14896.2028
102 | C-SOK-NAP-CC-FP-WC-R10 | 49 | 3.7 | 441.0686 | 0.25642 | 0.69718 | 0.57232 | 0.43787 | 0.84208 | 1074.425 | 652.975 | 1854.725 | 2765.6 | 26.05 | 13246.8815 | 886.4124 | 3099.1488 | 13.2601 | 105.3761 | 28.1858 | 1.4652 | 3.0604 | 17892.5612 | 0.80819 | -14849.3953
103 | C-SOK-NAP-CC-FP-WC-R10 | 58 | 1.45 | 339.9471 | 0.19763 | 0.69924 | 0.4865 | 0.38611 | 0.83177 | 1063.925 | 527.875 | 1854.725 | 2947.725 | 25.9525 | 15018.752 | 883.7068 | 3099.1522 | 13.4299 | 105.8352 | 28.2641 | 1.3764 | 3.0606 | 17889.9639 | 0.79402 | -14983.3557
104 | C-SOK-NAP-CC-FP-WC-R10 | 58 | 2.9 | 377.8953 | 0.21969 | 0.69578 | 0.57181 | 0.45121 | 0.85521 | 1072.75 | 646.625 | 1854.725 | 2899.3 | 26.0505 | 13032.1609 | 890.4235 | 3099.2037 | 13.3073 | 102.9597 | 28.1013 | 1.4681 | 3.0607 | 17923.8995 | 0.8094 | -14847.1339
105 | C-SOK-NAP-CC-FP-WC-R10 | 58 | 4.35 | 403.8052 | 0.23475 | 0.69316 | 0.64324 | 0.49308 | 0.86004 | 1079.725 | 730.025 | 1854.725 | 2871.95 | 26.1277 | 11590.8949 | 895.2268 | 3099.0748 | 13.2179 | 100.5599 | 27.953 | 1.5313 | 3.0601 | 17918.4015 | 0.82072 | -14779.9385
106 | C-SOK-NAP-CC-FP-WC-R600 | 23 | 0.6 | 589.8441 | 0.34291 | 0.70805 | 0.25477 | 0.15813 | 0.79303 | 1214.575 | 315.525 | 2104.7 | 2267.6 | 28.7967 | 17028.7803 | 941.7145 | 3395.541 | 13.2339 | 110.6929 | 22.2073 | 1.1078 | 3.0833 | 12376.9208 | 0.69725 | -21283.6463
107 | C-SOK-NAP-CC-FP-WC-R600 | 23 | 1.15 | 615.1222 | 0.3576 | 0.70801 | 0.25807 | 0.19798 | 0.82143 | 1213.825 | 327 | 2104.7 | 2254.125 | 28.8019 | 16577.8697 | 945.5518 | 3395.6364 | 13.1885 | 108.3037 | 22.2155 | 1.129 | 3.0836 | 12469.1001 | 0.70717 | -21450.9284
108 | C-SOK-NAP-CC-FP-WC-R600 | 23 | 1.75 | 626.5819 | 0.36427 | 0.70771 | 0.26102 | 0.22981 | 0.82141 | 1214.775 | 337.575 | 2104.7 | 2266.525 | 28.8131 | 16345.6384 | 944.506 | 3395.6002 | 13.1929 | 107.1757 | 22.2551 | 1.1474 | 3.0837 | 12485.7517 | 0.71193 | -21510.611
109 | C-SOK-NAP-CC-FP-WC-R600 | 32 | 0.8 | 484.4792 | 0.28165 | 0.70497 | 0.33278 | 0.2398 | 0.82828 | 1210.2 | 407.925 | 2104.7 | 2503 | 28.8197 | 15259.9779 | 933.1516 | 3395.5912 | 13.2466 | 105.3938 | 22.5044 | 1.1649 | 3.0824 | 12486.4582 | 0.735 | -21513.7365
110 | C-SOK-NAP-CC-FP-WC-R600 | 32 | 1.6 | 516.4847 | 0.30026 | 0.70479 | 0.35841 | 0.29467 | 0.85209 | 1208.3 | 453.6 | 2104.7 | 2489 | 28.8473 | 14422.4444 | 937.5906 | 3395.5788 | 13.1704 | 103.4004 | 22.4812 | 1.2065 | 3.0835 | 12559.5883 | 0.74507 | -21556.9939
111 | C-SOK-NAP-CC-FP-WC-R600 | 32 | 2.4 | 535.1092 | 0.31109 | 0.70406 | 0.37806 | 0.3361 | 0.85557 | 1210.25 | 488 | 2104.7 | 2478.2 | 28.8753 | 13874.4028 | 937.4296 | 3395.6922 | 13.1567 | 102.3321 | 22.4881 | 1.2394 | 3.0837 | 12561.6965 | 0.75222 | -21514.011
112 | C-SOK-NAP-CC-FP-WC-R600 | 40.5 | 1 | 415.0638 | 0.2413 | 0.70325 | 0.38673 | 0.30332 | 0.84918 | 1201.9 | 466.8 | 2104.7 | 2688.25 | 28.8436 | 14004.8241 | 928.9236 | 3395.7051 | 13.2795 | 102.0038 | 22.6732 | 1.211 | 3.0837 | 12554.5999 | 0.75903 | -21717.7178
113 | C-SOK-NAP-CC-FP-WC-R600 | 40.5 | 2.05 | 449.6806 | 0.26142 | 0.7015 | 0.43564 | 0.37029 | 0.87077 | 1204.875 | 550.3 | 2104.7 | 2673.9 | 28.8963 | 12783.3638 | 932.7306 | 3395.6877 | 13.1852 | 100.0753 | 22.6423 | 1.2751 | 3.0836 | 12610.3564 | 0.77266 | -21717.1197
114 | C-SOK-NAP-CC-FP-WC-R600 | 40.5 | 3.05 | 475.2555 | 0.27629 | 0.70057 | 0.47195 | 0.42688 | 0.87513 | 1206.95 | 605.525 | 2104.7 | 2646.2 | 28.9434 | 11897.8639 | 934.734 | 3395.7134 | 13.1454 | 98.6872 | 22.6019 | 1.3222 | 3.0841 | 12613.5777 | 0.77836 | -21576.6771
115 | C-SOK-NAP-CC-FP-WC-R60 | 49 | 1.25 | 366.3954 | 0.21301 | 0.70065 | 0.42967 | 0.35762 | 0.86707 | 1200.65 | 521.375 | 2104.7 | 2844.925 | 28.8904 | 12982.42 | 928.5799 | 3395.7807 | 13.2969 | 99.3529 | 22.7356 | 1.2563 | 3.0843 | 12606.5778 | 0.77366 | -21802.2958
116 | C-SOK-NAP-CC-FP-WC-R60 | 49 | 2.45 | 400.7339 | 0.23297 | 0.69859 | 0.49125 | 0.43442 | 0.88498 | 1204.925 | 623.025 | 2104.7 | 2816.7 | 28.9541 | 11537.7602 | 933.4405 | 3395.6885 | 13.1971 | 97.0153 | 22.6702 | 1.328 | 3.0842 | 12652.2574 | 0.78536 | -21721.1738
117 | C-SOK-NAP-CC-FP-WC-R60 | 49 | 3.7 | 427.6332 | 0.24861 | 0.69642 | 0.5487 | 0.49775 | 0.89291 | 1210.925 | 703.425 | 2104.7 | 2784.2 | 29.0295 | 10291.3241 | 936.3406 | 3395.6496 | 13.1247 | 95.0436 | 22.6089 | 1.3913 | 3.0842 | 12656.7418 | 0.79778 | -21665.6273
118 | C-SOK-NAP-CC-FP-WC-R60 | 58 | 1.45 | 326.5432 | 0.18984 | 0.69855 | 0.46373 | 0.40507 | 0.87907 | 1200.675 | 567.3 | 2104.7 | 2969.825 | 28.918 | 12151.0945 | 932.9081 | 3395.8072 | 13.2967 | 96.3248 | 22.6727 | 1.2942 | 3.0839 | 12643.3708 | 0.78139 | -21797.4512
119 | C-SOK-NAP-CC-FP-WC-R60 | 58 | 2.9 | 362.0447 | 0.21048 | 0.6953 | 0.54757 | 0.4907 | 0.89856 | 1208.625 | 697.775 | 2104.7 | 2941.2 | 29.0219 | 10328.554 | 939.0644 | 3395.7266 | 13.1651 | 93.394 | 22.5734 | 1.3806 | 3.0843 | 12681.9497 | 0.79666 | -21698.0376
120 | C-SOK-NAP-CC-FP-WC-R60 | 58 | 4.35 | 388.1695 | 0.22566 | 0.69281 | 0.61915 | 0.55526 | 0.90682 | 1216.1 | 788.7 | 2104.7 | 2910.75 | 29.1151 | 8865.2212 | 943.8496 | 3395.7521 | 13.0628 | 90.8574 | 22.4756 | 1.4506 | 3.0845 | 12690.8291 | 0.81076 | -21689.6995
121 | C-SOK-NAP-FC-ET-HC-OFF0 | 11.5 | 0.288 | 799.3904 | 0.46473 | 0.63191 | 0.43072 | 0.52719 | 1 | 868.4 | 364.05 | 2468.675 | 1900.75 | 0 | 5480.3853 | 688.3333 | 2226.4938 | 9.8041 | 53.997 | 9.2808 | 1.0755 | 2.7159 | 641.83 | 0.46288 | 4937.7728
122 | C-SOK-NAP-FC-ET-HC-OFF0 | 11.5 | 0.575 | 820.4199 | 0.47695 | 0.6317 | 0.43933 | 0.64974 | 1 | 868.275 | 372.125 | 2468.675 | 1854.125 | 0 | 5324.9779 | 683.9254 | 2226.9688 | 9.8939 | 54.3309 | 9.3405 | 1.1045 | 2.7153 | 641.83 | 0.46779 | 5021.3327
123 | C-SOK-NAP-FC-ET-HC-OFF0 | 11.5 | 0.863 | 832.283 | 0.48385 | 0.63159 | 0.44641 | 0.69176 | 1 | 868.975 | 377.875 | 2468.675 | 1831.25 | 0 | 5234.6526 | 684.509 | 2226.8283 | 9.8912 | 54.4188 | 9.3327 | 1.1143 | 2.7155 | 641.83 | 0.47074 | 5065.6388
124 | C-SOK-NAP-FC-ET-HC-OFF0 | 15.5 | 0.388 | 710.9303 | 0.4133 | 0.63287 | 0.58911 | 0.6829 | 1 | 839.325 | 476.825 | 2468.675 | 2111.975 | 0 | 3933.9195 | 630.4074 | 2226.7076 | 10.6078 | 56.155 | 10.1324 | 1.1559 | 2.7153 | 641.83 | 0.52514 | 5232.7198
125 | C-SOK-NAP-FC-ET-HC-OFF0 | 15.5 | 0.775 | 736.5313 | 0.42818 | 0.63295 | 0.61392 | 0.7939 | 1 | 836.9 | 496.5 | 2468.675 | 2055 | 0 | 3636.9738 | 629.0349 | 2226.5336 | 10.6407 | 59.1591 | 10.1545 | 1.1917 | 2.7155 | 641.83 | 0.5328 | 5333.714
126 | C-SOK-NAP-FC-ET-HC-OFF0 | 15.5 | 1.163 | 750.5852 | 0.43636 | 0.6331 | 0.62819 | 0.8321 | 1 | 834.775 | 508.075 | 2468.675 | 2025.45 | 0 | 3482.1169 | 629.2921 | 2226.9455 | 10.6434 | 60.2882 | 10.1504 | 1.2015 | 2.715 | 641.83 | 0.53595 | 5398.7922
127 | C-SOK-NAP-FC-ET-HC-OFF0 | 20 | 0.5 | 622.8084 | 0.36207 | 0.634 | 0.70452 | 0.79851 | 1 | 812.7 | 555.25 | 2468.675 | 2335.725 | 0 | 2807.1625 | 575.3554 | 2226.2659 | 11.6103 | 60.495 | 11.1022 | 1.2227 | 2.7159 | 641.83 | 0.55374 | 5558.6585
128 | C-SOK-NAP-FC-ET-HC-OFF0 | 20 | 1 | 648.1258 | 0.37679 | 0.63429 | 0.73904 | 0.88987 | 1 | 807.275 | 580.25 | 2468.675 | 2275.2 | 0 | 2434.6273 | 574.1793 | 2226.2102 | 11.6443 | 66.3609 | 11.1248 | 1.2614 | 2.716 | 641.83 | 0.56053 | 5696.6417
129 | C-SOK-NAP-FC-ET-HC-OFF0 | 20 | 1.5 | 661.1123 | 0.38434 | 0.63459 | 0.76289 | 0.95042 | 1 | 803.5 | 598.825 | 2468.675 | 2242.7 | 0 | 2178.7596 | 573.2058 | 2226.615 | 11.6442 | 72.6231 | 11.144 | 1.2873 | 2.7155 | 641.83 | 0.56856 | 5704.6075
130 | C-SOK-NAP-FC-ET-HC-OFF | 24 | 0.6 | 556.0286 | 0.32325 | 0.63483 | 0.73032 | 0.86128 | 1 | 806.7 | 584.85 | 2468.675 | 2516.1 | 0 | 2530.1817 | 565.5461 | 2226.4837 | 11.8234 | 68.439 | 11.2959 | 1.2539 | 2.716 | 641.83 | 0.53682 | 6181.02
131 | C-SOK-NAP-FC-ET-HC-OFF | 24 | 1.2 | 579.1947 | 0.33672 | 0.63536 | 0.77473 | 0.94676 | 1 | 798.85 | 616.15 | 2468.675 | 2452.9 | 0 | 2071.3302 | 562.5701 | 2226.5331 | 11.887 | 77.6656 | 11.3542 | 1.2979 | 2.7155 | 641.83 | 0.54773 | 6286.9094
132 | C-SOK-NAP-FC-ET-HC-OFF | 24 | 1.8 | 587.5615 | 0.34158 | 0.63606 | 0.81689 | 0.99691 | 1 | 790.4 | 640.075 | 2468.675 | 2428.35 | 0 | 1656.0958 | 560.0328 | 2226.4181 | 11.8658 | 87.8448 | 11.4056 | 1.3262 | 2.7156 | 641.83 | 0.56866 | 6082.5291
133 | C-SOK-NAP-FC-ET-HC-OFF | 28.5 | 0.713 | 471.9624 | 0.27438 | 0.6369 | 0.79284 | 0.916 | 1 | 787.45 | 618.125 | 2468.675 | 2729.6 | 0 | 1923.1452 | 544.084 | 2226.3184 | 12.0938 | 74.5875 | 11.742 | 1.2946 | 2.7163 | 641.83 | 0.57556 | 5709.1006
134 | C-SOK-NAP-FC-ET-HC-OFF | 28.5 | 1.425 | 491.2867 | 0.28561 | 0.63779 | 0.85437 | 0.98147 | 1 | 774.1 | 657.625 | 2468.675 | 2671.675 | 0 | 1323.9514 | 538.7555 | 2226.1824 | 12.181 | 87.1241 | 11.8569 | 1.3365 | 2.7162 | 641.83 | 0.59473 | 5674.4314
135 | C-SOK-NAP-FC-ET-HC-OFF | 28.5 | 2.138 | 502.9043 | 0.29236 | 0.63814 | 0.88449 | 0.99691 | 1 | 768.65 | 677.175 | 2468.675 | 2641.15 | 0 | 1041.9225 | 536.2989 | 2226.1688 | 12.2387 | 93.6184 | 11.9098 | 1.3548 | 2.7158 | 641.83 | 0.60024 | 5729.602
136 | C-SOK-NAP-FC-ET-HC-R100 | 11.5 | 0.288 | 766.4109 | 0.44556 | 0.64247 | 0.25127 | 0.16123 | 0.74034 | 618.05 | 187.125 | 2227.75 | 1979.9 | 0 | 9643.6544 | 554.0997 | 1703.0421 | 11.9802 | 65.6445 | 18.7611 | 1.2628 | 2.7861 | 7377.0756 | 0.49301 | 2135.177
137 | C-SOK-NAP-FC-ET-HC-R100 | 11.5 | 0.575 | 797.3662 | 0.46355 | 0.64185 | 0.25955 | 0.19058 | 0.76635 | 619.65 | 190.575 | 2227.75 | 1904.5 | 0 | 9388.5551 | 551.7205 | 1703.198 | 12.135 | 64.9271 | 18.8483 | 1.2881 | 2.7863 | 7385.4874 | 0.50343 | 2279.8289
138 | C-SOK-NAP-FC-ET-HC-R100 | 11.5 | 0.863 | 812.0484 | 0.47209 | 0.64154 | 0.27134 | 0.20329 | 0.76788 | 620.425 | 195.25 | 2227.75 | 1872.425 | 0 | 9248.4186 | 550.6997 | 1703.2488 | 12.1929 | 64.5035 | 18.8815 | 1.2999 | 2.7864 | 7386.4391 | 0.50983 | 2307.0498
139 | C-SOK-NAP-FC-ET-HC-R100 | 15.5 | 0.388 | 677.1153 | 0.39364 | 0.64507 | 0.37679 | 0.24794 | 0.78265 | 594.325 | 251.65 | 2227.75 | 2198.4 | 0 | 8274.9058 | 512.4737 | 1702.995 | 12.9591 | 63.7962 | 20.1347 | 1.3481 | 2.7863 | 7389.9237 | 0.54314 | 2559.686
140 | C-SOK-NAP-FC-ET-HC-R100 | 15.5 | 0.775 | 713.5174 | 0.41481 | 0.64468 | 0.40419 | 0.28963 | 0.80509 | 595.125 | 263.825 | 2227.75 | 2110.075 | 0 | 7840.1352 | 513.7381 | 1702.9936 | 12.9901 | 62.9623 | 20.0991 | 1.3862 | 2.7867 | 7394.1304 | 0.55557 | 2734.6826
141 | C-SOK-NAP-FC-ET-HC-R100 | 15.5 | 1.163 | 730.916 | 0.42492 | 0.64417 | 0.42784 | 0.30772 | 0.80199 | 596.35 | 273.4 | 2227.75 | 2065.875 | 0 | 7607.9074 | 515.0494 | 1702.8976 | 12.9808 | 62.3403 | 20.0518 | 1.4033 | 2.7865 | 7393.5843 | 0.56318 | 2760.7314
142 | C-SOK-NAP-FC-ET-HC-R100 | 20 | 0.5 | 598.6906 | 0.34805 | 0.64648 | 0.45611 | 0.33316 | 0.81366 | 579.8 | 289.975 | 2227.75 | 2405.05 | 0 | 7257.4795 | 478.6046 | 1702.7341 | 14 | 64.0175 | 21.403 | 1.4286 | 2.7871 | 7397.5711 | 0.56055 | 3100.7585
143 | C-SOK-NAP-FC-ET-HC-R100 | 20 | 1 | 637.8893 | 0.37084 | 0.64634 | 0.50906 | 0.38745 | 0.83239 | 578.275 | 312.675 | 2227.75 | 2303.15 | 0 | 6601.1262 | 480.9798 | 1702.6808 | 13.9956 | 62.7299 | 21.3144 | 1.4819 | 2.7868 | 7400.5923 | 0.57783 | 3271.0821
144 | C-SOK-NAP-FC-ET-HC-R100 | 20 | 1.5 | 658.8806 | 0.38304 | 0.64589 | 0.55169 | 0.41973 | 0.82998 | 578.15 | 331.325 | 2227.75 | 2249.375 | 0 | 6174.6677 | 482.7931 | 1702.7028 | 13.9638 | 61.7426 | 21.2414 | 1.5172 | 2.7873 | 7398.4411 | 0.59206 | 3256.2862
145 | C-SOK-NAP-FC-ET-HC-R10 | 24 | 0.6 | 546.8098 | 0.31789 | 0.64681 | 0.47777 | 0.39848 | 0.83438 | 580.025 | 306.875 | 2227.75 | 2547.3 | 0 | 6746.3827 | 477.8378 | 1702.7783 | 13.8299 | 65.9267 | 21.4399 | 1.4843 | 2.7866 | 7401.8511 | 0.55039 | 3789.7522
146 | C-SOK-NAP-FC-ET-HC-R10 | 24 | 1.2 | 585.5003 | 0.34038 | 0.64675 | 0.55389 | 0.45923 | 0.85541 | 576.025 | 338.15 | 2227.75 | 2445.475 | 0 | 5901.4748 | 477.0749 | 1702.5796 | 13.9655 | 64.1139 | 21.4789 | 1.5532 | 2.7872 | 7406.3037 | 0.57454 | 3919.1396
147 | C-SOK-NAP-FC-ET-HC-R10 | 24 | 1.8 | 608.053 | 0.35349 | 0.64649 | 0.60586 | 0.49981 | 0.85648 | 574.6 | 359.875 | 2227.75 | 2389.75 | 0 | 5363.4771 | 478.9642 | 1702.7388 | 13.9503 | 62.7546 | 21.4024 | 1.5922 | 2.7869 | 7405.2721 | 0.59021 | 3924.4479
148 | C-SOK-NAP-FC-ET-HC-R10 | 28.5 | 0.713 | 469.8139 | 0.27313 | 0.64877 | 0.51924 | 0.45774 | 0.85683 | 568.7 | 319.85 | 2227.75 | 2735.8 | 0 | 6122.4338 | 465.8243 | 1702.6702 | 13.8776 | 66.7647 | 21.9326 | 1.5441 | 2.7869 | 7405.9927 | 0.58488 | 3502.8693
149 | C-SOK-NAP-FC-ET-HC-R10 | 28.5 | 1.425 | 509.2392 | 0.29605 | 0.64926 | 0.61488 | 0.53109 | 0.86935 | 562.075 | 360.275 | 2227.75 | 2629.75 | 0 | 5110.4679 | 466.6902 | 1702.6573 | 13.9814 | 64.5779 | 21.9063 | 1.6282 | 2.7869 | 7410.9776 | 0.60933 | 3643.2839
150 | C-SOK-NAP-FC-ET-HC-R10 | 28.5 | 2.138 | 533.3475 | 0.31006 | 0.64892 | 0.678 | 0.58708 | 0.87447 | 559.35 | 386.85 | 2227.75 | 2568.9 | 0 | 4416.6515 | 464.9397 | 1702.7297 | 14.126 | 63.2886 | 21.9788 | 1.6938 | 2.7868 | 7411.1231 | 0.62767 | 3646.2569
151 | C-SOK-NAP-FC-ET-HC-R600 | 11.5 | 0.288 | 769.1202 | 0.44713 | 0.64552 | 0.23656 | 0.154 | 0.79371 | 662.175 | 190.55 | 2346.175 | 1975.075 | 0 | 8078.8681 | 555.7828 | 1803.5724 | 12.0185 | 62.3442 | 15.9768 | 1.2286 | 2.7982 | 5313.9712 | 0.49529 | 1263.9266
152 | C-SOK-NAP-FC-ET-HC-R600 | 11.5 | 0.575 | 802.5869 | 0.46659 | 0.64492 | 0.24563 | 0.20177 | 0.81761 | 663.7 | 194 | 2346.175 | 1894.1 | 0 | 7837.1042 | 552.2765 | 1803.6097 | 12.1989 | 61.6616 | 16.094 | 1.2587 | 2.7975 | 5331.3442 | 0.50327 | 1435.9148
153 | C-SOK-NAP-FC-ET-HC-R600 | 11.5 | 0.863 | 818.0038 | 0.47555 | 0.64447 | 0.25775 | 0.22462 | 0.81977 | 664.9 | 199.75 | 2346.175 | 1857.7 | 0 | 7693.4654 | 551.5404 | 1803.3954 | 12.2404 | 61.1868 | 16.1156 | 1.2738 | 2.7978 | 5332.8831 | 0.50974 | 1467.8465
154 | C-SOK-NAP-FC-ET-HC-R600 | 15.5 | 0.388 | 674.128 | 0.39191 | 0.64801 | 0.35759 | 0.25912 | 0.83556 | 637.6 | 257.825 | 2346.175 | 2205.55 | 0 | 6826.0284 | 512.2234 | 1803.1314 | 12.9449 | 59.935 | 17.2217 | 1.3097 | 2.7983 | 5338.1684 | 0.53871 | 1716.877
155 | C-SOK-NAP-FC-ET-HC-R600 | 15.5 | 0.775 | 713.0042 | 0.41451 | 0.64765 | 0.38562 | 0.31883 | 0.85869 | 638.1 | 270.55 | 2346.175 | 2106.525 | 0 | 6419.6949 | 514.4646 | 1803.3289 | 12.9444 | 59.4208 | 17.1761 | 1.3537 | 2.7979 | 5350.5159 | 0.54755 | 1952.658
156 | C-SOK-NAP-FC-ET-HC-R600 | 15.5 | 1.163 | 733.6799 | 0.42653 | 0.64712 | 0.41116 | 0.36296 | 0.8604 | 639.575 | 283.25 | 2346.175 | 2055.8 | 0 | 6131.275 | 516.0978 | 1803.1201 | 12.9022 | 58.8891 | 17.1274 | 1.379 | 2.7986 | 5349.6529 | 0.55799 | 1984.8975
157 | C-SOK-NAP-FC-ET-HC-R600 | 20 | 0.5 | 590.77 | 0.34345 | 0.64947 | 0.43468 | 0.35345 | 0.86724 | 622.025 | 296.975 | 2346.175 | 2423.75 | 0 | 5951.5925 | 480.1792 | 1803.1276 | 13.7986 | 60.1776 | 18.2598 | 1.3827 | 2.7984 | 5352.816 | 0.5503 | 2288.7641
158 | C-SOK-NAP-FC-ET-HC-R600 | 20 | 1 | 631.1433 | 0.36692 | 0.64923 | 0.49047 | 0.43707 | 0.88123 | 620.725 | 323.65 | 2346.175 | 2319.025 | 0 | 5317.0009 | 481.3809 | 1802.8219 | 13.8224 | 59.5253 | 18.2367 | 1.4436 | 2.7991 | 5361.7405 | 0.56634 | 2482.0049
159 | C-SOK-NAP-FC-ET-HC-R600 | 20 | 1.5 | 653.9514 | 0.38018 | 0.64897 | 0.53194 | 0.4874 | 0.88823 | 620.025 | 343.525 | 2346.175 | 2260.45 | 0 | 4882.4775 | 483.8937 | 1802.8865 | 13.7323 | 58.8896 | 18.1548 | 1.4851 | 2.7987 | 5363.1225 | 0.58006 | 2519.7381
160 | C-SOK-NAP-FC-ET-HC-R60 | 24 | 0.6 | 536.4492 | 0.31187 | 0.6497 | 0.46789 | 0.43203 | 0.88646 | 621.625 | 319.825 | 2346.175 | 2573.875 | 0 | 5470.8431 | 476.6706 | 1803.0783 | 13.7444 | 62.1903 | 18.3934 | 1.4366 | 2.7985 | 5361.189 | 0.54282 | 2910.0713
161 | C-SOK-NAP-FC-ET-HC-R60 | 24 | 1.2 | 575.2461 | 0.33442 | 0.64978 | 0.53328 | 0.52494 | 0.89896 | 618.35 | 350.85 | 2346.175 | 2474.875 | 0 | 4747.8047 | 479.5364 | 1802.7538 | 13.6957 | 61.897 | 18.3086 | 1.5059 | 2.7989 | 5367.7691 | 0.55898 | 3143.319
162 | C-SOK-NAP-FC-ET-HC-R60 | 24 | 1.8 | 599.2204 | 0.34836 | 0.6495 | 0.58791 | 0.57049 | 0.91131 | 616.75 | 377.125 | 2346.175 | 2412.75 | 0 | 4215.9774 | 480.0582 | 1803.0258 | 13.7143 | 60.4159 | 18.2954 | 1.5442 | 2.7985 | 5370.1738 | 0.57397 | 3216.0016
163 | C-SOK-NAP-FC-ET-HC-R60 | 28.5 | 0.713 | 458.3892 | 0.26649 | 0.65163 | 0.50034 | 0.51136 | 0.90161 | 611.025 | 332.05 | 2346.175 | 2767.8 | 0 | 4996.4829 | 466.3334 | 1802.9807 | 13.7235 | 64.2717 | 18.767 | 1.4871 | 2.7988 | 5369.5099 | 0.57032 | 2674.2381
164 | C-SOK-NAP-FC-ET-HC-R60 | 28.5 | 1.425 | 495.8268 | 0.28825 | 0.65167 | 0.5932 | 0.61205 | 0.92036 | 604.825 | 375.5 | 2346.175 | 2669.275 | 0 | 4042.7251 | 467.5942 | 1802.7297 | 13.7047 | 63.3032 | 18.7302 | 1.5719 | 2.7988 | 5374.2389 | 0.59498 | 2835.5983
165 | C-SOK-NAP-FC-ET-HC-R60 | 28.5 | 2.138 | 518.9908 | 0.30172 | 0.65171 | 0.66346 | 0.66576 | 0.93008 | 600.35 | 407.175 | 2346.175 | 2611.3 | 0 | 3389.0268 | 465.5433 | 1802.8753 | 13.8235 | 61.6059 | 18.8159 | 1.6266 | 2.7991 | 5380.3751 | 0.6131 | 2858.02
166 | C-SOK-NAP-FC-ET-WC-OFF0 | 18 | 0.45 | 685.6783 | 0.39862 | 0.59454 | 0.43978 | 0.60239 | 1 | 1606.05 | 694.375 | 2468.675 | 1985.25 | 30.1363 | 8953.0607 | 1064.8246 | 3519.1209 | 9.2925 | 71.5598 | 9.4747 | 0.9712 | 2.6618 | 1016.1548 | 0.59335 | 5018.9156
167 | C-SOK-NAP-FC-ET-WC-OFF0 | 18 | 0.9 | 702.8952 | 0.40863 | 0.59446 | 0.44648 | 0.71343 | 1 | 1606.95 | 710.5 | 2468.675 | 1939.925 | 30.1367 | 8737.9876 | 1065.1019 | 3519.1716 | 9.3001 | 70.6491 | 9.4711 | 0.99402 | 2.6614 | 1016.1548 | 0.59581 | 5113.8136
168 | C-SOK-NAP-FC-ET-WC-OFF0 | 18 | 1.35 | 710.9401 | 0.41331 | 0.59431 | 0.44968 | 0.7457 | 1 | 1607.825 | 718.2 | 2468.675 | 1917.8 | 30.1383 | 8658.1395 | 1065.497 | 3519.2384 | 9.3036 | 70.3997 | 9.4673 | 1.0007 | 2.6613 | 1016.1548 | 0.59557 | 5175.5078
169 | C-SOK-NAP-FC-ET-WC-OFF0 | 24.5 | 0.6 | 612.2789 | 0.35595 | 0.59023 | 0.56921 | 0.72424 | 1 | 1602.575 | 889.175 | 2468.675 | 2156.725 | 30.2157 | 6907.7022 | 1047.5439 | 3519.4189 | 9.4038 | 75.5838 | 9.6383 | 1.0457 | 2.6638 | 1016.1548 | 0.63283 | 5507.889
170 | C-SOK-NAP-FC-ET-WC-OFF0 | 24.5 | 1.25 | 629.1214 | 0.36574 | 0.58986 | 0.58561 | 0.82827 | 1 | 1602.425 | 916.775 | 2468.675 | 2107.325 | 30.2189 | 6553.6112 | 1047.4113 | 3519.4954 | 9.4046 | 77.2927 | 9.6394 | 1.0776 | 2.6637 | 1016.1548 | 0.63947 | 5556.9485
171 | C-SOK-NAP-FC-ET-WC-OFF0 | 24.5 | 1.85 | 638.7325 | 0.37133 | 0.58974 | 0.59462 | 0.86652 | 1 | 1602.25 | 932.525 | 2468.675 | 2081.75 | 30.2215 | 6377.4926 | 1048.6736 | 3519.3593 | 9.3959 | 78.0557 | 9.6281 | 1.0889 | 2.6639 | 1016.1548 | 0.64134 | 5612.7063
172 | C-SOK-NAP-FC-ET-WC-OFF0 | 31 | 0.8 | 512.8033 | 0.29812 | 0.58962 | 0.66164 | 0.82551 | 1 | 1575.45 | 1000.85 | 2468.675 | 2394.075 | 30.189 | 5391.3517 | 1029.0755 | 3518.8626 | 9.4564 | 79.1556 | 9.8167 | 1.1105 | 2.6659 | 1016.1548 | 0.69414 | 4862.1678
173 | C-SOK-NAP-FC-ET-WC-OFF0 | 31 | 1.55 | 534.0143 | 0.31045 | 0.58905 | 0.68913 | 0.9038 | 1 | 1574.9 | 1049.275 | 2468.675 | 2333.775 | 30.1954 | 4892.8504 | 1031.8154 | 3519.643 | 9.436 | 82.5229 | 9.7906 | 1.1452 | 2.6653 | 1016.1548 | 0.69758 | 5006.4299
174 | C-SOK-NAP-FC-ET-WC-OFF0 | 31 | 2.35 | 545.8388 | 0.31733 | 0.58897 | 0.7047 | 0.96907 | 1 | 1574.275 | 1077.475 | 2468.675 | 2305.7 | 30.1909 | 4586.4111 | 1031.9204 | 3518.9373 | 9.431 | 86.79 | 9.7887 | 1.1701 | 2.6656 | 1016.1548 | 0.7006 | 5066.0822
175 | C-SOK-NAP-FC-ET-WC-OFF | 38 | 0.95 | 438.1501 | 0.25472 | 0.58932 | 0.72454 | 0.88656 | 1 | 1550.4 | 1074.15 | 2468.675 | 2601.325 | 30.1364 | 4362.7258 | 1015.0273 | 3519.0792 | 9.5303 | 83.0968 | 9.9537 | 1.1585 | 2.6661 | 1016.1548 | 0.72513 | 4576.564
176 | C-SOK-NAP-FC-ET-WC-OFF | 38 | 1.9 | 462.8282 | 0.26907 | 0.58784 | 0.77281 | 0.9712 | 1 | 1554.35 | 1160.25 | 2468.675 | 2530.05 | 30.175 | 3542.9116 | 1018.4113 | 3519.2835 | 9.4931 | 90.2374 | 9.9245 | 1.2114 | 2.6671 | 1016.1548 | 0.73567 | 4648.8428
177 | C-SOK-NAP-FC-ET-WC-OFF | 38 | 2.85 | 476.9907 | 0.2773 | 0.58728 | 0.79521 | 0.99731 | 1 | 1556.05 | 1208.05 | 2468.675 | 2492.1 | 30.1786 | 3172.2635 | 1020.6503 | 3519.3878 | 9.4771 | 94.2206 | 9.9012 | 1.2382 | 2.6665 | 1016.1548 | 0.73494 | 4804.4031
178 | C-SOK-NAP-FC-ET-WC-OFF | 44.5 | 1.1 | 386.2151 | 0.22453 | 0.58955 | 0.76923 | 0.92427 | 1 | 1528.9 | 1124.75 | 2468.675 | 2756.35 | 30.0884 | 3635.1638 | 1003.9601 | 3519.1218 | 9.6078 | 86.0462 | 10.0666 | 1.1975 | 2.667 | 1016.1548 | 0.74477 | 4386.5578
179 | C-SOK-NAP-FC-ET-WC-OFF | 44.5 | 2.25 | 411.6642 | 0.23932 | 0.58732 | 0.82677 | 0.99419 | 1 | 1537.575 | 1235.15 | 2468.675 | 2681.575 | 30.1399 | 2687.4787 | 1008.4459 | 3518.9748 | 9.5588 | 95.4864 | 10.0234 | 1.2565 | 2.6676 | 1016.1548 | 0.7538 | 4510.2257
180 | C-SOK-NAP-FC-ET-WC-OFF | 44.5 | 3.35 | 423.9119 | 0.24644 | 0.58673 | 0.85788 | 0.99731 | 1 | 1537.25 | 1298 | 2468.675 | 2651.7 | 30.1347 | 2204.501 | 1009.6952 | 3519.5476 | 9.5437 | 96.7527 | 10.0086 | 1.2851 | 2.6664 | 1016.1548 | 0.75824 | 4560.6037
181 | C-SOK-NAP-FC-ET-WC-R100 | 18 | 0.45 | 668.6728 | 0.38873 | 0.56405 | 0.2654 | 0.19221 | 0.75863 | 1373.875 | 362.725 | 2227.75 | 2061.075 | 22.329 | 15814.0258 | 921.2589 | 2630.4083 | 9.2915 | 92.5788 | 18.4002 | 1.134 | 2.7407 | 11436.8433 | 0.62622 | -2591.4745
182 | C-SOK-NAP-FC-ET-WC-R100 | 18 | 0.9 | 697.1096 | 0.40527 | 0.56416 | 0.27406 | 0.2246 | 0.78162 | 1373.4 | 376.775 | 2227.75 | 1990.25 | 22.3298 | 15381.5578 | 922.6163 | 2630.3167 | 9.2988 | 91.2427 | 18.4052 | 1.1598 | 2.7409 | 11466.5314 | 0.63735 | -2505.5274
183 | C-SOK-NAP-FC-ET-WC-R100 | 18 | 1.35 | 707.7311 | 0.41144 | 0.56363 | 0.27796 | 0.23833 | 0.78293 | 1375.9 | 385.65 | 2227.75 | 1962.025 | 22.3418 | 15234.8113 | 922.519 | 2630.5617 | 9.3091 | 90.7908 | 18.4116 | 1.1707 | 2.7406 | 11471.1201 | 0.64053 | -2480.004
184 | C-SOK-NAP-FC-ET-WC-R100 | 24.5 | 0.6 | 588.1081 | 0.3419 | 0.56187 | 0.34156 | 0.27377 | 0.79565 | 1368.825 | 465.125 | 2227.75 | 2262.8 | 22.3605 | 14186.9753 | 908.7492 | 2630.5228 | 9.357 | 91.9038 | 18.6809 | 1.2043 | 2.7417 | 11477.2726 | 0.64239 | -1868.4217
185 | C-SOK-NAP-FC-ET-WC-R100 | 24.5 | 1.25 | 617.6208 | 0.35906 | 0.56177 | 0.3575 | 0.32218 | 0.81664 | 1367.675 | 492.775 | 2227.75 | 2180.75 | 22.3653 | 13552.5185 | 910.2235 | 2630.5893 | 9.3546 | 90.825 | 18.6735 | 1.2451 | 2.7417 | 11497.3948 | 0.65512 | -1756.9132
186 | C-SOK-NAP-FC-ET-WC-R100 | 24.5 | 1.85 | 628.5552 | 0.36541 | 0.56156 | 0.37181 | 0.342 | 0.81212 | 1366.55 | 516.175 | 2227.75 | 2149.6 | 22.3746 | 13251.5255 | 910.635 | 2630.4631 | 9.3496 | 90.1779 | 18.6649 | 1.2623 | 2.7421 | 11496.1043 | 0.66354 | -1809.5784
187 | C-SOK-NAP-FC-ET-WC-R100 | 31 | 0.8 | 500.1588 | 0.29077 | 0.56292 | 0.40519 | 0.35367 | 0.82449 | 1342.85 | 524.05 | 2227.75 | 2480.1 | 22.2959 | 12697.7106 | 892.8843 | 2630.2871 | 9.4048 | 91.066 | 19.0194 | 1.2756 | 2.7416 | 11506.3457 | 0.69334 | -2206.1596
188 | C-SOK-NAP-FC-ET-WC-R100 | 31 | 1.55 | 529.1083 | 0.3076 | 0.56266 | 0.4384 | 0.40509 | 0.83946 | 1340.65 | 577.075 | 2227.75 | 2397.775 | 22.3053 | 11858.6415 | 893.5015 | 2630.5305 | 9.411 | 89.7815 | 19.023 | 1.323 | 2.7418 | 11520.2972 | 0.70788 | -2135.4153
189 | C-SOK-NAP-FC-ET-WC-R100 | 31 | 2.35 | 545.8029 | 0.3173 | 0.56317 | 0.46764 | 0.43668 | 0.83989 | 1334.875 | 619.775 | 2227.75 | 2352 | 22.2949 | 11260.9931 | 891.8297 | 2630.5872 | 9.4287 | 88.9974 | 19.0493 | 1.3625 | 2.7419 | 11513.3644 | 0.72053 | -2184.4034
190 | C-SOK-NAP-FC-ET-WC-R10 | 38 | 0.95 | 433.6715 | 0.25212 | 0.56226 | 0.45482 | 0.41738 | 0.84401 | 1329.4 | 575.475 | 2227.75 | 2664.975 | 22.2943 | 11557.9066 | 882.0484 | 2630.316 | 9.4618 | 90.7958 | 19.2591 | 1.3341 | 2.7426 | 11524.8015 | 0.72375 | -2364.5511
191 | C-SOK-NAP-FC-ET-WC-R10 | 38 | 1.9 | 467.4011 | 0.27173 | 0.56209 | 0.50667 | 0.47793 | 0.86364 | 1324.825 | 656.8 | 2227.75 | 2567.275 | 22.3001 | 10405.1354 | 881.7873 | 2630.4953 | 9.4881 | 89.3174 | 19.2816 | 1.4037 | 2.7426 | 11540.6052 | 0.73757 | -2206.1246
192 | C-SOK-NAP-FC-ET-WC-R10 | 38 | 2.85 | 489.9605 | 0.28484 | 0.56254 | 0.54815 | 0.51867 | 0.86703 | 1318 | 719.125 | 2227.75 | 2506.35 | 22.2887 | 9580.2371 | 880.1999 | 2630.496 | 9.5208 | 88.1857 | 19.3087 | 1.4544 | 2.7421 | 11536.9618 | 0.74708 | -2138.6154
193 | C-SOK-NAP-FC-ET-WC-R10 | 44.5 | 1.1 | 390.2024 | 0.22685 | 0.56158 | 0.49034 | 0.46686 | 0.86295 | 1321.85 | 617.075 | 2227.75 | 2792.775 | 22.2937 | 10691.4856 | 876.3126 | 2630.5738 | 9.5081 | 90.4613 | 19.3918 | 1.3827 | 2.7419 | 11540.267 | 0.73841 | -2327.239
194 | C-SOK-NAP-FC-ET-WC-R10 | 44.5 | 2.25 | 426.2304 | 0.24779 | 0.56185 | 0.56004 | 0.54293 | 0.87536 | 1313.175 | 723.975 | 2227.75 | 2685 | 22.2933 | 9230.8122 | 874.8484 | 2630.4062 | 9.5577 | 88.7403 | 19.4405 | 1.4751 | 2.7426 | 11556.5108 | 0.75367 | -2176.2694
195 | C-SOK-NAP-FC-ET-WC-R10 | 44.5 | 3.35 | 449.8419 | 0.26152 | 0.56127 | 0.61121 | 0.59226 | 0.88291 | 1311.575 | 803.825 | 2227.75 | 2621.95 | 22.3157 | 8218.4891 | 874.9147 | 2630.7027 | 9.5629 | 87.8248 | 19.4375 | 1.5527 | 2.7424 | 11554.7212 | 0.76523 | -2115.8752
196 | C-SOK-NAP-FC-ET-WC-R600 | 18 | 0.45 | 669.2896 | 0.38909 | 0.5637 | 0.25229 | 0.2006 | 0.81482 | 1495 | 376.625 | 2346.175 | 2053.3 | 24.2128 | 13499.0825 | 956.6992 | 2805.0808 | 9.2502 | 87.4051 | 15.0584 | 1.0759 | 2.7533 | 8096.9807 | 0.62598 | -4875.2973
197 | C-SOK-NAP-FC-ET-WC-R600 | 18 | 0.9 | 696.5207 | 0.40492 | 0.56386 | 0.26074 | 0.24749 | 0.83652 | 1494.475 | 393.625 | 2346.175 | 1981.875 | 24.2163 | 13124.7235 | 957.8971 | 2805.1919 | 9.2589 | 86.1383 | 15.0856 | 1.1044 | 2.7536 | 8141.8924 | 0.6348 | -4805.4903
198 | C-SOK-NAP-FC-ET-WC-R600 | 18 | 1.35 | 709.5819 | 0.41252 | 0.56338 | 0.26673 | 0.2768 | 0.83768 | 1496.275 | 405.525 | 2346.175 | 1946.275 | 24.2306 | 12939.3588 | 958.7487 | 2804.942 | 9.2583 | 85.1309 | 15.0763 | 1.1146 | 2.7536 | 8145.75 | 0.63871 | -4772.8601
199 | C-SOK-NAP-FC-ET-WC-R600 | 24.5 | 0.6 | 583.6755 | 0.33932 | 0.56169 | 0.31625 | 0.29797 | 0.84974 | 1490.875 | 478.85 | 2346.175 | 2268.35 | 24.2454 | 12192.5043 | 946.6844 | 2805.1219 | 9.2842 | 87.3139 | 15.2664 | 1.1406 | 2.7531 | 8157.2694 | 0.62613 | -4012.8991
200 | C-SOK-NAP-FC-ET-WC-R600 | 24.5 | 1.25 | 611.8748 | 0.35572 | 0.56132 | 0.34337 | 0.36316 | 0.8713 | 1489.25 | 516.8 | 2346.175 | 2182.7 | 24.2506 | 11512.977 | 946.3997 | 2805.1098 | 9.2937 | 85.8498 | 15.309 | 1.1815 | 2.7542 | 8193.1397 | 0.6459 | -4032.5782
201 | C-SOK-NAP-FC-ET-WC-R600 | 24.5 | 1.85 | 625.726 | 0.36377 | 0.56145 | 0.35695 | 0.40594 | 0.87424 | 1487.075 | 542.175 | 2346.175 | 2142.6 | 24.2604 | 11161.647 | 946.6829 | 2805.2414 | 9.2901 | 85.3344 | 15.3044 | 1.2083 | 2.7547 | 8191.0669 | 0.65439 | -4025.2838
202 | C-SOK-NAP-FC-ET-WC-R600 | 31 | 0.8 | 489.3015 | 0.28446 | 0.56287 | 0.3898 | 0.38463 | 0.87602 | 1460.7 | 551.1 | 2346.175 | 2500.825 | 24.1835 | 10786.2059 | 929.1695 | 2804.8723 | 9.3248 | 86.1386 | 15.5788 | 1.205 | 2.7544 | 8197.663 | 0.6842 | -4539.5141
203 | C-SOK-NAP-FC-ET-WC-R600 | 31 | 1.55 | 517.287 | 0.30073 | 0.56285 | 0.42261 | 0.46287 | 0.89022 | 1456.425 | 605.475 | 2346.175 | 2418.125 | 24.1799 | 10005.0371 | 928.57 | 2804.8469 | 9.3382 | 85.3967 | 15.6117 | 1.2565 | 2.7545 | 8221.0327 | 0.69738 | -4463.1489
204 | C-SOK-NAP-FC-ET-WC-R600 | 31 | 2.35 | 537.1762 | 0.31229 | 0.56217 | 0.45092 | 0.51311 | 0.89798 | 1457.7 | 655.9 | 2346.175 | 2361.425 | 24.2031 | 9423.517 | 928.1716 | 2805.2016 | 9.3427 | 84.9589 | 15.6223 | 1.298 | 2.7545 | 8224.297 | 0.70773 | -4421.2659
205 | C-SOK-NAP-FC-ET-WC-R60 | 38 | 0.95 | 420.945 | 0.24472 | 0.56232 | 0.43954 | 0.45802 | 0.89486 | 1446.25 | 606.55 | 2346.175 | 2693.9 | 24.1774 | 9792.736 | 917.9528 | 2804.9846 | 9.3725 | 86.1793 | 15.7859 | 1.2573 | 2.7552 | 8224.2813 | 0.71363 | -4721.3006
206 | C-SOK-NAP-FC-ET-WC-R60 | 38 | 1.9 | 454.4005 | 0.26417 | 0.56209 | 0.49379 | 0.553 | 0.90954 | 1439.725 | 696.525 | 2346.175 | 2592.9 | 24.1779 | 8666.9266 | 916.4087 | 2804.7754 | 9.4 | 85.3929 | 15.8236 | 1.3283 | 2.7549 | 8238.116 | 0.72727 | -4556.2619
207 | C-SOK-NAP-FC-ET-WC-R60 | 38 | 2.85 | 476.12 | 0.27679 | 0.56191 | 0.5339 | 0.59776 | 0.92126 | 1437.175 | 765.175 | 2346.175 | 2532.125 | 24.1892 | 7927.7203 | 917.0957 | 2804.9496 | 9.3986 | 84.6247 | 15.8231 | 1.375 | 2.7549 | 8248.1102 | 0.73578 | -4453.5312
208 | C-SOK-NAP-FC-ET-WC-R60 | 44.5 | 1.1 | 376.8223 | 0.21907 | 0.5622 | 0.47581 | 0.52447 | 0.90709 | 1434.55 | 650.375 | 2346.175 | 2829.025 | 24.1663 | 9018.7899 | 911.6637 | 2805.0096 | 9.4126 | 86.3411 | 15.9063 | 1.2999 | 2.7548 | 8243.4611 | 0.72812 | -4728.6417
209 | C-SOK-NAP-FC-ET-WC-R60 | 44.5 | 2.25 | 411.2999 | 0.23911 | 0.56177 | 0.54351 | 0.62961 | 0.92617 | 1429.55 | 765.675 | 2346.175 | 2720.775 | 24.1834 | 7663.7401 | 910.6076 | 2804.9255 | 9.4352 | 85.9459 | 15.9385 | 1.3927 | 2.7554 | 8256.8648 | 0.74253 | -4517.6184
210 | C-SOK-NAP-FC-ET-WC-R60 | 44.5 | 3.35 | 433.2232 | 0.25186 | 0.56144 | 0.59537 | 0.67669 | 0.93589 | 1425.775 | 850.075 | 2346.175 | 2657.15 | 24.1959 | 6771.8552 | 911.1515 | 2804.7958 | 9.434 | 85.1042 | 15.9458 | 1.4536 | 2.7553 | 8273.2247 | 0.7524 | -4446.8419
211 | C-SOK-NAP-FC-FP-HC-OFF0 | 11.5 | 0.288 | 605.2577 | 0.35187 | 0.63149 | 0.27761 | 0.40206 | 1 | 884.575 | 258.8 | 2468.675 | 2401.3 | 0 | 6957.682 | 690.5736 | 2226.6534 | 9.7639 | 55.1302 | 9.251 | 1.0075 | 2.7158 | 641.83 | 0.40002 | 4176.105
212 | C-SOK-NAP-FC-FP-HC-OFF0 | 11.5 | 0.575 | 617.0892 | 0.35875 | 0.63136 | 0.27871 | 0.53613 | 1 | 885.55 | 259.225 | 2468.675 | 2421.875 | 0 | 6862.8404 | 687.402 | 2227.1898 | 9.81 | 53.6965 | 9.2935 | 1.036 | 2.7151 | 641.83 | 0.40595 | 4215.6742
213 | C-SOK-NAP-FC-FP-HC-OFF0 | 11.5 | 0.863 | 622.0928 | 0.36166 | 0.63133 | 0.27873 | 0.59829 | 1 | 886.075 | 259.275 | 2468.675 | 2428.375 | 0 | 6823.1945 | 686.5421 | 2227.3284 | 9.8229 | 53.0403 | 9.3053 | 1.0482 | 2.7149 | 641.83 | 0.40831 | 4232.984
214 | C-SOK-NAP-FC-FP-HC-OFF0 | 15.5 | 0.388 | 539.8477 | 0.31384 | 0.63204 | 0.40091 | 0.55334 | 1 | 865.85 | 350.2 | 2468.675 | 2548.575 | 0 | 5732.9158 | 650.3051 | 2226.8515 | 10.2471 | 55.8499 | 9.8224 | 1.0761 | 2.7151 | 641.83 | 0.478 | 4367.917
215 | C-SOK-NAP-FC-FP-HC-OFF0 | 15.5 | 0.775 | 557.2403 | 0.32395 | 0.63224 | 0.41632 | 0.6726 | 1 | 863.325 | 361.175 | 2468.675 | 2547.35 | 0 | 5515.3643 | 648.2846 | 2227.2602 | 10.2748 | 56.2983 | 9.8544 | 1.1023 | 2.715 | 641.83 | 0.48809 | 4421.4871
216 | C-SOK-NAP-FC-FP-HC-OFF0 | 15.5 | 1.163 | 568.0194 | 0.33022 | 0.63222 | 0.42837 | 0.72315 | 1 | 863.025 | 371.125 | 2468.675 | 2539.375 | 0 | 5373.7218 | 646.5068 | 2227.2301 | 10.3005 | 56.599 | 9.8816 | 1.1172 | 2.7151 | 641.83 | 0.49497 | 4446.3985
217 | C-SOK-NAP-FC-FP-HC-OFF0 | 20 | 0.5 | 477.2233 | 0.27744 | 0.63289 | 0.49879 | 0.66794 | 1 | 845.925 | 420.075 | 2468.675 | 2707.95 | 0 | 4763.5854 | 609.6283 | 2226.8115 | 10.8925 | 58.198 | 10.4783 | 1.1289 | 2.7153 | 641.83 | 0.51939 | 4587.1938
218 | C-SOK-NAP-FC-FP-HC-OFF0 | 20 | 1 | 500.7708 | 0.29112 | 0.63295 | 0.53438 | 0.78471 | 1 | 842.475 | 447.65 | 2468.675 | 2680.275 | 0 | 4364.9736 | 605.8612 | 2226.6354 | 10.9541 | 60.3261 | 10.5431 | 1.1673 | 2.7154 | 641.83 | 0.53465 | 4660.7056
219 | C-SOK-NAP-FC-FP-HC-OFF0 | 20 | 1.5 | 512.247 | 0.2978 | 0.6329 | 0.55456 | 0.81116 | 1 | 841.3 | 463.05 | 2468.675 | 2666.675 | 0 | 4165.2573 | 603.3944 | 2227.0158 | 10.9985 | 60.7989 | 10.5865 | 1.1749 | 2.715 | 641.83 | 0.54226 | 4689.5105
220 | C-SOK-NAP-FC-FP-HC-OFF | 24 | 0.6 | 431.4891 | 0.25085 | 0.63325 | 0.53205 | 0.73993 | 1 | 843.7 | 455.125 | 2468.675 | 2834.225 | 0 | 4413.1697 | 604.5067 | 2226.7171 | 10.9922 | 62.1645 | 10.5673 | 1.1589 | 2.7155 | 641.83 | 0.51206 | 5052.9936
221 | C-SOK-NAP-FC-FP-HC-OFF | 24 | 1.2 | 455.4982 | 0.26481 | 0.63359 | 0.58828 | 0.85597 | 1 | 835.475 | 494.625 | 2468.675 | 2797.475 | 0 | 3826.139 | 597.2306 | 2226.7067 | 11.1011 | 65.3635 | 10.6953 | 1.2045 | 2.7153 | 641.83 | 0.53826 | 5047.7298
222 | C-SOK-NAP-FC-FP-HC-OFF | 24 | 1.8 | 467.8075 | 0.27196 | 0.63353 | 0.62604 | 0.90086 | 1 | 832.275 | 520.5 | 2468.675 | 2770.1 | 0 | 3455.7749 | 594.261 | 2226.444 | 11.1279 | 66.8507 | 10.7503 | 1.2251 | 2.7161 | 641.83 | 0.55729 | 4970.447
223 | C-SOK-NAP-FC-FP-HC-OFF | 28.5 | 0.713 | 369.8888 | 0.21504 | 0.63438 | 0.60192 | 0.80329 | 1 | 828.825 | 500.125 | 2468.675 | 2982.5 | 0 | 3732.1677 | 582.4923 | 2226.2546 | 11.2494 | 63.7311 | 10.9671 | 1.1971 | 2.7162 | 641.83 | 0.56613 | 4573.8074
224 | C-SOK-NAP-FC-FP-HC-OFF | 28.5 | 1.425 | 394.2976 | 0.22923 | 0.63465 | 0.66545 | 0.91964 | 1 | 819.95 | 545.625 | 2468.675 | 2937.45 | 0 | 3080.4498 | 573.9828 | 2226.3916 | 11.4013 | 69.4375 | 11.1286 | 1.2495 | 2.7158 | 641.83 | 0.58865 | 4622.5816
225 | C-SOK-NAP-FC-FP-HC-OFF | 28.5 | 2.138 | 410.8251 | 0.23883 | 0.63486 | 0.70187 | 0.98728 | 1 | 816.075 | 571.725 | 2468.675 | 2911.875 | 0 | 2706.2268 | 573.8036 | 2226.4377 | 11.3911 | 76.0287 | 11.1315 | 1.2813 | 2.7155 | 641.83 | 0.59663 | 4722.879
226 | C-SOK-NAP-FC-FP-HC-R100 | 11.5 | 0.288 | 655.9443 | 0.38134 | 0.64135 | 0.17459 | 0.13477 | 0.72058 | 627.35 | 145.125 | 2227.75 | 2139.6 | 0 | 10337.7229 | 567.8048 | 1703.2398 | 11.6478 | 66.7676 | 18.3481 | 1.2303 | 2.7864 | 7371.6223 | 0.48504 | 1505.3422
227 | C-SOK-NAP-FC-FP-HC-R100 | 11.5 | 0.575 | 683.5726 | 0.3974 | 0.6407 | 0.17531 | 0.1739 | 0.75391 | 629.825 | 143.725 | 2227.75 | 2129.35 | 0 | 10066.8595 | 562.9204 | 1703.2546 | 11.7925 | 65.8326 | 18.5025 | 1.2611 | 2.7864 | 7379.0649 | 0.5017 | 1617.1757
228 | C-SOK-NAP-FC-FP-HC-R100 | 11.5 | 0.863 | 696.4036 | 0.40486 | 0.64038 | 0.18149 | 0.1925 | 0.75959 | 630.95 | 145 | 2227.75 | 2132.825 | 0 | 9924.914 | 562.3648 | 1703.2148 | 11.7835 | 65.418 | 18.5206 | 1.2767 | 2.7864 | 7380.2527 | 0.51072 | 1632.0616
229 | C-SOK-NAP-FC-FP-HC-R100 | 15.5 | 0.388 | 574.7643 | 0.33414 | 0.64332 | 0.27182 | 0.20852 | 0.76491 | 610.45 | 198.625 | 2227.75 | 2312.95 | 0 | 9213.9596 | 537.3348 | 1703.258 | 12.254 | 64.7041 | 19.2957 | 1.2994 | 2.7864 | 7383.8366 | 0.53594 | 1858.4125
230 | C-SOK-NAP-FC-FP-HC-R100 | 15.5 | 0.775 | 604.042 | 0.35116 | 0.64275 | 0.2889 | 0.25456 | 0.79488 | 611.375 | 203.75 | 2227.75 | 2308.525 | 0 | 8806.8239 | 535.3986 | 1703.115 | 12.2689 | 64.0872 | 19.3645 | 1.3405 | 2.7861 | 7388.7466 | 0.55444 | 1969.1872
231 | C-SOK-NAP-FC-FP-HC-R100 | 15.5 | 1.163 | 618.7515 | 0.35971 | 0.6423 | 0.30612 | 0.27999 | 0.79672 | 612.675 | 210.85 | 2227.75 | 2302.1 | 0 | 8569.7797 | 534.5644 | 1703.1465 | 12.2667 | 63.6261 | 19.3931 | 1.3623 | 2.7861 | 7389.6641 | 0.56657 | 1958.4524
232 | C-SOK-NAP-FC-FP-HC-R100 | 20 | 0.5 | 503.0327 | 0.29244 | 0.64438 | 0.34346 | 0.2819 | 0.7975 | 598.225 | 235.375 | 2227.75 | 2484.925 | 0 | 8298.86 | 510.1806 | 1702.8198 | 12.9428 | 64.0383 | 20.219 | 1.3663 | 2.7872 | 7391.4004 | 0.56521 | 2176.4034
233 | C-SOK-NAP-FC-FP-HC-R100 | 20 | 1 | 535.2319 | 0.31116 | 0.64419 | 0.38317 | 0.33775 | 0.82399 | 597 | 251.675 | 2227.75 | 2470.95 | 0 | 7702.331 | 507.7542 | 1702.7015 | 12.9702 | 63.3293 | 20.3128 | 1.4206 | 2.7873 | 7396.2758 | 0.58755 | 2281.9382
234 | C-SOK-NAP-FC-FP-HC-R100 | 20 | 1.5 | 552.9265 | 0.32145 | 0.64392 | 0.41602 | 0.37231 | 0.82286 | 596.675 | 265.05 | 2227.75 | 2458.375 | 0 | 7324.3816 | 507.0628 | 1702.8581 | 12.9517 | 62.8064 | 20.3363 | 1.4548 | 2.7871 | 7395.6677 | 0.60313 | 2253.2384
235 | C-SOK-NAP-FC-FP-HC-R10 | 24 | 0.6 | 454.263 | 0.26409 | 0.645 | 0.37208 | 0.33523 | 0.81861 | 595.525 | 254.4 | 2227.75 | 2618.55 | 0 | 7795.8301 | 505.2673 | 1702.7324 | 12.9708 | 64.6655 | 20.401 | 1.413 | 2.7869 | 7396.6661 | 0.56751 | 2567.6894
236 | C-SOK-NAP-FC-FP-HC-R10 | 24 | 1.2 | 487.9268 | 0.28366 | 0.64512 | 0.4402 | 0.40229 | 0.84215 | 591.3 | 280.525 | 2227.75 | 2584.6 | 0 | 6964.114 | 503.7548 | 1702.9222 | 12.9561 | 63.4083 | 20.4621 | 1.4825 | 2.7864 | 7400.8771 | 0.5996 | 2599.1324
237 | C-SOK-NAP-FC-FP-HC-R10 | 24 | 1.8 | 504.6047 | 0.29335 | 0.64481 | 0.48199 | 0.44045 | 0.84642 | 589.925 | 297.675 | 2227.75 | 2585.925 | 0 | 6496.809 | 501.2842 | 1702.8081 | 12.9809 | 62.7732 | 20.5499 | 1.5215 | 2.7871 | 7399.2573 | 0.61861 | 2541.6772
238 | C-SOK-NAP-FC-FP-HC-R10 | 28.5 | 0.713 | 394.9155 | 0.22959 | 0.64644 | 0.41548 | 0.38961 | 0.83702 | 586.775 | 271.525 | 2227.75 | 2768.4 | 0 | 7194.0977 | 494.6883 | 1702.8565 | 13.0861 | 64.5052 | 20.7958 | 1.4659 | 2.7871 | 7401.3335 | 0.60239 | 2371.7484
239 | C-SOK-NAP-FC-FP-HC-R10 | 28.5 | 1.425 | 430.8435 | 0.25047 | 0.6467 | 0.499 | 0.46487 | 0.85822 | 580.775 | 306.45 | 2227.75 | 2723.85 | 0 | 6227.5699 | 491.983 | 1702.4857 | 13.1553 | 63.2179 | 20.9019 | 1.5498 | 2.7873 | 7404.9867 | 0.63086 | 2481.6993
240 | C-SOK-NAP-FC-FP-HC-R10 | 28.5 | 2.138 | 452.5485 | 0.26309 | 0.64639 | 0.5554 | 0.51544 | 0.86294 | 578.8 | 330 | 2227.75 | 2714.25 | 0 | 5603.4126 | 489.8364 | 1702.8153 | 13.1919 | 62.4345 | 20.9821 | 1.601 | 2.7865 | 7404.8744 | 0.64921 | 2485.7688
241 | C-SOK-NAP-FC-FP-HC-R600 | 11.5 | 0.288 | 656.2159 | 0.38149 | 0.6444 | 0.16472 | 0.11364 | 0.76932 | 671.6 | 148.2 | 2346.175 | 2134.05 | 0 | 8765.8243 | 569.7552 | 1803.5558 | 11.7245 | 64.3704 | 15.6013 | 1.1951 | 2.7976 | 5299.5881 | 0.48903 | 600.5997
242 | C-SOK-NAP-FC-FP-HC-R600 | 11.5 | 0.575 | 682.4421 | 0.39674 | 0.64373 | 0.16663 | 0.16621 | 0.8066 | 674 | 146.65 | 2346.175 | 2118.275 | 0 | 8527.6093 | 564.5512 | 1803.4178 | 11.8825 | 63.0467 | 15.7588 | 1.2226 | 2.7978 | 5317.7481 | 0.50382 | 727.5478
243 | C-SOK-NAP-FC-FP-HC-R600 | 11.5 | 0.863 | 695.194 | 0.40415 | 0.64345 | 0.17168 | 0.20082 | 0.8101 | 675.225 | 147.025 | 2346.175 | 2125.5 | 0 | 8401.7707 | 562.4346 | 1803.4089 | 11.9192 | 62.5866 | 15.8182 | 1.2448 | 2.7977 | 5321.8471 | 0.5112 | 747.1688
244 | C-SOK-NAP-FC-FP-HC-R600 | 15.5 | 0.388 | 570.7971 | 0.33183 | 0.64616 | 0.25907 | 0.19978 | 0.81664 | 654.35 | 202.85 | 2346.175 | 2313.475 | 0 | 7737.3888 | 538.6452 | 1803.2733 | 12.2922 | 61.2515 | 16.4483 | 1.2556 | 2.798 | 5326.0692 | 0.53414 | 975.6614
245 | C-SOK-NAP-FC-FP-HC-R600 | 15.5 | 0.775 | 598.193 | 0.34776 | 0.64583 | 0.2762 | 0.26207 | 0.84585 | 654.725 | 208.7 | 2346.175 | 2304.275 | 0 | 7385.2533 | 536.123 | 1803.2007 | 12.3371 | 60.6829 | 16.5392 | 1.2981 | 2.7982 | 5339.2759 | 0.54947 | 1103.4157
246 | C-SOK-NAP-FC-FP-HC-R600 | 15.5 | 1.163 | 614.1011 | 0.35701 | 0.6456 | 0.29457 | 0.30694 | 0.84912 | 655.475 | 216.55 | 2346.175 | 2300.5 | 0 | 7139.8604 | 536.4525 | 1803.5538 | 12.2859 | 60.1787 | 16.5318 | 1.3233 | 2.798 | 5339.6243 | 0.56142 | 1110.0346
247 | C-SOK-NAP-FC-FP-HC-R600 | 20 | 0.5 | 494.6941 | 0.28759 | 0.64745 | 0.3284 | 0.28106 | 0.84793 | 640.875 | 241.225 | 2346.175 | 2491.8 | 0 | 6949.6338 | 511.4034 | 1803.0547 | 12.9235 | 60.3413 | 17.2531 | 1.3164 | 2.7985 | 5342.1762 | 0.55747 | 1307.5514
248 | C-SOK-NAP-FC-FP-HC-R600 | 20 | 1 | 525.7964 | 0.30567 | 0.64716 | 0.3688 | 0.36146 | 0.87023 | 639.925 | 259 | 2346.175 | 2480.275 | 0 | 6407.3309 | 509.1817 | 1803.0483 | 12.9322 | 59.913 | 17.3384 | 1.3753 | 2.7984 | 5352.943 | 0.57738 | 1428.4183
249 | C-SOK-NAP-FC-FP-HC-R600 | 20 | 1.5 | 542.6301 | 0.31546 | 0.64685 | 0.39989 | 0.42247 | 0.87211 | 640.175 | 273.925 | 2346.175 | 2477.45 | 0 | 6037.0535 | 507.9836 | 1803.1508 | 12.8968 | 59.7468 | 17.3744 | 1.4154 | 2.7986 | 5352.3195 | 0.59392 | 1397.3684
250 | C-SOK-NAP-FC-FP-HC-R60 | 24 | 0.6 | 441.7422 | 0.25681 | 0.64812 | 0.35847 | 0.33666 | 0.86649 | 637.575 | 261.525 | 2346.175 | 2629.375 | 0 | 6544.6272 | 506.4443 | 1803.0372 | 12.9535 | 60.8859 | 17.4198 | 1.3576 | 2.7986 | 5351.7296 | 0.55868 | 1653.0404
251 | C-SOK-NAP-FC-FP-HC-R60 | 24 | 1.2 | 474.243 | 0.2757 | 0.64802 | 0.42087 | 0.4367 | 0.88357 | 634.275 | 289.975 | 2346.175 | 2616.875 | 0 | 5812.3552 | 503.621 | 1802.7833 | 12.9534 | 60.3645 | 17.5213 | 1.4282 | 2.7988 | 5360.7789 | 0.58556 | 1732.8845
252 | C-SOK-NAP-FC-FP-HC-R60 | 24 | 1.8 | 491.8169 | 0.28592 | 0.64782 | 0.46345 | 0.50005 | 0.89256 | 632.775 | 308.75 | 2346.175 | 2605.25 | 0 | 5332.7292 | 502.9259 | 1803.1083 | 12.892 | 60.1242 | 17.5435 | 1.4768 | 2.7983 | 5361.1199 | 0.6055 | 1698.7144
253 | C-SOK-NAP-FC-FP-HC-R60 | 28.5 | 0.713 | 381.4416 | 0.22175 | 0.64954 | 0.39952 | 0.39879 | 0.8816 | 628.7 | 280.325 | 2346.175 | 2791.9 | 0 | 6051.5493 | 496.9185 | 1803.0529 | 13.0093 | 60.908 | 17.7298 | 1.4046 | 2.799 | 5359.5355 | 0.58957 | 1472.9925
254 | C-SOK-NAP-FC-FP-HC-R60 | 28.5 | 1.425 | 414.2226 | 0.24081 | 0.64946 | 0.47902 | 0.50379 | 0.89848 | 623.3 | 316.475 | 2346.175 | 2772.375 | 0 | 5186.443 | 491.6778 | 1802.9886 | 13.1114 | 60.1619 | 17.9073 | 1.4788 | 2.7985 | 5366.504 | 0.61673 | 1579.1289
255 | C-SOK-NAP-FC-FP-HC-R60 | 28.5 | 2.138 | 437.2905 | 0.25422 | 0.64907 | 0.53317 | 0.5683 | 0.91036 | 622.325 | 342.25 | 2346.175 | 2746.45 | 0 | 4614.7657 | 492.5424 | 1803.0464 | 13.0419 | 59.8126 | 17.8838 | 1.5298 | 2.7984 | 5368.9409 | 0.63061 | 1691.1885
256 | C-SOK-NAP-FC-FP-WC-OFF0 | 18 | 0.45 | 552.7871 | 0.32136 | 0.59687 | 0.33581 | 0.52046 | 1 | 1607.675 | 533.55 | 2468.675 | 2564.175 | 30.0703 | 10581.7308 | 1049.3637 | 3519.3822 | 9.3781 | 73.0076 | 9.613 | 0.91482 | 2.6612 | 1016.1548 | 0.56609 | 4317.5086
257 | C-SOK-NAP-FC-FP-WC-OFF0 | 18 | 0.9 | 564.0829 | 0.32793 | 0.59689 | 0.33723 | 0.64359 | 1 | 1607.975 | 540.4 | 2468.675 | 2556.875 | 30.0679 | 10433.0669 | 1047.0196 | 3519.3484 | 9.4044 | 71.0287 | 9.633 | 0.93724 | 2.6608 | 1016.1548 | 0.56908 | 4375.3543
258 | C-SOK-NAP-FC-FP-WC-OFF0 | 18 | 1.35 | 569.943 | 0.33134 | 0.59682 | 0.33959 | 0.68154 | 1 | 1608.85 | 544.675 | 2468.675 | 2549.85 | 30.0711 | 10360.4748 | 1047.6005 | 3518.8238 | 9.4024 | 70.4194 | 9.6283 | 0.94293 | 2.6614 | 1016.1548 | 0.57059 | 4405.2626
259 | C-SOK-NAP-FC-FP-WC-OFF0 | 24.5 | 0.6 | 491.5228 | 0.28575 | 0.59376 | 0.43407 | 0.64632 | 1 | 1606.35 | 680.05 | 2468.675 | 2712.375 | 30.1169 | 9009.8113 | 1037.1456 | 3519.3859 | 9.4506 | 76.3217 | 9.7304 | 0.97311 | 2.6625 | 1016.1548 | 0.6055 | 4750.7278
260 | C-SOK-NAP-FC-FP-WC-OFF0 | 24.5 | 1.25 | 504.7031 | 0.29341 | 0.59366 | 0.44326 | 0.75851 | 1 | 1604.5 | 697.35 | 2468.675 | 2686.5 | 30.1086 | 8754.78 | 1035.9897 | 3519.2559 | 9.4635 | 76.2571 | 9.7394 | 0.99582 | 2.662 | 1016.1548 | 0.61023 | 4819.5566
261 | C-SOK-NAP-FC-FP-WC-OFF0 | 24.5 | 1.85 | 512.0534 | 0.29768 | 0.59337 | 0.44961 | 0.78353 | 1 | 1606.3 | 708.5 | 2468.675 | 2675.025 | 30.1183 | 8637.6057 | 1036.7323 | 3519.0317 | 9.4607 | 76.3737 | 9.7335 | 1.0016 | 2.6625 | 1016.1548 | 0.61158 | 4872.8718
262 | C-SOK-NAP-FC-FP-WC-OFF0 | 31 | 0.8 | 408.533 | 0.2375 | 0.59409 | 0.50704 | 0.73622 | 1 | 1583.775 | 767.2 | 2468.675 | 2909.4 | 30.0874 | 7803.4834 | 1024.3934 | 3519.5506 | 9.464 | 77.9537 | 9.8571 | 1.0179 | 2.664 | 1016.1548 | 0.67108 | 4165.6736
263 | C-SOK-NAP-FC-FP-WC-OFF0 | 31 | 1.55 | 426.4751 | 0.24793 | 0.59332 | 0.52756 | 0.83281 | 1 | 1585.825 | 804.55 | 2468.675 | 2880.225 | 30.1155 | 7403.3052 | 1025.1879 | 3519.315 | 9.4633 | 79.6333 | 9.8522 | 1.0472 | 2.665 | 1016.1548 | 0.67497 | 4297.0812
264 | C-SOK-NAP-FC-FP-WC-OFF0 | 31 | 2.35 | 434.8491 | 0.2528 | 0.59346 | 0.53811 | 0.85676 | 1 | 1584.6 | 824.75 | 2468.675 | 2867.175 | 30.1058 | 7215.1581 | 1026.0387 | 3519.4103 | 9.4578 | 80.2406 | 9.8432 | 1.0527 | 2.6647 | 1016.1548 | 0.67555 | 4373.6711
265 | C-SOK-NAP-FC-FP-WC-OFF | 38 | 0.95 | 352.9873 | 0.20521 | 0.59265 | 0.56329 | 0.79843 | 1 | 1574.55 | 837.925 | 2468.675 | 3071.775 | 30.0946 | 6899.1803 | 1015.2097 | 3519.26 | 9.5044 | 80.2354 | 9.9496 | 1.0538 | 2.6653 | 1016.1548 | 0.70421 | 3967.5173
266 | C-SOK-NAP-FC-FP-WC-OFF | 38 | 1.9 | 376.0608 | 0.21862 | 0.59171 | 0.60105 | 0.90711 | 1 | 1576.35 | 907.1 | 2468.675 | 3023.2 | 30.0991 | 6218.3429 | 1017.092 | 3519.4389 | 9.4876 | 83.792 | 9.9292 | 1.0985 | 2.6645 | 1016.1548 | 0.71012 | 4142.425
267 | C-SOK-NAP-FC-FP-WC-OFF | 38 | 2.85 | 389.7886 | 0.2266 | 0.59067 | 0.62725 | 0.95478 | 1 | 1581.075 | 958.675 | 2468.675 | 3006.2 | 30.1249 | 5778.808 | 1017.0412 | 3519.6186 | 9.4832 | 86.5927 | 9.9315 | 1.1202 | 2.6649 | 1016.1548 | 0.71681 | 4194.5911
268 | C-SOK-NAP-FC-FP-WC-OFF | 44.5 | 1.1 | 317.9641 | 0.18485 | 0.59225 | 0.60593 | 0.83432 | 1 | 1562.05 | 889.7 | 2468.675 | 3176.8 | 30.0657 | 6215.1662 | 1009.0597 | 3519.5683 | 9.5589 | 81.3943 | 10.0132 | 1.0811 | 2.6659 | 1016.1548 | 0.71702 | 4003.9927
269 | C-SOK-NAP-FC-FP-WC-OFF | 44.5 | 2.25 | 343.8439 | 0.19989 | 0.59039 | 0.66155 | 0.9466 | 1 | 1569.25 | 992.85 | 2468.675 | 3126.425 | 30.1 | 5263.6369 | 1011.3836 | 3519.5457 | 9.5297 | 86.9953 | 9.9896 | 1.1353 | 2.6657 | 1016.1548 | 0.72833 | 4156.7968
270 | C-SOK-NAP-FC-FP-WC-OFF | 44.5 | 3.35 | 360.0245 | 0.2093 | 0.58935 | 0.7 | 0.99731 | 1 | 1572.675 | 1071.075 | 2468.675 | 3094.875 | 30.1264 | 4628.9191 | 1012.2234 | 3519.2832 | 9.5135 | 91.6961 | 9.9825 | 1.1775 | 2.6663 | 1016.1548 | 0.73703 | 4213.0566
271 | C-SOK-NAP-FC-FP-WC-R100 | 18 | 0.45 | 599.3454 | 0.34843 | 0.5648 | 0.21346 | 0.17539 | 0.7444 | 1377.375 | 295.175 | 2227.75 | 2256.275 | 22.3195 | 16598.9522 | 920.9042 | 2630.2273 | 9.301 | 93.3526 | 18.3893 | 1.1096 | 2.7411 | 11419.0423 | 0.62287 | -3043.307
272 | C-SOK-NAP-FC-FP-WC-R100 | 18 | 0.9 | 627.6686 | 0.3649 | 0.56491 | 0.21578 | 0.21445 | 0.7783 | 1377.35 | 299.55 | 2227.75 | 2238.65 | 22.32 | 16151.015 | 919.0682 | 2630.4641 | 9.3296 | 91.8832 | 18.456 | 1.1367 | 2.7411 | 11450.3518 | 0.63706 | -2938.8976
273 | C-SOK-NAP-FC-FP-WC-R100 | 18 | 1.35 | 638.7343 | 0.37133 | 0.56464 | 0.2195 | 0.23235 | 0.78158 | 1378.25 | 306.85 | 2227.75 | 2244.6 | 22.3269 | 15963.7057 | 917.4633 | 2630.2719 | 9.3408 | 91.4674 | 18.4915 | 1.1511 | 2.7413 | 11455.7275 | 0.64327 | -2935.1839
274 | C-SOK-NAP-FC-FP-WC-R100 | 24.5 | 0.6 | 522.1836 | 0.30357 | 0.56335 | 0.26568 | 0.24664 | 0.78359 | 1374.175 | 370.375 | 2227.75 | 2433.95 | 22.3336 | 15317.4484 | 914.1281 | 2630.2813 | 9.3283 | 92.4474 | 18.5556 | 1.1643 | 2.7411 | 11457.3378 | 0.6308 | -2308.2745
275 | C-SOK-NAP-FC-FP-WC-R100 | 24.5 | 1.25 | 551.0671 | 0.32036 | 0.56368 | 0.27648 | 0.29982 | 0.81332 | 1371.425 | 390.575 | 2227.75 | 2429.6 | 22.3308 | 14669.5469 | 911.835 | 2630.4518 | 9.3393 | 91.6559 | 18.6253 | 1.2074 | 2.7409 | 11482.9227 | 0.64709 | -2197.9071
276 | C-SOK-NAP-FC-FP-WC-R100 | 24.5 | 1.85 | 562.0552 | 0.32675 | 0.56349 | 0.28486 | 0.32681 | 0.81462 | 1371.575 | 406.6 | 2227.75 | 2430.375 | 22.3365 | 14362.4328 | 910.3899 | 2630.4798 | 9.339 | 91.1688 | 18.6549 | 1.2259 | 2.7407 | 11485.352 | 0.65716 | -2240.8296
277 | C-SOK-NAP-FC-FP-WC-R100 | 31 | 0.8 | 443.4698 | 0.25781 | 0.56453 | 0.32777 | 0.31752 | 0.81316 | 1352.725 | 425.275 | 2227.75 | 2634.15 | 22.2793 | 13916.3283 | 900.5712 | 2630.4359 | 9.3659 | 90.5908 | 18.8514 | 1.2252 | 2.742 | 11488.9368 | 0.68975 | -2708.8272
278 | C-SOK-NAP-FC-FP-WC-R100 | 31 | 1.55 | 471.0432 | 0.27384 | 0.56394 | 0.35799 | 0.3743 | 0.83628 | 1351.375 | 472.425 | 2227.75 | 2612.75 | 22.2961 | 13047.0615 | 896.775 | 2630.32 | 9.3878 | 89.6456 | 18.9461 | 1.2745 | 2.7424 | 11507.8681 | 0.71113 | -2699.208
279 | C-SOK-NAP-FC-FP-WC-R100 | 31 | 2.35 | 487.3911 | 0.28335 | 0.56429 | 0.37793 | 0.41104 | 0.83744 | 1348.25 | 506.175 | 2227.75 | 2603.9 | 22.2885 | 12519.9177 | 893.0876 | 2630.485 | 9.4121 | 89.5357 | 19.0143 | 1.3132 | 2.742 | 11503.9448 | 0.72136 | -2695.8865
280 | C-SOK-NAP-FC-FP-WC-R10 | 38 | 0.95 | 387.3716 | 0.2252 | 0.56196 | 0.37732 | 0.37295 | 0.83205 | 1352.725 | 486.525 | 2227.75 | 2784.475 | 22.3237 | 12871.5393 | 895.0241 | 2630.5421 | 9.3843 | 89.4149 | 18.9827 | 1.2739 | 2.7428 | 11508.0669 | 0.72045 | -2819.2702
281 | C-SOK-NAP-FC-FP-WC-R10 | 38 | 1.9 | 420.9054 | 0.24469 | 0.56179 | 0.4238 | 0.44005 | 0.85574 | 1348.325 | 562.75 | 2227.75 | 2749.275 | 22.3299 | 11716.8167 | 892.7205 | 2630.5285 | 9.3936 | 88.7359 | 19.046 | 1.3433 | 2.7425 | 11525.8518 | 0.7365 | -2658.1054
282 | C-SOK-NAP-FC-FP-WC-R10 | 38 | 2.85 | 442.3485 | 0.25716 | 0.56196 | 0.46029 | 0.4806 | 0.86198 | 1344.55 | 621.05 | 2227.75 | 2735.6 | 22.3282 | 10943.9757 | 889.8972 | 2630.6712 | 9.4108 | 88.4159 | 19.0963 | 1.3907 | 2.7419 | 11521.1976 | 0.74616 | -2573.2251
283 | C-SOK-NAP-FC-FP-WC-R10 | 44.5 | 1.1 | 350.2502 | 0.20362 | 0.56075 | 0.40986 | 0.41793 | 0.84774 | 1350.3 | 532.375 | 2227.75 | 2895.9 | 22.3355 | 12094.8558 | 893.9611 | 2630.5316 | 9.3893 | 88.6524 | 19.018 | 1.3173 | 2.7421 | 11523.5301 | 0.7327 | -2733.8788
284 | C-SOK-NAP-FC-FP-WC-R10 | 44.5 | 2.25 | 384.9712 | 0.2238 | 0.56041 | 0.47179 | 0.49437 | 0.87023 | 1345.525 | 632.1 | 2227.75 | 2855.75 | 22.3494 | 10689.8864 | 890.9298 | 2630.5421 | 9.4074 | 87.964 | 19.0956 | 1.405 | 2.7423 | 11539.6573 | 0.75004 | -2557.5631
285 | C-SOK-NAP-FC-FP-WC-R10 | 44.5 | 3.35 | 409.9209 | 0.23831 | 0.56058 | 0.52807 | 0.548 | 0.87406 | 1339.55 | 717.325 | 2227.75 | 2836.2 | 22.3569 | 9590.9977 | 887.8771 | 2630.6556 | 9.4238 | 87.4081 | 19.1557 | 1.4732 | 2.7426 | 11537.6126 | 0.76442 | -2523.6806
286 | C-SOK-NAP-FC-FP-WC-R600 | 18 | 0.45 | 597.3593 | 0.34728 | 0.56444 | 0.20404 | 0.17164 | 0.80027 | 1498.85 | 309.6 | 2346.175 | 2249.65 | 24.2045 | 14277.0737 | 956.3407 | 2805.0601 | 9.2655 | 88.7799 | 15.0316 | 1.0506 | 2.7537 | 8063.1856 | 0.62444 | -5331.8876
287 | C-SOK-NAP-FC-FP-WC-R600 | 18 | 0.9 | 621.2661 | 0.36117 | 0.56466 | 0.20395 | 0.22438 | 0.83156 | 1497.9 | 311.275 | 2346.175 | 2244.1 | 24.2027 | 13950.2566 | 954.3171 | 2805.1987 | 9.2948 | 87.2479 | 15.1144 | 1.0762 | 2.7537 | 8116.9244 | 0.63403 | -5259.408
288 | C-SOK-NAP-FC-FP-WC-R600 | 18 | 1.35 | 632.3444 | 0.36762 | 0.56474 | 0.20677 | 0.25586 | 0.83588 | 1496.775 | 318 | 2346.175 | 2250.125 | 24.2011 | 13775.7384 | 953.0619 | 2805.0407 | 9.3047 | 86.324 | 15.1405 | 1.0885 | 2.7538 | 8124.6832 | 0.63876 | -5238.179
289 | C-SOK-NAP-FC-FP-WC-R600 | 24.5 | 0.6 | 514.9067 | 0.29934 | 0.56322 | 0.25363 | 0.25449 | 0.83669 | 1493.875 | 387.625 | 2346.175 | 2435.725 | 24.2177 | 13198.507 | 950.5126 | 2804.9944 | 9.2807 | 87.5806 | 15.18 | 1.0995 | 2.754 | 8125.8026 | 0.62499 | -4617.9477
290 | C-SOK-NAP-FC-FP-WC-R600 | 24.5 | 1.25 | 539.8726 | 0.31386 | 0.56334 | 0.26597 | 0.32251 | 0.86465 | 1491.7 | 409.975 | 2346.175 | 2433.075 | 24.2162 | 12661.9131 | 947.9557 | 2804.9031 | 9.2936 | 86.6475 | 15.2571 | 1.1382 | 2.7536 | 8166.4087 | 0.63935 | -4543.2311
291 | C-SOK-NAP-FC-FP-WC-R600 | 24.5 | 1.85 | 552.9912 | 0.32148 | 0.56351 | 0.27337 | 0.37507 | 0.86783 | 1490.925 | 425.9 | 2346.175 | 2440.225 | 24.2223 | 12353.0372 | 945.5904 | 2805.2091 | 9.305 | 86.1793 | 15.2945 | 1.1622 | 2.754 | 8166.2466 | 0.64693 | -4515.7251
292 | C-SOK-NAP-FC-FP-WC-R600 | 31 | 0.8 | 430.6747 | 0.25037 | 0.56369 | 0.31521 | 0.32629 | 0.86438 | 1474.3 | 448.125 | 2346.175 | 2645.025 | 24.1805 | 12010.1249 | 938.2898 | 2804.8851 | 9.2884 | 85.5519 | 15.4137 | 1.15 | 2.7548 | 8173.0407 | 0.68254 | -5090.3496
293 | C-SOK-NAP-FC-FP-WC-R600 | 31 | 1.55 | 455.8515 | 0.26501 | 0.56414 | 0.3425 | 0.4066 | 0.88185 | 1468.8 | 494.725 | 2346.175 | 2646.75 | 24.1685 | 11272.7523 | 932.5122 | 2804.9588 | 9.3266 | 85.0661 | 15.5292 | 1.2002 | 2.7547 | 8199.277 | 0.69815 | -5041.658
294 | C-SOK-NAP-FC-FP-WC-R600 | 31 | 2.35 | 472.291 | 0.27457 | 0.56468 | 0.36174 | 0.47025 | 0.88778 | 1463.9 | 528 | 2346.175 | 2636.35 | 24.1583 | 10748.8027 | 928.963 | 2805.0489 | 9.3464 | 84.8744 | 15.5831 | 1.2384 | 2.7546 | 8197.902 | 0.70868 | -5012.9073
295 | C-SOK-NAP-FC-FP-WC-R60 | 38 | 0.95 | 373.055 | 0.21688 | 0.56247 | 0.36335 | 0.38842 | 0.8795 | 1467.875 | 509.75 | 2346.175 | 2811.025 | 24.1924 | 11108.1583 | 930.5465 | 2804.9523 | 9.3207 | 84.557 | 15.5602 | 1.1951 | 2.7553 | 8198.1615 | 0.71038 | -5209.5608
296 | C-SOK-NAP-FC-FP-WC-R60 | 38 | 1.9 | 403.4112 | 0.23452 | 0.56241 | 0.40737 | 0.47938 | 0.8978 | 1463.375 | 587.3 | 2346.175 | 2798.675 | 24.1971 | 10114.3817 | 927.577 | 2805.0777 | 9.3305 | 84.221 | 15.6282 | 1.2563 | 2.7549 | 8220.166 | 0.7232 | -5037.112
297 | C-SOK-NAP-FC-FP-WC-R60 | 38 | 2.85 | 425.4026 | 0.24731 | 0.56262 | 0.44555 | 0.54485 | 0.90709 | 1458.95 | 652.425 | 2346.175 | 2773.15 | 24.1955 | 9327.934 | 925.0751 | 2805.0883 | 9.3403 | 84.1557 | 15.6728 | 1.3103 | 2.7549 | 8225.1677 | 0.73447 | -4957.2581
298 | C-SOK-NAP-FC-FP-WC-R60 | 44.5 | 1.1 | 335.2994 | 0.19493 | 0.56173 | 0.394 | 0.43728 | 0.89296 | 1463.5 | 554.7 | 2346.175 | 2930.575 | 24.199 | 10476.8933 | 929.5788 | 2804.8523 | 9.3237 | 83.8829 | 15.5927 | 1.2296 | 2.7548 | 8216.8928 | 0.71946 | -5109.1344
299 | C-SOK-NAP-FC-FP-WC-R60 | 44.5 | 2.25 | 367.7002 | 0.21376 | 0.56186 | 0.45755 | 0.54617 | 0.9118 | 1455.85 | 660.675 | 2346.175 | 2908.3 | 24.2072 | 9157.8415 | 924.7452 | 2804.882 | 9.3481 | 83.5248 | 15.6895 | 1.3095 | 2.7556 | 8235.3462 | 0.73784 | -4960.1829
300 | C-SOK-NAP-FC-FP-WC-R60 | 44.5 | 3.35 | 389.5518 | 0.22647 | 0.56112 | 0.5056 | 0.60893 | 0.92349 | 1455.275 | 743.775 | 2346.175 | 2891.7 | 24.236 | 8253.3002 | 923.1897 | 2804.8897 | 9.3379 | 83.7066 | 15.7237 | 1.3706 | 2.7556 | 8244.6997 | 0.75016 | -4886.019
301 | C-SOK-STR-FC-ET-HC-OFF0 | 11.5 | 0.288 | 501.305 | 0.43581 | 0.67321 | 0.33616 | 0.053667 | 1 | 384.275 | 132.875 | 1446.5 | 2418.425 | 0 | 8731.7881 | 437.5659 | 1243.3783 | 12.9503 | 50.9333 | 20.794 | 1.0945 | 2.8887 | 6046.5519 | 0.32066 | 3916.4018
302 | C-SOK-STR-FC-ET-HC-OFF0 | 11.5 | 0.575 | 515.945 | 0.44853 | 0.67319 | 0.35187 | 0.062417 | 1 | 383.8 | 137.55 | 1446.5 | 2381.125 | 0 | 8608.3586 | 437.1998 | 1243.681 | 13.0518 | 50.5061 | 20.8129 | 1.1006 | 2.8884 | 6046.5519 | 0.33254 | 3960.27
303 | C-SOK-STR-FC-ET-HC-OFF0 | 11.5 | 0.863 | 521.9744 | 0.45378 | 0.67311 | 0.35533 | 0.068596 | 1 | 384.1 | 139.85 | 1446.5 | 2366.725 | 0 | 8555.5547 | 436.8967 | 1243.3881 | 13.0934 | 50.3722 | 20.8272 | 1.1045 | 2.8892 | 6046.5519 | 0.33757 | 3976.3978
304 | C-SOK-STR-FC-ET-HC-OFF0 | 15.5 | 0.388 | 451.2849 | 0.39232 | 0.67388 | 0.48748 | 0.10831 | 1 | 374.25 | 181.25 | 1446.5 | 2553.375 | 0 | 7713.3373 | 419.7361 | 1243.3938 | 13.6389 | 48.3594 | 21.6783 | 1.1472 | 2.889 | 6046.5519 | 0.40932 | 4131.7499
305 | C-SOK-STR-FC-ET-HC-OFF0 | 15.5 | 0.775 | 468.2388 | 0.40706 | 0.67392 | 0.52061 | 0.12345 | 1 | 372.5 | 191.775 | 1446.5 | 2509.075 | 0 | 7471.1908 | 418.8565 | 1243.5689 | 13.7829 | 47.7197 | 21.7226 | 1.1622 | 2.8881 | 6046.5519 | 0.42772 | 4153.4729
306 | C-SOK-STR-FC-ET-HC-OFF0 | 15.5 | 1.163 | 478.1975 | 0.41572 | 0.6739 | 0.54323 | 0.13156 | 1 | 371.75 | 198.35 | 1446.5 | 2484.125 | 0 | 7319.8127 | 419.7928 | 1243.3051 | 13.7763 | 47.3101 | 21.6743 | 1.1719 | 2.8888 | 6046.5519 | 0.43926 | 4156.2202
307 | C-SOK-STR-FC-ET-HC-OFF0 | 20 | 0.5 | 405.844 | 0.35282 | 0.67453 | 0.62096 | 0.16729 | 1 | 365.475 | 223.9 | 1446.5 | 2690.15 | 0 | 6750.4511 | 403.2387 | 1243.1416 | 14.4811 | 46.5313 | 22.5654 | 1.2089 | 2.8898 | 6046.5519 | 0.47084 | 4295.1313
308 | C-SOK-STR-FC-ET-HC-OFF0 | 20 | 1 | 424.7679 | 0.36927 | 0.67468 | 0.6696 | 0.18958 | 1 | 362 | 239.15 | 1446.5 | 2634.975 | 0 | 6395.1121 | 401.7674 | 1242.9798 | 14.7518 | 45.6059 | 22.6476 | 1.2331 | 2.8901 | 6046.5519 | 0.49154 | 4319.533
309 | C-SOK-STR-FC-ET-HC-OFF0 | 20 | 1.5 | 433.8634 | 0.37718 | 0.67494 | 0.69712 | 0.19854 | 1 | 359.975 | 247.35 | 1446.5 | 2611.55 | 0 | 6215.931 | 401.793 | 1243.082 | 14.8825 | 44.9108 | 22.6463 | 1.2402 | 2.8898 | 6046.5519 | 0.5017 | 4323.9023
310 | C-SOK-STR-FC-ET-HC-OFF | 24 | 0.6 | 371.4105 | 0.32288 | 0.67519 | 0.70501 | 0.21084 | 1 | 358.65 | 251.1 | 1446.5 | 2799.65 | 0 | 6105.1588 | 391.2876 | 1242.9552 | 15.2648 | 45.4741 | 23.2531 | 1.2557 | 2.8897 | 6046.5519 | 0.50054 | 4452.1258
311 | C-SOK-STR-FC-ET-HC-OFF | 24 | 1.2 | 388.5408 | 0.33778 | 0.67554 | 0.75639 | 0.2377 | 1 | 354.85 | 266.95 | 1446.5 | 2748.375 | 0 | 5710.1665 | 391.8238 | 1243.1675 | 15.4626 | 44.3441 | 23.2227 | 1.281 | 2.8897 | 6046.5519 | 0.52067 | 4469.7479
312 | C-SOK-STR-FC-ET-HC-OFF | 24 | 1.8 | 397.8691 | 0.34589 | 0.67587 | 0.78955 | 0.25263 | 1 | 352.075 | 278.55 | 1446.5 | 2722.725 | 0 | 5469.4263 | 389.3419 | 1243.2154 | 15.7788 | 43.7051 | 23.3697 | 1.3009 | 2.8892 | 6046.5519 | 0.53338 | 4455.6754
313 | C-SOK-STR-FC-ET-HC-OFF | 28.5 | 0.713 | 336.4228 | 0.29247 | 0.67617 | 0.77896 | 0.25784 | 1 | 351.825 | 273.15 | 1446.5 | 2913.55 | 0 | 5485.5146 | 382.4048 | 1243.1366 | 15.8477 | 44.6679 | 23.7955 | 1.3107 | 2.89 | 6046.5519 | 0.52942 | 4511.9466
314 | C-SOK-STR-FC-ET-HC-OFF | 28.5 | 1.425 | 351.4933 | 0.30557 | 0.67673 | 0.83558 | 0.28903 | 1 | 346.7 | 290.65 | 1446.5 | 2867.2 | 0 | 5040.4604 | 382.2691 | 1242.8397 | 16.184 | 43.2095 | 23.8016 | 1.3378 | 2.89 | 6046.5519 | 0.55064 | 4501.4634
315 | C-SOK-STR-FC-ET-HC-OFF | 28.5 | 2.138 | 359.6363 | 0.31265 | 0.67705 | 0.87113 | 0.30123 | 1 | 343.925 | 302.225 | 1446.5 | 2843.55 | 0 | 4806.0695 | 379.1078 | 1243.0359 | 16.6534 | 42.4675 | 24 | 1.3598 | 2.8894 | 6046.5519 | 0.56083 | 4501.3207
316 | C-SOK-STR-FC-ET-WC-OFF0 | 18 | 0.45 | 413.4505 | 0.35943 | 0.59235 | 0.3215 | 0.083902 | 1 | 876.275 | 286.775 | 1446.5 | 2508.7 | 15.5776 | 14303.8091 | 688.8725 | 1886.8529 | 9.7802 | 77.0798 | 20.9101 | 1.0404 | 2.8418 | 9572.9904 | 0.46027 | 4016.7012
317 | C-SOK-STR-FC-ET-WC-OFF0 | 18 | 0.9 | 422.9821 | 0.36772 | 0.59172 | 0.32588 | 0.093207 | 1 | 878.125 | 292.525 | 1446.5 | 2487.25 | 15.592 | 14185.144 | 690.3825 | 1886.6692 | 9.7689 | 76.6827 | 20.8646 | 1.0462 | 2.8422 | 9572.9904 | 0.46668 | 4060.5049
318 | C-SOK-STR-FC-ET-WC-OFF0 | 18 | 1.35 | 429.9649 | 0.37379 | 0.5916 | 0.33171 | 0.099957 | 1 | 878.85 | 297.6 | 1446.5 | 2469.825 | 15.5921 | 14074.0055 | 691.5481 | 1886.8405 | 9.762 | 76.1062 | 20.8294 | 1.0476 | 2.842 | 9572.9904 | 0.47367 | 4073.4295
319 | C-SOK-STR-FC-ET-WC-OFF0 | 24.5 | 0.6 | 375.4956 | 0.32643 | 0.58799 | 0.44279 | 0.13507 | 1 | 877.875 | 385.725 | 1446.5 | 2610.275 | 15.6378 | 12859.3599 | 684.2849 | 1886.9997 | 9.8229 | 74.0387 | 21.0518 | 1.0913 | 2.8422 | 9572.9904 | 0.53613 | 4267.4783
320 | C-SOK-STR-FC-ET-WC-OFF0 | 24.5 | 1.25 | 387.4403 | 0.33682 | 0.58681 | 0.46025 | 0.15182 | 1 | 879.95 | 402.2 | 1446.5 | 2577.95 | 15.653 | 12563.7092 | 685.218 | 1887.0437 | 9.8061 | 73.4529 | 21.0219 | 1.1067 | 2.8417 | 9572.9904 | 0.55234 | 4249.3156
321 | C-SOK-STR-FC-ET-WC-OFF0 | 24.5 | 1.85 | 394.3402 | 0.34282 | 0.58652 | 0.47164 | 0.15967 | 1 | 880.35 | 413.475 | 1446.5 | 2559.1 | 15.6585 | 12396.8895 | 685.6072 | 1887.0099 | 9.7973 | 73.2817 | 21.0099 | 1.1182 | 2.8417 | 9572.9904 | 0.56034 | 4247.6763
322 | C-SOK-STR-FC-ET-WC-OFF0 | 31 | 0.8 | 335.0555 | 0.29128 | 0.58783 | 0.54043 | 0.18368 | 1 | 866.125 | 454.6 | 1446.5 | 2728.575 | 15.6237 | 11592.1069 | 676.2586 | 1887.011 | 9.9197 | 71.824 | 21.3006 | 1.1466 | 2.8418 | 9572.9904 | 0.59696 | 4186.2494
323 | C-SOK-STR-FC-ET-WC-OFF0 | 31 | 1.55 | 348.9526 | 0.30336 | 0.58656 | 0.56469 | 0.20457 | 1 | 868.275 | 477.975 | 1446.5 | 2684.025 | 15.6387 | 11200.3611 | 677.0323 | 1886.9092 | 9.9215 | 71.1885 | 21.2761 | 1.1691 | 2.8419 | 9572.9904 | 0.61103 | 4207.6884
324 | C-SOK-STR-FC-ET-WC-OFF0 | 31 | 2.35 | 356.9457 | 0.31031 | 0.58573 | 0.5821 | 0.21509 | 1 | 870 | 496.025 | 1446.5 | 2662.8 | 15.6529 | 10961.386 | 678.6767 | 1886.8877 | 9.9045 | 70.5433 | 21.2251 | 1.1777 | 2.8422 | 9572.9904 | 0.62006 | 4204.1015
325 | C-SOK-STR-FC-ET-WC-OFF | 38 | 0.95 | 299.9719 | 0.26078 | 0.58598 | 0.62164 | 0.22611 | 1 | 860.125 | 512.95 | 1446.5 | 2843.975 | 15.6351 | 10528.6503 | 672.2762 | 1887.1173 | 9.985 | 69.9323 | 21.4277 | 1.197 | 2.842 | 9572.9904 | 0.63962 | 4107.9016
326 | C-SOK-STR-FC-ET-WC-OFF | 38 | 1.9 | 317.4895 | 0.27601 | 0.58429 | 0.66193 | 0.25457 | 1 | 862.925 | 551.825 | 1446.5 | 2788.6 | 15.6546 | 9931.7156 | 673.74 | 1887.0741 | 9.9935 | 68.823 | 21.3804 | 1.2301 | 2.8417 | 9572.9904 | 0.65571 | 4153.7412
327 | C-SOK-STR-FC-ET-WC-OFF | 38 | 2.85 | 325.889 | 0.28331 | 0.58387 | 0.68635 | 0.26925 | 1 | 862.975 | 578.125 | 1446.5 | 2761.175 | 15.6643 | 9590.8899 | 674.7623 | 1886.8273 | 9.9858 | 68.1335 | 21.3475 | 1.2497 | 2.8419 | 9572.9904 | 0.66676 | 4126.71
328 | C-SOK-STR-FC-ET-WC-OFF | 44.5 | 1.1 | 274.6281 | 0.23875 | 0.58448 | 0.67574 | 0.2641 | 1 | 856.5 | 552.4 | 1446.5 | 2935.425 | 15.6431 | 9725.0784 | 670.9603 | 1886.7867 | 10.0236 | 68.7265 | 21.4682 | 1.2445 | 2.8419 | 9572.9904 | 0.66394 | 4107.02
329 | C-SOK-STR-FC-ET-WC-OFF | 44.5 | 2.25 | 292.4273 | 0.25422 | 0.5827 | 0.73163 | 0.29646 | 1 | 858.55 | 607.95 | 1446.5 | 2879.7 | 15.6676 | 8960.056 | 673.3688 | 1887.013 | 10.0334 | 66.884 | 21.3912 | 1.2824 | 2.8415 | 9572.9904 | 0.68424 | 4109.0143
330 | C-SOK-STR-FC-ET-WC-OFF | 44.5 | 3.35 | 301.0139 | 0.26168 | 0.5821 | 0.76301 | 0.30781 | 1 | 858.45 | 639.75 | 1446.5 | 2849.85 | 15.6795 | 8593.7286 | 674.8979 | 1886.9065 | 10.0466 | 65.8113 | 21.3443 | 1.3002 | 2.8423 | 9572.9904 | 0.69284 | 4114.4
331 | C-SOK-STR-FC-FP-HC-OFF0 | 11.5 | 0.288 | 337.3991 | 0.29332 | 0.67303 | 0.14032 | 0.015387 | 1 | 392.375 | 69.825 | 1446.5 | 2934.425 | 0 | 9851.5624 | 428.7201 | 1243.5403 | 13.0027 | 54.8429 | 21.2219 | 1.0472 | 2.8878 | 6046.5519 | 0.18796 | 3150.7977
332 | C-SOK-STR-FC-FP-HC-OFF0 | 11.5 | 0.575 | 343.7708 | 0.29886 | 0.67292 | 0.13796 | 0.027205 | 1 | 393.025 | 69.325 | 1446.5 | 2964.475 | 0 | 9792.1703 | 425.9417 | 1243.5247 | 13.0773 | 54.7053 | 21.3617 | 1.0557 | 2.8883 | 6046.5519 | 0.1999 | 3163.0961
333 | C-SOK-STR-FC-FP-HC-OFF0 | 11.5 | 0.863 | 345.262 | 0.30015 | 0.67285 | 0.13362 | 0.030773 | 1 | 393.525 | 67.5 | 1446.5 | 2985.35 | 0 | 9791.062 | 425.9066 | 1243.5413 | 13.0514 | 54.7414 | 21.3642 | 1.0578 | 2.8886 | 6046.5519 | 0.19954 | 3178.245
334 | C-SOK-STR-FC-FP-HC-OFF0 | 15.5 | 0.388 | 302.4673 | 0.26295 | 0.67332 | 0.23685 | 0.053956 | 1 | 386.925 | 102.7 | 1446.5 | 3027.05 | 0 | 9179.281 | 418.4499 | 1243.2549 | 13.189 | 52.8319 | 21.743 | 1.0853 | 2.8886 | 6046.5519 | 0.29857 | 3288.4746
335 | C-SOK-STR-FC-FP-HC-OFF0 | 15.5 | 0.775 | 312.1595 | 0.27137 | 0.67326 | 0.2498 | 0.069692 | 1 | 387.025 | 106.95 | 1446.5 | 3052.3 | 0 | 9025.9315 | 416.543 | 1243.1806 | 13.2013 | 52.481 | 21.843 | 1.0959 | 2.889 | 6046.5519 | 0.32113 | 3284.7081
336 | C-SOK-STR-FC-FP-HC-OFF0 | 15.5 | 1.163 | 318.1553 | 0.27659 | 0.67335 | 0.2544 | 0.081719 | 1 | 387.1 | 109.35 | 1446.5 | 3056.95 | 0 | 8932.5507 | 415.9794 | 1243.1161 | 13.1818 | 52.3733 | 21.8739 | 1.1048 | 2.8897 | 6046.5519 | 0.33406 | 3284.0027
337 | C-SOK-STR-FC-FP-HC-OFF0 | 20 | 0.5 | 268.7076 | 0.2336 | 0.67387 | 0.3139 | 0.092823 | 1 | 382.25 | 128.875 | 1446.5 | 3135.7 | 0 | 8592.492 | 410.2678 | 1243.5032 | 13.3772 | 51.6135 | 22.1767 | 1.1206 | 2.888 | 6046.5519 | 0.36896 | 3391.2891
338 | C-SOK-STR-FC-FP-HC-OFF0 | 20 | 1 | 283.961 | 0.24686 | 0.67396 | 0.3512 | 0.11371 | 1 | 380.55 | 141.225 | 1446.5 | 3136.35 | 0 | 8297.0359 | 408.0208 | 1243.4516 | 13.4553 | 50.9826 | 22.2992 | 1.1386 | 2.8883 | 6046.5519 | 0.4011 | 3401.2638
339 | C-SOK-STR-FC-FP-HC-OFF0 | 20 | 1.5 | 291.9694 | 0.25382 | 0.67391 | 0.36817 | 0.12648 | 1 | 380.2 | 147.475 | 1446.5 | 3126 | 0 | 8144.003 | 407.0603 | 1243.1881 | 13.5048 | 50.7017 | 22.3539 | 1.1493 | 2.8898 | 6046.5519 | 0.41658 | 3406.8374
340 | C-SOK-STR-FC-FP-HC-OFF | 24 | 0.6 | 246.0433 | 0.2139 | 0.67408 | 0.36636 | 0.12278 | 1 | 380.625 | 148.75 | 1446.5 | 3208.925 | 0 | 8173.0547 | 406.3753 | 1243.1589 | 13.4788 | 51.0417 | 22.3896 | 1.1496 | 2.8891 | 6046.5519 | 0.40664 | 3503.8147
341 | C-SOK-STR-FC-FP-HC-OFF | 24 | 1.2 | 263.3167 | 0.22891 | 0.67421 | 0.41536 | 0.15213 | 1 | 377.85 | 165.1 | 1446.5 | 3194.425 | 0 | 7773.587 | 402.9208 | 1242.9775 | 13.6383 | 50.4171 | 22.5825 | 1.1791 | 2.89 | 6046.5519 | 0.44312 | 3519.2371
342 | C-SOK-STR-FC-FP-HC-OFF | 24 | 1.8 | 272.0448 | 0.2365 | 0.6742 | 0.43925 | 0.16952 | 1 | 376.725 | 172.65 | 1446.5 | 3187.325 | 0 | 7560.4097 | 402.1405 | 1243.2923 | 13.6829 | 49.9062 | 22.6267 | 1.1896 | 2.8893 | 6046.5519 | 0.4616 | 3515.2369
343 | C-SOK-STR-FC-FP-HC-OFF | 28.5 | 0.713 | 224.2543 | 0.19495 | 0.67479 | 0.42404 | 0.15572 | 1 | 377.875 | 170.75 | 1446.5 | 3278.5 | 0 | 7710.012 | 404.0627 | 1243.5384 | 13.4901 | 50.4542 | 22.5178 | 1.1847 | 2.8881 | 6046.5519 | 0.4474 | 3531.7726
344 | C-SOK-STR-FC-FP-HC-OFF | 28.5 | 1.425 | 241.7576 | 0.21017 | 0.67484 | 0.48369 | 0.19242 | 1 | 374.25 | 188.6 | 1446.5 | 3267.175 | 0 | 7218.5677 | 397.6348 | 1243.4469 | 13.8374 | 49.6407 | 22.8831 | 1.2189 | 2.8888 | 6046.5519 | 0.4864 | 3538.7246
345 | C-SOK-STR-FC-FP-HC-OFF | 28.5 | 2.138 | 251.4028 | 0.21856 | 0.67479 | 0.50958 | 0.2126 | 1 | 373.5 | 197.65 | 1446.5 | 3254.25 | 0 | 6979.3574 | 397.8262 | 1243.3676 | 13.8332 | 49.2899 | 22.8714 | 1.2361 | 2.8888 | 6046.5519 | 0.50112 | 3574.4475
346 | C-SOK-TOU-CC-ET-HC-R100 | 16.5 | 0.413 | 610.3823 | 0.41175 | 0.72704 | 0.30494 | 0.092971 | 0.61814 | 255.625 | 86.475 | 850.5 | 2253.525 | 0 | 22944.6534 | 417.9163 | 970.1318 | 17.8437 | 123.5161 | 57.9018 | 1.2355 | 3.1045 | 25635.3394 | 0.58909 | -8723.67
347 | C-SOK-TOU-CC-ET-HC-R100 | 16.5 | 0.825 | 653.9029 | 0.44111 | 0.72675 | 0.32903 | 0.10873 | 0.65831 | 256.1 | 90.175 | 850.5 | 2142.475 | 0 | 22359.6234 | 423.3072 | 970.0433 | 17.8084 | 121.2147 | 57.362 | 1.2564 | 3.1021 | 25685.7334 | 0.60863 | -8574.382
348 | C-SOK-TOU-CC-ET-HC-R100 | 16.5 | 1.238 | 667.9171 | 0.45056 | 0.72663 | 0.34635 | 0.11571 | 0.66146 | 255.825 | 92.7 | 850.5 | 2104.1 | 0 | 22147.4837 | 424.6115 | 970.0898 | 17.7904 | 120.4694 | 57.2322 | 1.267 | 3.1025 | 25696.46 | 0.61619 | -8579.5271
349 | C-SOK-TOU-CC-ET-HC-R100 | 22.5 | 0.563 | 536.9018 | 0.36218 | 0.72544 | 0.44592 | 0.14071 | 0.65748 | 250.425 | 118.55 | 850.5 | 2451.525 | 0 | 21327.9565 | 401.5348 | 969.9874 | 18.7591 | 121.3107 | 60.0544 | 1.2935 | 3.1047 | 25692.5639 | 0.63025 | -8352.1391
350 | C-SOK-TOU-CC-ET-HC-R100 | 22.5 | 1.125 | 576.3466 | 0.38879 | 0.72495 | 0.49562 | 0.16293 | 0.68886 | 250.2 | 126.275 | 850.5 | 2344.825 | 0 | 20566.737 | 406.413 | 970.1354 | 18.7345 | 118.8469 | 59.5345 | 1.3209 | 3.1054 | 25739.1545 | 0.64968 | -8240.7985
351 | C-SOK-TOU-CC-ET-HC-R100 | 22.5 | 1.688 | 590.9657 | 0.39865 | 0.72457 | 0.52425 | 0.17122 | 0.69849 | 249.65 | 131.625 | 850.5 | 2301.175 | 0 | 20254.9594 | 405.6357 | 970.1142 | 19.044 | 118.087 | 59.6387 | 1.3358 | 3.1042 | 25742.9248 | 0.65737 | -8189.54
352 | C-SOK-TOU-CC-ET-HC-R100 | 29 | 0.725 | 472.7716 | 0.31892 | 0.72621 | 0.52301 | 0.18654 | 0.68971 | 246.725 | 135.75 | 850.5 | 2636.05 | 0 | 19978.7031 | 397.2891 | 970.1043 | 18.4822 | 120.0251 | 60.6947 | 1.343 | 3.1054 | 25733.0404 | 0.65652 | -8054.4424
353 | C-SOK-TOU-CC-ET-HC-R100 | 29 | 1.45 | 508.1442 | 0.34278 | 0.72509 | 0.58955 | 0.21515 | 0.7166 | 246.35 | 149.175 | 850.5 | 2534.25 | 0 | 19050.3697 | 396.9723 | 970.1259 | 19.0888 | 117.7547 | 60.8393 | 1.3826 | 3.1045 | 25781.2798 | 0.67737 | -7998.1452
354 | C-SOK-TOU-CC-ET-HC-R100 | 29 | 2.175 | 522.7075 | 0.35261 | 0.72487 | 0.62365 | 0.22652 | 0.72177 | 246.125 | 156.2 | 850.5 | 2491.325 | 0 | 18680.7067 | 400.0785 | 970.178 | 18.9092 | 116.7678 | 60.4526 | 1.3978 | 3.1061 | 25788.8716 | 0.68357 | -7949.2297
355 | C-SOK-TOU-CC-ET-HC-R10 | 35 | 0.875 | 425.8079 | 0.28724 | 0.72425 | 0.6243 | 0.22568 | 0.7117 | 241.3 | 154.25 | 850.5 | 2776.9 | 0 | 18740.2229 | 383.8506 | 970.1091 | 19.9144 | 118.4294 | 62.5768 | 1.3867 | 3.1072 | 25761.818 | 0.68971 | -8103.307
356 | C-SOK-TOU-CC-ET-HC-R10 | 35 | 1.75 | 458.1767 | 0.30908 | 0.72398 | 0.67771 | 0.25616 | 0.73428 | 241.725 | 165.725 | 850.5 | 2682.425 | 0 | 17833.8452 | 387.8719 | 970.1341 | 19.8244 | 117.0742 | 62.1275 | 1.4372 | 3.1079 | 25809.1122 | 0.70059 | -7932.458
357 | C-SOK-TOU-CC-ET-HC-R10 | 35 | 2.625 | 470.9642 | 0.3177 | 0.72361 | 0.70904 | 0.27059 | 0.73475 | 241.6 | 172.25 | 850.5 | 2642.575 | 0 | 17432.0586 | 389.959 | 970.0977 | 19.8385 | 115.8437 | 61.8578 | 1.4506 | 3.1074 | 25816.3958 | 0.70645 | -7911.0021
358 | C-SOK-TOU-CC-ET-HC-R10 | 41 | 1.025 | 389.2693 | 0.26259 | 0.72398 | 0.67056 | 0.26207 | 0.7272 | 238.725 | 162.475 | 850.5 | 2891.125 | 0 | 17764.6654 | 381.4835 | 970.1156 | 20.0218 | 117.5391 | 62.9708 | 1.4287 | 3.1076 | 25789.4604 | 0.70701 | -8043.8363
359 | C-SOK-TOU-CC-ET-HC-R10 | 41 | 2.05 | 418.4849 | 0.2823 | 0.72357 | 0.7386 | 0.29443 | 0.74974 | 237.025 | 174.925 | 850.5 | 2802.475 | 0 | 16767.3014 | 382.5762 | 970.2167 | 20.469 | 115.8814 | 62.8977 | 1.4808 | 3.1071 | 25825.549 | 0.71799 | -7858.2726
360 | C-SOK-TOU-CC-ET-HC-R10 | 41 | 3.075 | 432.4365 | 0.29171 | 0.72312 | 0.78017 | 0.31224 | 0.75078 | 238.4 | 185.95 | 850.5 | 2760.35 | 0 | 16258.8316 | 385.5855 | 970.1519 | 20.3132 | 114.7418 | 62.4933 | 1.5037 | 3.1078 | 25832.099 | 0.72401 | -7814.8417
361 | C-SOK-TOU-CC-ET-HC-R600 | 16.5 | 0.413 | 610.2845 | 0.41367 | 0.73472 | 0.2787 | 0.084554 | 0.67107 | 318.275 | 100.075 | 1048.625 | 2239.825 | 0 | 16618.0745 | 425.3279 | 1162.3597 | 18.2578 | 102.2637 | 43.716 | 1.2234 | 3.1473 | 18397.0081 | 0.59046 | -13303.4314
362 | C-SOK-TOU-CC-ET-HC-R600 | 16.5 | 0.825 | 649.9073 | 0.44052 | 0.73451 | 0.29182 | 0.097874 | 0.70887 | 319 | 100.825 | 1048.625 | 2135.5 | 0 | 16210.6448 | 431.239 | 1162.3426 | 18.2322 | 100.5062 | 43.3833 | 1.2373 | 3.146 | 18491.4558 | 0.60121 | -13238.2475
363 | C-SOK-TOU-CC-ET-HC-R600 | 16.5 | 1.238 | 664.5477 | 0.45045 | 0.73422 | 0.30874 | 0.10466 | 0.71425 | 319.65 | 104.475 | 1048.625 | 2095.2 | 0 | 16031.3409 | 434.4485 | 1162.3569 | 18.0939 | 99.6385 | 43.157 | 1.2429 | 3.1463 | 18517.1833 | 0.60686 | -13254.0749
364 | C-SOK-TOU-CC-ET-HC-R600 | 22.5 | 0.563 | 530.5903 | 0.35965 | 0.73326 | 0.40838 | 0.1343 | 0.71249 | 311.925 | 136.35 | 1048.625 | 2451 | 0 | 15240.309 | 408.5471 | 1162.2541 | 19.0898 | 99.383 | 45.4621 | 1.2764 | 3.1476 | 18491.2281 | 0.62204 | -12981.4515
365 | C-SOK-TOU-CC-ET-HC-R600 | 22.5 | 1.125 | 564.8025 | 0.38284 | 0.73275 | 0.45387 | 0.15458 | 0.73559 | 312.625 | 145.725 | 1048.625 | 2356.625 | 0 | 14681.1828 | 413.8683 | 1162.2761 | 18.9728 | 97.6123 | 45.1124 | 1.3007 | 3.1484 | 18564.6526 | 0.63445 | -12946.5382
366 | C-SOK-TOU-CC-ET-HC-R600 | 22.5 | 1.688 | 579.3644 | 0.39271 | 0.73237 | 0.48297 | 0.16507 | 0.73905 | 312.4 | 152.5 | 1048.625 | 2314.575 | 0 | 14409.9883 | 414.3761 | 1162.3047 | 19.0916 | 96.8239 | 45.1004 | 1.3143 | 3.1475 | 18582.5708 | 0.64077 | -12945.0634
367 | C-SOK-TOU-CC-ET-HC-R600 | 29 | 0.725 | 460.6556 | 0.31224 | 0.73376 | 0.48669 | 0.18506 | 0.73848 | 307.875 | 158.775 | 1048.625 | 2649.975 | 0 | 14127.6461 | 403.3553 | 1162.2494 | 18.8866 | 98.0501 | 46.0908 | 1.3279 | 3.1482 | 18549.3643 | 0.64337 | -12764.0445
368 | C-SOK-TOU-CC-ET-HC-R600 | 29 | 1.45 | 490.4008 | 0.33241 | 0.73273 | 0.55698 | 0.21249 | 0.75971 | 306.8 | 173.925 | 1048.625 | 2563.475 | 0 | 13376.2511 | 404.3837 | 1162.3123 | 19.1984 | 95.7943 | 46.1057 | 1.3597 | 3.1481 | 18603.7686 | 0.66142 | -12760.3983
369 | C-SOK-TOU-CC-ET-HC-R600 | 29 | 2.175 | 506.1563 | 0.34309 | 0.73238 | 0.59363 | 0.22795 | 0.76148 | 306.95 | 183.35 | 1048.625 | 2516.975 | 0 | 13018.7154 | 408.2142 | 1162.3399 | 19.0043 | 94.8338 | 45.7679 | 1.3774 | 3.1486 | 18619.7153 | 0.66647 | -12718.7823
370 | C-SOK-TOU-CC-ET-HC-R60 | 35 | 0.875 | 410.4503 | 0.27821 | 0.73233 | 0.57538 | 0.22827 | 0.76027 | 301.95 | 179.85 | 1048.625 | 2798 | 0 | 13088.9802 | 391.903 | 1162.3016 | 19.7263 | 96.3334 | 47.3201 | 1.3732 | 3.1483 | 18583.649 | 0.67356 | -12820.9071
371 | C-SOK-TOU-CC-ET-HC-R60 | 35 | 1.75 | 439.5727 | 0.29795 | 0.73131 | 0.64726 | 0.26316 | 0.77674 | 301.5 | 195.825 | 1048.625 | 2716.2 | 0 | 12258.2547 | 393.6769 | 1162.3611 | 19.9999 | 94.2936 | 47.2447 | 1.4142 | 3.1492 | 18631.888 | 0.68654 | -12741.7208
372 | C-SOK-TOU-CC-ET-HC-R60 | 35 | 2.625 | 453.7596 | 0.30757 | 0.73098 | 0.69128 | 0.27912 | 0.78169 | 301.025 | 207.375 | 1048.625 | 2673.875 | 0 | 11842.9483 | 396.3463 | 1162.3352 | 19.9517 | 93.1349 | 46.9991 | 1.4339 | 3.149 | 18644.8973 | 0.69214 | -12686.2961
373 | C-SOK-TOU-CC-ET-HC-R60 | 41 | 1.025 | 372.159 | 0.25226 | 0.73188 | 0.62877 | 0.2692 | 0.77694 | 298.2 | 191.275 | 1048.625 | 2920.9 | 0 | 12251.1778 | 387.7852 | 1162.3865 | 20.0043 | 95.1944 | 47.8152 | 1.4142 | 3.1493 | 18611.9498 | 0.6912 | -12790.2924
374 | C-SOK-TOU-CC-ET-HC-R60 | 41 | 2.05 | 400.1149 | 0.27121 | 0.73068 | 0.71122 | 0.30845 | 0.79512 | 296.825 | 210.85 | 1048.625 | 2836.875 | 0 | 11307.7033 | 388.5776 | 1162.3412 | 20.4812 | 92.9485 | 47.8342 | 1.4631 | 3.1501 | 18657.9127 | 0.70368 | -12676.9595
375 | C-SOK-TOU-CC-ET-HC-R60 | 41 | 3.075 | 414.0459 | 0.28065 | 0.73038 | 0.75251 | 0.32764 | 0.79939 | 297.05 | 222.6 | 1048.625 | 2796.425 | 0 | 10865.4081 | 390.735 | 1162.2892 | 20.4827 | 92.0654 | 47.6375 | 1.4907 | 3.1493 | 18672.2258 | 0.70694 | -12581.7578
376 | C-SOK-TOU-CC-FP-HC-R100 | 16.5 | 0.413 | 515.6582 | 0.34785 | 0.72796 | 0.1873 | 0.07624 | 0.59161 | 260.275 | 60.5 | 850.5 | 2341.05 | 0 | 23773.7847 | 428.6705 | 970.0666 | 17.3151 | 123.6812 | 56.5213 | 1.2131 | 3.1023 | 25577.6803 | 0.5923 | -9368.9143
377 | C-SOK-TOU-CC-FP-HC-R100 | 16.5 | 0.825 | 554.1809 | 0.37384 | 0.72777 | 0.18801 | 0.094007 | 0.63646 | 260.6 | 58.175 | 850.5 | 2300.15 | 0 | 23202.9706 | 431.2716 | 970.018 | 17.2779 | 121.1808 | 56.316 | 1.2339 | 3.1014 | 25623.5098 | 0.61853 | -9253.5811
378 | C-SOK-TOU-CC-FP-HC-R100 | 16.5 | 1.238 | 569.5329 | 0.38419 | 0.72777 | 0.19517 | 0.10265 | 0.64842 | 260.85 | 58.825 | 850.5 | 2289.15 | 0 | 22947.5538 | 431.8487 | 970.0785 | 17.2593 | 120.0357 | 56.2803 | 1.2431 | 3.1014 | 25638.0554 | 0.63061 | -9250.2543
379 | C-SOK-TOU-CC-FP-HC-R100 | 22.5 | 0.563 | 450.1533 | 0.30366 | 0.72722 | 0.2853 | 0.11539 | 0.63706 | 256.9 | 82.85 | 850.5 | 2499.475 | 0 | 22452.005 | 419.6364 | 970.1451 | 17.7915 | 120.1392 | 57.7112 | 1.2569 | 3.103 | 25643.5678 | 0.635 | -9094.4275
380 | C-SOK-TOU-CC-FP-HC-R100 | 22.5 | 1.125 | 487.0884 | 0.32858 | 0.72702 | 0.3045 | 0.14111 | 0.67015 | 257.2 | 85.325 | 850.5 | 2462.55 | 0 | 21707.9473 | 421.9517 | 970.0936 | 17.667 | 117.78 | 57.5223 | 1.2864 | 3.1019 | 25686.0722 | 0.65857 | -8997.6992
381 | C-SOK-TOU-CC-FP-HC-R100 | 22.5 | 1.688 | 500.503 | 0.33763 | 0.72664 | 0.32028 | 0.15157 | 0.67857 | 257.6 | 87.875 | 850.5 | 2465.3 | 0 | 21402.9941 | 421.3366 | 970.1112 | 17.6625 | 117.1467 | 57.6131 | 1.3014 | 3.1036 | 25693.5509 | 0.66898 | -8989.6718
382 | C-SOK-TOU-CC-FP-HC-R100 | 29 | 0.725 | 396.0051 | 0.26714 | 0.72658 | 0.35962 | 0.15523 | 0.66645 | 254.9 | 99.9 | 850.5 | 2642 | 0 | 21258.9219 | 415.1454 | 970.0352 | 18.0053 | 117.4255 | 58.3527 | 1.3012 | 3.1036 | 25692.5963 | 0.66845 | -8967.2114
383 | C-SOK-TOU-CC-FP-HC-R100 | 29 | 1.45 | 429.3406 | 0.28962 | 0.72665 | 0.38891 | 0.18489 | 0.69549 | 255.725 | 105.225 | 850.5 | 2622.375 | 0 | 20416.2584 | 417.513 | 970.1373 | 17.764 | 115.5762 | 58.1419 | 1.336 | 3.1043 | 25728.1569 | 0.68715 | -8827.2838
384 | C-SOK-TOU-CC-FP-HC-R100 | 29 | 2.175 | 444.0682 | 0.29956 | 0.72659 | 0.41185 | 0.19797 | 0.7063 | 256.025 | 110.125 | 850.5 | 2621 | 0 | 20017.4208 | 417.3154 | 970.0764 | 17.7124 | 114.9717 | 58.1736 | 1.3543 | 3.1036 | 25732.6858 | 0.69563 | -8760.6494
385 | C-SOK-TOU-CC-FP-HC-R10 | 35 | 0.875 | 359.055 | 0.24221 | 0.726 | 0.42569 | 0.1892 | 0.6877 | 252.575 | 113.575 | 850.5 | 2749.925 | 0 | 20247.1003 | 413.5329 | 970.0502 | 18.2047 | 114.9276 | 58.6173 | 1.3358 | 3.1055 | 25723.8096 | 0.69423 | -8907.4304
386 | C-SOK-TOU-CC-FP-HC-R10 | 35 | 1.75 | 388.7236 | 0.26222 | 0.72587 | 0.4659 | 0.22107 | 0.71478 | 252.75 | 122.15 | 850.5 | 2735.525 | 0 | 19331.0232 | 413.5771 | 970.1363 | 18.1081 | 113.8138 | 58.6874 | 1.3831 | 3.1049 | 25760.2235 | 0.71127 | -8779.8779
387 | C-SOK-TOU-CC-FP-HC-R10 | 35 | 2.625 | 403.5371 | 0.27222 | 0.7257 | 0.49311 | 0.2375 | 0.72395 | 253.4 | 128.3 | 850.5 | 2725.825 | 0 | 18857.3276 | 414.608 | 970.0681 | 17.9787 | 112.9605 | 58.5721 | 1.4028 | 3.1044 | 25765.8629 | 0.7191 | -8709.2025
388 | C-SOK-TOU-CC-FP-HC-R10 | 41 | 1.025 | 329.4165 | 0.22222 | 0.72611 | 0.46596 | 0.21924 | 0.70372 | 250.625 | 122.4 | 850.5 | 2842.075 | 0 | 19421.0712 | 415.052 | 970.1619 | 18.2054 | 113.1129 | 58.4857 | 1.3711 | 3.1068 | 25748.3085 | 0.70903 | -8803.0948
389 | C-SOK-TOU-CC-FP-HC-R10 | 41 | 2.05 | 356.8632 | 0.24073 | 0.72558 | 0.52123 | 0.2529 | 0.73285 | 250.75 | 133.125 | 850.5 | 2842.5 | 0 | 18408.2952 | 413.9262 | 970.117 | 18.189 | 112.0847 | 58.6978 | 1.4213 | 3.1073 | 25783.8563 | 0.72633 | -8673.1794
390 | C-SOK-TOU-CC-FP-HC-R10 | 41 | 3.075 | 369.61 | 0.24933 | 0.72518 | 0.54182 | 0.27242 | 0.73516 | 251.075 | 137.975 | 850.5 | 2842.475 | 0 | 17927.1977 | 414.5659 | 970.016 | 17.9975 | 111.5219 | 58.6359 | 1.4453 | 3.107 | 25792.2152 | 0.73365 | -8650.5501
391 | C-SOK-TOU-CC-FP-HC-R600 | 16.5 | 0.413 | 509.0193 | 0.34503 | 0.73572 | 0.16733 | 0.064138 | 0.63516 | 323.275 | 68.15 | 1048.625 | 2332.575 | 0 | 17509.5055 | 437.3781 | 1162.3215 | 17.6936 | 104.0141 | 42.5125 | 1.1964 | 3.1471 | 18318.7824 | 0.59177 | -13945.9396
392 | C-SOK-TOU-CC-FP-HC-R600 | 16.5 | 0.825 | 542.1415 | 0.36748 | 0.7357 | 0.16384 | 0.08133 | 0.68467 | 323.675 | 64.45 | 1048.625 | 2304.925 | 0 | 17054.5476 | 439.8099 | 1162.3403 | 17.6513 | 101.9969 | 42.4474 | 1.2154 | 3.1453 | 18391.0338 | 0.61429 | -13883.339
393 | C-SOK-TOU-CC-FP-HC-R600 | 16.5 | 1.238 | 554.2182 | 0.37566 | 0.73554 | 0.1642 | 0.087989 | 0.69887 | 324.425 | 62.775 | 1048.625 | 2303.175 | 0 | 16896.4266 | 441.8001 | 1162.3328 | 17.518 | 101.2263 | 42.3254 | 1.2209 | 3.145 | 18413.939 | 0.62076 | -13859.4013
394 | C-SOK-TOU-CC-FP-HC-R600 | 22.5 | 0.563 | 439.1369 | 0.29766 | 0.73488 | 0.25877 | 0.10488 | 0.68547 | 319.275 | 94.875 | 1048.625 | 2506.575 | 0 | 16363.0137 | 427.8378 | 1162.3393 | 18.0627 | 100.3009 | 43.5233 | 1.2393 | 3.1464 | 18412.5833 | 0.62893 | -13730.7881
395 | C-SOK-TOU-CC-FP-HC-R600 | 22.5 | 1.125 | 470.1668 | 0.31869 | 0.73445 | 0.27918 | 0.12855 | 0.72072 | 320.075 | 97.25 | 1048.625 | 2478.8 | 0 | 15800.6337 | 430.0101 | 1162.2749 | 17.9853 | 98.4885 | 43.4797 | 1.2658 | 3.1469 | 18485.2267 | 0.64773 | -13702.2625
396 | C-SOK-TOU-CC-FP-HC-R600 | 22.5 | 1.688 | 481.7655 | 0.32655 | 0.73415 | 0.29101 | 0.14138 | 0.72637 | 320.5 | 99.175 | 1048.625 | 2495.4 | 0 | 15561.2646 | 429.1835 | 1162.2091 | 17.9949 | 97.7451 | 43.5923 | 1.2772 | 3.1475 | 18504.6896 | 0.65621 | -13731.16
397 | C-SOK-TOU-CC-FP-HC-R600 | 29 | 0.725 | 381.0878 | 0.25831 | 0.73487 | 0.32187 | 0.14459 | 0.71852 | 316.925 | 112.875 | 1048.625 | 2664.05 | 0 | 15425.8641 | 424.4908 | 1162.3155 | 18.0771 | 97.9225 | 43.9643 | 1.2801 | 3.1467 | 18482.7551 | 0.65348 | -13603.8847
398 | C-SOK-TOU-CC-FP-HC-R600 | 29 | 1.45 | 409.6131 | 0.27765 | 0.7339 | 0.37422 | 0.17472 | 0.74314 | 317.25 | 123.05 | 1048.625 | 2657.325 | 0 | 14702.1858 | 425.2381 | 1162.3214 | 18.0045 | 95.947 | 44.0296 | 1.3119 | 3.1471 | 18547.2427 | 0.67483 | -13632.7153
399 | C-SOK-TOU-CC-FP-HC-R600 | 29 | 2.175 | 422.8387 | 0.28661 | 0.73374 | 0.39076 | 0.19335 | 0.74797 | 317.725 | 127.125 | 1048.625 | 2663.6 | 0 | 14370.5488 | 424.8701 | 1162.3798 | 17.9862 | 95.2026 | 44.0961 | 1.3291 | 3.1472 | 18563.4746 | 0.68219 | -13621.0748
400 | C-SOK-TOU-CC-FP-HC-R60 | 35 | 0.875 | 340.3621 | 0.23071 | 0.73387 | 0.38736 | 0.1782 | 0.73983 | 314.35 | 129.9 | 1048.625 | 2787.475 | 0 | 14617.2069 | 420.6229 | 1162.376 | 18.3415 | 95.7774 | 44.4093 | 1.3144 | 3.1483 | 18527.3592 | 0.67854 | -13623.0275
401 | C-SOK-TOU-CC-FP-HC-R60 | 35 | 1.75 | 366.3452 | 0.24832 | 0.73319 | 0.43888 | 0.21395 | 0.76004 | 314.525 | 141.425 | 1048.625 | 2784.95 | 0 | 13843.1605 | 421.198 | 1162.3135 | 18.2865 | 93.9249 | 44.4738 | 1.3494 | 3.1483 | 18584.4237 | 0.69552 | -13610.0319
402 | C-SOK-TOU-CC-FP-HC-R60 | 35 | 2.625 | 380.4139 | 0.25785 | 0.73309 | 0.46995 | 0.23439 | 0.76383 | 314.525 | 149.45 | 1048.625 | 2790.75 | 0 | 13433.2888 | 421.5409 | 1162.362 | 18.1799 | 93.3053 | 44.4808 | 1.3725 | 3.1486 | 18602.6653 | 0.70204 | -13581.3855
403 | C-SOK-TOU-CC-FP-HC-R60 | 41 | 1.025 | 310.5252 | 0.21048 | 0.73373 | 0.43267 | 0.2091 | 0.75624 | 312.6 | 142.7 | 1048.625 | 2885 | 0 | 13946.4469 | 422.4564 | 1162.4434 | 18.321 | 93.8863 | 44.3138 | 1.3426 | 3.1487 | 18561.6093 | 0.6904 | -13523.735
404 | C-SOK-TOU-CC-FP-HC-R60 | 41 | 2.05 | 335.1403 | 0.22717 | 0.73298 | 0.49836 | 0.24986 | 0.77429 | 312.125 | 157.175 | 1048.625 | 2893.6 | 0 | 13058.0453 | 421.4385 | 1162.4239 | 18.3274 | 92.1975 | 44.5077 | 1.3864 | 3.1492 | 18610.4749 | 0.70826 | -13504.0164
405 | C-SOK-TOU-CC-FP-HC-R60 | 41 | 3.075 | 347.1071 | 0.23528 | 0.7325 | 0.53794 | 0.27068 | 0.78128 | 312.375 | 166.35 | 1048.625 | 2892.025 | 0 | 12588.2244 | 420.6928 | 1162.2883 | 18.3514 | 91.3288 | 44.6055 | 1.411 | 3.1488 | 18625.6548 | 0.71803 | -13506.3819
406 | C-SOK-TOU-FC-ET-HC-OFF0 | 11.5 | 0.288 | 647.351 | 0.43879 | 0.65162 | 0.39562 | 0.22658 | 1 | 535 | 208.85 | 1821 | 2115.15 | 0 | 5587.0235 | 511.1846 | 1534.6756 | 10.6303 | 43.7241 | 12.625 | 1.1672 | 2.8027 | 2588.0754 | 0.39403 | 4511.1748
407 | C-SOK-TOU-FC-ET-HC-OFF0 | 11.5 | 0.575 | 667.3134 | 0.45232 | 0.65159 | 0.41035 | 0.2721 | 1 | 534.55 | 216.525 | 1821 | 2071.125 | 0 | 5381.1676 | 507.7647 | 1535.0294 | 10.7232 | 43.7114 | 12.7082 | 1.1952 | 2.8013 | 2588.0754 | 0.40892 | 4536.0035
408 | C-SOK-TOU-FC-ET-HC-OFF0 | 11.5 | 0.863 | 678.0421 | 0.45959 | 0.65159 | 0.42045 | 0.2967 | 1 | 534.625 | 221.325 | 1821 | 2049.5 | 0 | 5257.6874 | 507.1714 | 1535.1567 | 10.7266 | 43.7728 | 12.7232 | 1.2154 | 2.8011 | 2588.0754 | 0.41831 | 4535.7406
409 | C-SOK-TOU-FC-ET-HC-OFF0 | 15.5 | 0.388 | 575.744 | 0.39025 | 0.65274 | 0.55224 | 0.34876 | 1 | 518.275 | 277.05 | 1821 | 2298.275 | 0 | 4337.209 | 479.5456 | 1534.7828 | 11.2876 | 41.821 | 13.458 | 1.2689 | 2.8025 | 2588.0754 | 0.46762 | 4750.9382
410 | C-SOK-TOU-FC-ET-HC-OFF0 | 15.5 | 0.775 | 601.1327 | 0.40746 | 0.65297 | 0.58669 | 0.40985 | 1 | 515.375 | 292.05 | 1821 | 2238.575 | 0 | 3973.9272 | 477.3485 | 1534.761 | 11.347 | 41.8962 | 13.5191 | 1.3228 | 2.8022 | 2588.0754 | 0.48656 | 4783.9756
411 | C-SOK-TOU-FC-ET-HC-OFF0 | 15.5 | 1.163 | 611.5195 | 0.4145 | 0.65304 | 0.60214 | 0.42503 | 1 | 514.425 | 299.8 | 1821 | 2214.025 | 0 | 3842.7047 | 477.8949 | 1534.5732 | 11.3486 | 41.6097 | 13.5028 | 1.3365 | 2.8023 | 2588.0754 | 0.49201 | 4814.9763
412 | C-SOK-TOU-FC-ET-HC-OFF0 | 20 | 0.5 | 508.6566 | 0.34478 | 0.65371 | 0.67648 | 0.45834 | 1 | 503.325 | 330.5 | 1821 | 2484.85 | 0 | 3314.5087 | 448.0324 | 1534.4264 | 12.1913 | 40.4817 | 14.4027 | 1.3702 | 2.8026 | 2588.0754 | 0.50974 | 4987.48
413 | C-SOK-TOU-FC-ET-HC-OFF0 | 20 | 1 | 532.513 | 0.36095 | 0.65399 | 0.72088 | 0.52172 | 1 | 499.65 | 349.825 | 1821 | 2421.55 | 0 | 2887.5964 | 445.2839 | 1534.7738 | 12.3226 | 40.1538 | 14.4932 | 1.4339 | 2.8024 | 2588.0754 | 0.52686 | 5039.079
414 | C-SOK-TOU-FC-ET-HC-OFF0 | 20 | 1.5 | 543.7028 | 0.36854 | 0.65381 | 0.74418 | 0.54865 | 1 | 498.775 | 360.425 | 1821 | 2393.4 | 0 | 2680.6677 | 442.1377 | 1534.6362 | 12.4775 | 39.6428 | 14.5966 | 1.4581 | 2.8028 | 2588.0754 | 0.53521 | 5054.1631
415 | C-SOK-TOU-FC-ET-HC-OFF | 24 | 0.6 | 460.0241 | 0.31182 | 0.65397 | 0.73364 | 0.54606 | 1 | 498.45 | 359.875 | 1821 | 2630.525 | 0 | 2749.3414 | 432.6237 | 1534.5825 | 12.659 | 41.0062 | 14.9179 | 1.4443 | 2.803 | 2588.0754 | 0.52081 | 5290.5736
416 | C-SOK-TOU-FC-ET-HC-OFF | 24 | 1.2 | 479.3475 | 0.32491 | 0.65427 | 0.78812 | 0.61183 | 1 | 492.975 | 380.475 | 1821 | 2571.025 | 0 | 2256.3713 | 427.6881 | 1534.3831 | 12.8959 | 40.0835 | 15.089 | 1.5208 | 2.803 | 2588.0754 | 0.54236 | 5264.8482
417 | C-SOK-TOU-FC-ET-HC-OFF | 24 | 1.8 | 486.8432 | 0.33 | 0.65431 | 0.81681 | 0.6379 | 1 | 490.025 | 391.925 | 1821 | 2548.325 | 0 | 2019.3881 | 422.6877 | 1534.2594 | 13.1568 | 39.014 | 15.2682 | 1.5507 | 2.8035 | 2588.0754 | 0.55431 | 5207.6001
418 | C-SOK-TOU-FC-ET-HC-OFF | 28.5 | 0.713 | 406.9206 | 0.27582 | 0.65538 | 0.79035 | 0.63421 | 1 | 490.4 | 382.675 | 1821 | 2785.225 | 0 | 2183.3269 | 420.0685 | 1534.7207 | 12.9582 | 41.4176 | 15.3639 | 1.5276 | 2.8027 | 2588.0754 | 0.54352 | 5293.9148
419 | C-SOK-TOU-FC-ET-HC-OFF | 28.5 | 1.425 | 425.1033 | 0.28815 | 0.65553 | 0.848 | 0.70725 | 1 | 483.675 | 404.55 | 1821 | 2726.9 | 0 | 1653.7554 | 411.1988 | 1534.0621 | 13.4016 | 40.3665 | 15.6924 | 1.6264 | 2.8032 | 2588.0754 | 0.56372 | 5285.7122
420 | C-SOK-TOU-FC-ET-HC-OFF | 28.5 | 2.138 | 431.1338 | 0.29223 | 0.65533 | 0.87465 | 0.74099 | 1 | 481.075 | 416.675 | 1821 | 2707.2 | 0 | 1409.8004 | 402.9505 | 1534.5334 | 13.8197 | 39.5138 | 16.0165 | 1.67 | 2.8031 | 2588.0754 | 0.57598 | 5210.0882
421 | C-SOK-TOU-FC-ET-HC-R100 | 11.5 | 0.288 | 661.1862 | 0.44602 | 0.64973 | 0.20053 | 0.076097 | 0.60666 | 244.35 | 61.975 | 1024.225 | 2119.3 | 0 | 16191.8109 | 432.7198 | 822.0481 | 11.5968 | 88.6222 | 38.088 | 1.2233 | 2.8101 | 17259.9017 | 0.48813 | -1558.6932
422 | C-SOK-TOU-FC-ET-HC-R100 | 11.5 | 0.575 | 700.6488 | 0.47264 | 0.64825 | 0.21138 | 0.090875 | 0.64866 | 245.325 | 62.125 | 1024.225 | 2021.425 | 0 | 15826.4407 | 433.5944 | 821.6717 | 11.8603 | 87.2438 | 38.0721 | 1.2425 | 2.8128 | 17284.6912 | 0.50993 | -1391.479
423 | C-SOK-TOU-FC-ET-HC-R100 | 11.5 | 0.863 | 714.8137 | 0.4822 | 0.64844 | 0.23433 | 0.097778 | 0.65507 | 244.45 | 65.6 | 1024.225 | 1988.925 | 0 | 15648.0901 | 433.5315 | 822.0129 | 11.9305 | 86.5557 | 38.0834 | 1.2513 | 2.8103 | 17288.4573 | 0.52178 | -1391.9764
424 | C-SOK-TOU-FC-ET-HC-R100 | 15.5 | 0.388 | 587.7514 | 0.39648 | 0.65024 | 0.33809 | 0.12281 | 0.64952 | 237.875 | 90.075 | 1024.225 | 2307.025 | 0 | 15044.4839 | 410.0404 | 821.6904 | 12.4091 | 86.9957 | 39.968 | 1.2789 | 2.8111 | 17290.5534 | 0.53643 | -1122.7418
425 | C-SOK-TOU-FC-ET-HC-R100 | 15.5 | 0.775 | 625.8051 | 0.42215 | 0.64969 | 0.37748 | 0.14344 | 0.68318 | 237.925 | 94.675 | 1024.225 | 2208.125 | 0 | 14545.9727 | 412.181 | 822.081 | 12.5692 | 85.4025 | 39.8344 | 1.3021 | 2.81 | 17311.8618 | 0.55769 | -967.4158
426 | C-SOK-TOU-FC-ET-HC-R100 | 15.5 | 1.163 | 641.9723 | 0.43306 | 0.64899 | 0.41792 | 0.1515 | 0.69247 | 238.075 | 101.75 | 1024.225 | 2164.3 | 0 | 14298.127 | 413.991 | 822.0339 | 12.5169 | 84.732 | 39.6886 | 1.3154 | 2.8119 | 17313.0418 | 0.56912 | -938.812
427 | C-SOK-TOU-FC-ET-HC-R100 | 20 | 0.5 | 524.294 | 0.35368 | 0.6505 | 0.45563 | 0.17125 | 0.68271 | 232.8 | 113.5 | 1024.225 | 2480.65 | 0 | 13956.8295 | 389.79 | 821.7776 | 13.481 | 86.0164 | 41.7894 | 1.3308 | 2.8121 | 17309.684 | 0.57162 | -764.3051
428 | C-SOK-TOU-FC-ET-HC-R100 | 20 | 1 | 560.8744 | 0.37835 | 0.64966 | 0.51361 | 0.19689 | 0.71361 | 232.725 | 122.55 | 1024.225 | 2377.8 | 0 | 13349.7461 | 391.8039 | 821.6622 | 13.6426 | 84.6517 | 41.6592 | 1.3653 | 2.8121 | 17334.564 | 0.59094 | -593.1511
429 | C-SOK-TOU-FC-ET-HC-R100 | 20 | 1.5 | 574.6167 | 0.38762 | 0.6493 | 0.54568 | 0.20906 | 0.71923 | 232.15 | 127.8 | 1024.225 | 2336.55 | 0 | 13079.2859 | 391.5738 | 821.8251 | 13.7829 | 84.0684 | 41.6885 | 1.3824 | 2.8115 | 17338.2942 | 0.6008 | -579.2242
430 | C-SOK-TOU-FC-ET-HC-R10 | 24 | 0.6 | 481.1809 | 0.32459 | 0.65088 | 0.51644 | 0.20997 | 0.70633 | 231.3 | 127.3 | 1024.225 | 2606.375 | 0 | 13184.0415 | 379.8899 | 822.013 | 13.9809 | 85.9115 | 42.7534 | 1.3731 | 2.8118 | 17324.8349 | 0.58719 | -426.5746
431 | C-SOK-TOU-FC-ET-HC-R10 | 24 | 1.2 | 512.8257 | 0.34594 | 0.65043 | 0.58104 | 0.23951 | 0.73049 | 230.3 | 137 | 1024.225 | 2512.925 | 0 | 12528.4126 | 381.8647 | 821.9971 | 14.0335 | 84.8956 | 42.6201 | 1.418 | 2.8117 | 17349.6998 | 0.60639 | -298.1086
432 | C-SOK-TOU-FC-ET-HC-R10 | 24 | 1.8 | 525.9695 | 0.35481 | 0.64983 | 0.62167 | 0.25467 | 0.73333 | 229.225 | 143.825 | 1024.225 | 2474.575 | 0 | 12203.9949 | 380.9805 | 821.7949 | 14.2721 | 84.1401 | 42.7104 | 1.4361 | 2.8117 | 17352.9326 | 0.61731 | -306.1744
433 | C-SOK-TOU-FC-ET-HC-R10 | 28.5 | 0.713 | 435.2479 | 0.29361 | 0.65337 | 0.56605 | 0.25117 | 0.72505 | 226.35 | 135.275 | 1024.225 | 2737.65 | 0 | 12419.3988 | 375.6039 | 821.9659 | 13.8018 | 85.9659 | 43.2011 | 1.4188 | 2.8117 | 17339.2607 | 0.60863 | -292.6307
434 | C-SOK-TOU-FC-ET-HC-R10 | 28.5 | 1.425 | 462.7736 | 0.31218 | 0.65247 | 0.63876 | 0.28233 | 0.74749 | 225.2 | 146.7 | 1024.225 | 2655.8 | 0 | 11725.3305 | 374.926 | 821.9636 | 14.1021 | 85.0377 | 43.3115 | 1.4689 | 2.8109 | 17359.1442 | 0.62678 | -172.1026
435 | C-SOK-TOU-FC-ET-HC-R10 | 28.5 | 2.138 | 476.5635 | 0.32148 | 0.65163 | 0.68008 | 0.30064 | 0.75036 | 225.625 | 155.225 | 1024.225 | 2612.225 | 0 | 11356.0853 | 373.0832 | 821.6928 | 14.5015 | 84.2962 | 43.4985 | 1.4912 | 2.8118 | 17361.561 | 0.63623 | -146.8309
436 | C-SOK-TOU-FC-ET-HC-R600 | 11.5 | 0.288 | 657.0842 | 0.44539 | 0.65729 | 0.18332 | 0.063116 | 0.65504 | 288 | 67.475 | 1166.025 | 2114.025 | 0 | 11698.8637 | 431.8173 | 930.304 | 11.9371 | 72.8105 | 28.706 | 1.2129 | 2.8418 | 12172.0354 | 0.48641 | -3178.0817
437 | C-SOK-TOU-FC-ET-HC-R600 | 11.5 | 0.575 | 696.2835 | 0.47196 | 0.65648 | 0.19267 | 0.075125 | 0.70415 | 289.25 | 67.875 | 1166.025 | 2016.8 | 0 | 11395.4468 | 432.7425 | 930.2174 | 12.1933 | 71.6062 | 28.7523 | 1.2278 | 2.8425 | 12221.4049 | 0.50363 | -2978.4285
438 | C-SOK-TOU-FC-ET-HC-R600 | 11.5 | 0.863 | 709.902 | 0.48119 | 0.65604 | 0.20106 | 0.0803 | 0.71315 | 290 | 69.025 | 1166.025 | 1985.025 | 0 | 11295.9997 | 434.3058 | 930.1954 | 12.2067 | 71.0929 | 28.6916 | 1.231 | 2.8426 | 12236.0754 | 0.5082 | -2927.8715
439 | C-SOK-TOU-FC-ET-HC-R600 | 15.5 | 0.388 | 580.0552 | 0.39318 | 0.65825 | 0.3147 | 0.11473 | 0.70555 | 280.375 | 99.475 | 1166.025 | 2310.875 | 0 | 10668.3556 | 408.412 | 929.9766 | 12.7199 | 70.4085 | 30.2439 | 1.2667 | 2.8441 | 12228.2816 | 0.52929 | -2727.3963
440 | C-SOK-TOU-FC-ET-HC-R600 | 15.5 | 0.775 | 615.1619 | 0.41697 | 0.65762 | 0.35338 | 0.13282 | 0.73309 | 281.2 | 105.9 | 1166.025 | 2217.275 | 0 | 10299.9309 | 410.5408 | 930.1109 | 12.8656 | 69.2605 | 30.2016 | 1.2879 | 2.8441 | 12272.1625 | 0.54271 | -2565.292
441 | C-SOK-TOU-FC-ET-HC-R600 | 15.5 | 1.163 | 630.157 | 0.42714 | 0.65707 | 0.38306 | 0.1423 | 0.73905 | 281.125 | 110.85 | 1166.025 | 2176.725 | 0 | 10105.6638 | 411.8652 | 930.0441 | 12.8746 | 68.6243 | 30.1323 | 1.2989 | 2.8435 | 12279.7515 | 0.55063 | -2525.4643
442 | C-SOK-TOU-FC-ET-HC-R600 | 20 | 0.5 | 511.7334 | 0.34687 | 0.65866 | 0.42827 | 0.16789 | 0.73657 | 274.4 | 126.35 | 1166.025 | 2494.875 | 0 | 9751.2765 | 386.389 | 930.103 | 13.7695 | 69.1364 | 31.7966 | 1.3207 | 2.8435 | 12264.01 | 0.55786 | -2372.4043
443 | C-SOK-TOU-FC-ET-HC-R600 | 20 | 1 | 543.99 | 0.36873 | 0.65805 | 0.49195 | 0.19384 | 0.75802 | 274.225 | 137.975 | 1166.025 | 2404.975 | 0 | 9256.3516 | 387.7426 | 930.1188 | 13.9704 | 67.8011 | 31.7701 | 1.3514 | 2.8431 | 12295.3192 | 0.57338 | -2223.1004
444 | C-SOK-TOU-FC-ET-HC-R600 | 20 | 1.5 | 558.8234 | 0.37879 | 0.65753 | 0.52735 | 0.20881 | 0.76303 | 274.4 | 146.025 | 1166.025 | 2361.35 | 0 | 9002.6482 | 389.8741 | 930.2453 | 13.9378 | 67.048 | 31.6397 | 1.3659 | 2.8432 | 12303.2286 | 0.58185 | -2184.3419
445 | C-SOK-TOU-FC-ET-HC-R60 | 24 | 0.6 | 465.451 | 0.3155 | 0.65901 | 0.49167 | 0.21245 | 0.75707 | 272.275 | 142.575 | 1166.025 | 2631.325 | 0 | 9102.6464 | 377.1723 | 930.0361 | 14.1031 | 68.778 | 32.504 | 1.3645 | 2.8438 | 12284.1534 | 0.57082 | -2055.2529
446 | C-SOK-TOU-FC-ET-HC-R60 | 24 | 1.2 | 494.548 | 0.33522 | 0.65823 | 0.56701 | 0.24563 | 0.77635 | 271.55 | 157.55 | 1166.025 | 2544.35 | 0 | 8517.6576 | 378.4798 | 930.0189 | 14.2952 | 67.3093 | 32.4648 | 1.4024 | 2.8439 | 12309.2159 | 0.58896 | -1935.1478
447 | C-SOK-TOU-FC-ET-HC-R60 | 24 | 1.8 | 508.7551 | 0.34485 | 0.65767 | 0.61434 | 0.25991 | 0.78349 | 271.25 | 166.85 | 1166.025 | 2503 | 0 | 8222.4932 | 380.0809 | 929.8979 | 14.3413 | 66.3903 | 32.368 | 1.4194 | 2.8447 | 12317.7279 | 0.59764 | -1886.3013
448 | C-SOK-TOU-FC-ET-HC-R60 | 28.5 | 0.713 | 418.5088 | 0.28368 | 0.66085 | 0.53923 | 0.25979 | 0.77516 | 268.75 | 153.45 | 1166.025 | 2766.8 | 0 | 8487.097 | 374.9491 | 930.0558 | 13.7913 | 68.7307 | 32.7078 | 1.4108 | 2.8442 | 12301.2611 | 0.58695 | -1878.7398
449 | C-SOK-TOU-FC-ET-HC-R60 | 28.5 | 1.425 | 445.2006 | 0.30177 | 0.66013 | 0.63183 | 0.29678 | 0.79716 | 266.3 | 170.95 | 1166.025 | 2686.675 | 0 | 7803.381 | 373.707 | 929.9906 | 14.2182 | 66.9308 | 32.8513 | 1.4548 | 2.8439 | 12324.0612 | 0.60767 | -1776.1394
450 | C-SOK-TOU-FC-ET-HC-R60 | 28.5 | 2.138 | 457.6179 | 0.31019 | 0.65981 | 0.67213 | 0.31737 | 0.80256 | 265.55 | 179.55 | 1166.025 | 2650.475 | 0 | 7485.3631 | 371.9077 | 929.8987 | 14.497 | 66.4486 | 33.0075 | 1.4845 | 2.8449 | 12332.8193 | 0.61641 | -1743.7832
451 | C-SOK-TOU-FC-FP-HC-OFF0 | 11.5 | 0.288 | 467.0325 | 0.31657 | 0.65128 | 0.21294 | 0.14083 | 1 | 546.85 | 129.4 | 1821 | 2628.875 | 0 | 6893.8162 | 508.9753 | 1534.911 | 10.5692 | 47.5032 | 12.6777 | 1.0939 | 2.8014 | 2588.0754 | 0.30312 | 3742.838
452 | C-SOK-TOU-FC-FP-HC-OFF0 | 11.5 | 0.575 | 480.4293 | 0.32565 | 0.65121 | 0.21092 | 0.20173 | 1 | 547.175 | 128.4 | 1821 | 2651.975 | 0 | 6750.2122 | 502.6353 | 1535.1401 | 10.6822 | 47.7024 | 12.84 | 1.1268 | 2.8019 | 2588.0754 | 0.32112 | 3750.7905
453 | C-SOK-TOU-FC-FP-HC-OFF0 | 11.5 | 0.863 | 487.1883 | 0.33023 | 0.6513 | 0.21244 | 0.2329 | 1 | 547.275 | 129.7 | 1821 | 2665.675 | 0 | 6659.5504 | 500.8471 | 1535.2466 | 10.6855 | 47.7698 | 12.8854 | 1.1443 | 2.8015 | 2588.0754 | 0.33263 | 3739.0243
454 | C-SOK-TOU-FC-FP-HC-OFF0 | 15.5 | 0.388 | 412.8586 | 0.27985 | 0.65198 | 0.31875 | 0.23884 | 1 | 537.275 | 178.85 | 1821 | 2774.95 | 0 | 6008.9287 | 487.8943 | 1534.7696 | 10.8667 | 46.3041 | 13.2274 | 1.1639 | 2.8024 | 2588.0754 | 0.39191 | 3891.3338
455 | C-SOK-TOU-FC-FP-HC-OFF0 | 15.5 | 0.775 | 431.4608 | 0.29246 | 0.65206 | 0.33465 | 0.31222 | 1 | 536.325 | 186.8 | 1821 | 2779.975 | 0 | 5723.3631 | 482.9915 | 1535.0684 | 10.918 | 46.8613 | 13.3597 | 1.2108 | 2.8011 | 2588.0754 | 0.4174 | 3896.2536
456 | C-SOK-TOU-FC-FP-HC-OFF0 | 15.5 | 1.163 | 440.6216 | 0.29866 | 0.6521 | 0.34259 | 0.3455 | 1 | 536.05 | 190.35 | 1821 | 2776.6 | 0 | 5590.4013 | 482.6542 | 1534.6706 | 10.8944 | 47.1398 | 13.3699 | 1.2331 | 2.8022 | 2588.0754 | 0.42823 | 3904.9478
457 | C-SOK-TOU-FC-FP-HC-OFF0 | 20 | 0.5 | 366.8219 | 0.24864 | 0.6527 | 0.41686 | 0.32772 | 1 | 527.975 | 223.65 | 1821 | 2903.9 | 0 | 5193.5223 | 470.1078 | 1534.6048 | 11.2016 | 45.6136 | 13.728 | 1.23 | 2.8028 | 2588.0754 | 0.45213 | 4019.4345
458 | C-SOK-TOU-FC-FP-HC-OFF0 | 20 | 1 | 387.9151 | 0.26294 | 0.6528 | 0.44708 | 0.41104 | 1 | 525.95 | 238.975 | 1821 | 2886.15 | 0 | 4797.8744 | 465.9967 | 1534.5478 | 11.2345 | 46.6527 | 13.8478 | 1.2995 | 2.8025 | 2588.0754 | 0.4783 | 4047.544
459 | C-SOK-TOU-FC-FP-HC-OFF0 | 20 | 1.5 | 399.8635 | 0.27104 | 0.6528 | 0.46989 | 0.44657 | 1 | 525.475 | 248.9 | 1821 | 2875.6 | 0 | 4571.5237 | 465.929 | 1534.8077 | 11.2005 | 46.8185 | 13.8516 | 1.3295 | 2.8026 | 2588.0754 | 0.49247 | 4058.8549
460 | C-SOK-TOU-FC-FP-HC-OFF | 24 | 0.6 | 332.5499 | 0.22541 | 0.65289 | 0.47122 | 0.39161 | 1 | 524.275 | 252.225 | 1821 | 3001.025 | 0 | 4705.3707 | 458.871 | 1534.2612 | 11.4559 | 45.9701 | 14.0644 | 1.2842 | 2.8036 | 2588.0754 | 0.47656 | 4177.6589
461 | C-SOK-TOU-FC-FP-HC-OFF | 24 | 1.2 | 356.4106 | 0.24158 | 0.65302 | 0.52624 | 0.48501 | 1 | 520.675 | 276.575 | 1821 | 2968.85 | 0 | 4137.4193 | 452.6472 | 1534.5449 | 11.5622 | 46.6829 | 14.2581 | 1.3688 | 2.8031 | 2588.0754 | 0.51094 | 4183.333
462 | C-SOK-TOU-FC-FP-HC-OFF | 24 | 0.8 | 342.9426 | 0.23246 | 0.65309 | 0.49292 | 0.43774 | 1 | 522.5 | 261.825 | 1821 | 2986.2 | 0 | 4456.5641 | 456.4951 | 1535.0211 | 11.4811 | 46.4615 | 14.1375 | 1.3239 | 2.802 | 2588.0754 | 0.49212 | 4180.1566
463 | C-SOK-TOU-FC-FP-HC-OFF | 28.5 | 0.713 | 297.8871 | 0.20192 | 0.65358 | 0.51946 | 0.46128 | 1 | 521.4 | 276.75 | 1821 | 3112.775 | 0 | 4236.5452 | 454.1471 | 1534.7805 | 11.4616 | 46.5996 | 14.211 | 1.3388 | 2.8026 | 2588.0754 | 0.50253 | 4223.4537
464 | C-SOK-TOU-FC-FP-HC-OFF | 28.5 | 1.425 | 321.0779 | 0.21764 | 0.65378 | 0.58551 | 0.56044 | 1 | 516.275 | 303.15 | 1821 | 3072.375 | 0 | 3588.4577 | 446.4921 | 1534.4032 | 11.627 | 47.4099 | 14.4543 | 1.4385 | 2.8033 | 2588.0754 | 0.53684 | 4238.2703
465 | C-SOK-TOU-FC-FP-HC-OFF | 28.5 | 2.138 | 331.4404 | 0.22466 | 0.65362 | 0.61735 | 0.60075 | 1 | 514.425 | 315.875 | 1821 | 3067.4 | 0 | 3296.2197 | 442.8571 | 1534.5694 | 11.7049 | 47.5749 | 14.5724 | 1.474 | 2.8028 | 2588.0754 | 0.5511 | 4240.3649
466 | C-SOK-TOU-FC-FP-HC-R100 | 11.5 | 0.288 | 560.3185 | 0.37798 | 0.64885 | 0.1038 | 0.061504 | 0.57559 | 248.5 | 41.825 | 1024.225 | 2240.25 | 0 | 16751.3486 | 441.2825 | 822.0347 | 11.2521 | 89.3223 | 37.396 | 1.2031 | 2.8121 | 17234.0921 | 0.48601 | -2207.4073
467 | C-SOK-TOU-FC-FP-HC-R100 | 11.5 | 0.575 | 595.9978 | 0.40205 | 0.64799 | 0.096882 | 0.078378 | 0.62601 | 249.325 | 39.5 | 1024.225 | 2213.925 | 0 | 16370.5151 | 438.9152 | 821.9517 | 11.4737 | 87.8603 | 37.6125 | 1.2248 | 2.8093 | 17256.7517 | 0.51585 | -2059.4684
468 | C-SOK-TOU-FC-FP-HC-R100 | 11.5 | 0.863 | 609.0733 | 0.41087 | 0.64773 | 0.10324 | 0.086227 | 0.64028 | 249.15 | 37.85 | 1024.225 | 2215.6 | 0 | 16199.0847 | 438.0127 | 822.0282 | 11.5188 | 87.099 | 37.6918 | 1.2325 | 2.8094 | 17262.4354 | 0.53029 | -2046.2015
469 | C-SOK-TOU-FC-FP-HC-R100 | 15.5 | 0.388 | 494.4571 | 0.33355 | 0.64879 | 0.20748 | 0.10068 | 0.62804 | 244.05 | 63.3 | 1024.225 | 2393.3 | 0 | 15766.1019 | 425.7658 | 821.761 | 11.7119 | 86.7986 | 38.6422 | 1.2468 | 2.8113 | 17267.3763 | 0.54129 | -1871.2687
470 | C-SOK-TOU-FC-FP-HC-R100 | 15.5 | 0.775 | 529.6204 | 0.35727 | 0.64859 | 0.2198 | 0.12496 | 0.66404 | 244.875 | 64.2 | 1024.225 | 2358.875 | 0 | 15279.8653 | 424.7553 | 821.8833 | 11.845 | 85.3868 | 38.7605 | 1.2748 | 2.8107 | 17286.3395 | 0.56699 | -1733.4814
471 | C-SOK-TOU-FC-FP-HC-R100 | 15.5 | 1.163 | 541.1634 | 0.36506 | 0.64805 | 0.22445 | 0.13391 | 0.67494 | 245.525 | 64.85 | 1024.225 | 2363.7 | 0 | 15109.1021 | 422.8685 | 821.757 | 11.941 | 85.124 | 38.9198 | 1.2881 | 2.811 | 17291.1943 | 0.57607 | -1700.6949
472 | C-SOK-TOU-FC-FP-HC-R100 | 20 | 0.5 | 438.1419 | 0.29556 | 0.64938 | 0.28646 | 0.14234 | 0.65985 | 240.275 | 79.175 | 1024.225 | 2532.975 | 0 | 14879.5456 | 411.8633 | 821.8916 | 12.3309 | 85.3093 | 39.8196 | 1.2914 | 2.8113 | 17291.8692 | 0.57718 | -1606.1852
473 | C-SOK-TOU-FC-FP-HC-R100 | 20 | 1 | 470.5526 | 0.31742 | 0.64904 | 0.32091 | 0.17039 | 0.69235 | 240.9 | 84.2 | 1024.225 | 2508.025 | 0 | 14293.4883 | 412.1265 | 821.8085 | 12.2727 | 84.2384 | 39.8321 | 1.3275 | 2.8115 | 17308.4813 | 0.60158 | -1470.5962
474 | C-SOK-TOU-FC-FP-HC-R100 | 20 | 1.5 | 483.4437 | 0.32612 | 0.64845 | 0.34741 | 0.18273 | 0.7044 | 240.95 | 89.1 | 1024.225 | 2519.85 | 0 | 14012.3676 | 409.2976 | 822.1115 | 12.4051 | 83.7636 | 40.0735 | 1.3432 | 2.809 | 17311.0573 | 0.61503 | -1458.5699
475 | C-SOK-TOU-FC-FP-HC-R10 | 24 | 0.6 | 399.3613 | 0.2694 | 0.64942 | 0.33099 | 0.17418 | 0.68119 | 239.5 | 89.9 | 1024.225 | 2635.725 | 0 | 14252.9784 | 404.9971 | 821.716 | 12.6523 | 84.6177 | 40.4328 | 1.3248 | 2.8116 | 17307.3208 | 0.59461 | -1372.6348
476 | C-SOK-TOU-FC-FP-HC-R10 | 24 | 1.2 | 430.491 | 0.2904 | 0.64837 | 0.37945 | 0.20675 | 0.71039 | 240.525 | 99 | 1024.225 | 2619.825 | 0 | 13581.8878 | 403.5089 | 821.8735 | 12.7004 | 83.6987 | 40.6012 | 1.3672 | 2.8126 | 17325.0707 | 0.61885 | -1241.7136
477 | C-SOK-TOU-FC-FP-HC-R10 | 24 | 1.8 | 442.2001 | 0.2983 | 0.64826 | 0.41771 | 0.22315 | 0.72119 | 238.3 | 103.35 | 1024.225 | 2627.15 | 0 | 13216.7002 | 399.462 | 822.0905 | 12.8823 | 83.3035 | 40.9593 | 1.3932 | 2.8101 | 17328.176 | 0.63707 | -1293.7374
478 | C-SOK-TOU-FC-FP-HC-R10 | 28.5 | 0.713 | 362.4938 | 0.24453 | 0.64999 | 0.39218 | 0.20842 | 0.7001 | 237.6 | 102.1 | 1024.225 | 2736.975 | 0 | 13556.3963 | 399.0449 | 821.7833 | 12.9185 | 83.7696 | 40.9791 | 1.3636 | 2.813 | 17319.3527 | 0.62017 | -1284.1924
479 | C-SOK-TOU-FC-FP-HC-R10 | 28.5 | 1.425 | 390.0867 | 0.26314 | 0.64968 | 0.4299 | 0.24389 | 0.73045 | 237.25 | 108 | 1024.225 | 2734.625 | 0 | 12866.0462 | 399.2864 | 821.589 | 12.7165 | 83.3126 | 40.9986 | 1.4137 | 2.8127 | 17339.084 | 0.64018 | -1127.3904
480 | C-SOK-TOU-FC-FP-HC-R10 | 28.5 | 2.138 | 403.3831 | 0.27211 | 0.6495 | 0.46988 | 0.26346 | 0.73423 | 236.625 | 116.225 | 1024.225 | 2735.05 | 0 | 12478.9235 | 397.5758 | 821.6874 | 12.7797 | 82.8339 | 41.1562 | 1.4378 | 2.8121 | 17342.0052 | 0.65306 | -1129.6679
481 | C-SOK-TOU-FC-FP-HC-R600 | 11.5 | 0.288 | 552.1859 | 0.37429 | 0.65667 | 0.099257 | 0.045263 | 0.61477 | 292.175 | 46.4 | 1166.025 | 2246.075 | 0 | 12260.8185 | 440.3675 | 930.1759 | 11.595 | 74.5294 | 28.1421 | 1.1919 | 2.8426 | 12131.9915 | 0.48454 | -3869.8698
482 | C-SOK-TOU-FC-FP-HC-R600 | 11.5 | 0.575 | 583.449 | 0.39548 | 0.65587 | 0.088029 | 0.060211 | 0.67606 | 293.725 | 41.95 | 1166.025 | 2221.15 | 0 | 11950.688 | 438.42 | 930.2825 | 11.7952 | 73.2101 | 28.3241 | 1.2091 | 2.8415 | 12169.3959 | 0.51084 | -3689.8385
483 | C-SOK-TOU-FC-FP-HC-R600 | 11.5 | 0.863 | 594.7384 | 0.40313 | 0.65557 | 0.086772 | 0.065809 | 0.69304 | 294.4 | 40.2 | 1166.025 | 2224.625 | 0 | 11847.0368 | 437.857 | 930.2656 | 11.8413 | 72.783 | 28.3815 | 1.2148 | 2.8412 | 12182.6387 | 0.51839 | -3634.7917
484 | C-SOK-TOU-FC-FP-HC-R600 | 15.5 | 0.388 | 482.8798 | 0.32731 | 0.6572 | 0.1893 | 0.086559 | 0.67448 | 287.325 | 69.1 | 1166.025 | 2399.875 | 0 | 11416.0609 | 423.7508 | 930.106 | 12.1113 | 71.7286 | 29.2091 | 1.2345 | 2.8439 | 12185.6678 | 0.53094 | -3496.3566
485 | C-SOK-TOU-FC-FP-HC-R600 | 15.5 | 0.775 | 511.8117 | 0.34692 | 0.65655 | 0.20084 | 0.10898 | 0.71575 | 288.55 | 68.85 | 1166.025 | 2382.325 | 0 | 11043.4695 | 423.8664 | 930.2683 | 12.1248 | 70.5687 | 29.2759 | 1.2583 | 2.8418 | 12222.8796 | 0.55277 | -3361.5782
486 | C-SOK-TOU-FC-FP-HC-R600 | 15.5 | 1.163 | 522.8543 | 0.3544 | 0.65602 | 0.20862 | 0.11827 | 0.72881 | 289.325 | 70.25 | 1166.025 | 2388.55 | 0 | 10895.1554 | 422.955 | 930.2877 | 12.1582 | 70.2115 | 29.3564 | 1.2692 | 2.8412 | 12235.8496 | 0.56126 | -3324.357
487 | C-SOK-TOU-FC-FP-HC-R600 | 20 | 0.5 | 423.5901 | 0.28712 | 0.65774 | 0.2694 | 0.12967 | 0.71259 | 283.2 | 88.45 | 1166.025 | 2545.475 | 0 | 10662.6193 | 411.048 | 930.1409 | 12.5591 | 69.9588 | 30.0672 | 1.2768 | 2.8437 | 12223.6543 | 0.56217 | -3214.1948
488 | C-SOK-TOU-FC-FP-HC-R600 | 20 | 1 | 451.4021 | 0.30597 | 0.65687 | 0.30459 | 0.15916 | 0.74364 | 284.075 | 93.875 | 1166.025 | 2534.525 | 0 | 10195.3157 | 410.8875 | 930.111 | 12.5551 | 68.8272 | 30.1563 | 1.3074 | 2.8428 | 12262.0446 | 0.58389 | -3109.1803
489 | C-SOK-TOU-FC-FP-HC-R600 | 20 | 1.5 | 460.093 | 0.31186 | 0.6563 | 0.3143 | 0.17212 | 0.7516 | 284.5 | 94.75 | 1166.025 | 2562.225 | 0 | 10029.0917 | 408.9556 | 930.0357 | 12.5849 | 68.6092 | 30.2974 | 1.3207 | 2.8425 | 12271.1617 | 0.59215 | -3096.4628
490 | C-SOK-TOU-FC-FP-HC-R60 | 24 | 0.6 | 382.6212 | 0.25935 | 0.65747 | 0.32031 | 0.16312 | 0.73637 | 281.925 | 101.7 | 1166.025 | 2659.6 | 0 | 10135.9495 | 403.3813 | 930.0039 | 12.8443 | 69.1646 | 30.6104 | 1.3112 | 2.8433 | 12248.5702 | 0.57873 | -3003.3578
491 | C-SOK-TOU-FC-FP-HC-R60 | 24 | 1.2 | 407.5889 | 0.27627 | 0.65711 | 0.36868 | 0.20054 | 0.75987 | 281.5 | 110.1 | 1166.025 | 2669.275 | 0 | 9588.871 | 401.0955 | 930.2069 | 12.9144 | 68.0832 | 30.8387 | 1.3484 | 2.8438 | 12284.2005 | 0.60317 | -2956.5401
492 | C-SOK-TOU-FC-FP-HC-R60 | 24 | 1.8 | 419.3348 | 0.28424 | 0.65669 | 0.39873 | 0.21622 | 0.76724 | 281.55 | 117.025 | 1166.025 | 2682.725 | 0 | 9336.5707 | 400.2894 | 930.2007 | 12.9017 | 67.6564 | 30.9106 | 1.3654 | 2.8436 | 12292.9743 | 0.6124 | -2922.6089
493 | C-SOK-TOU-FC-FP-HC-R60 | 28.5 | 0.713 | 343.6528 | 0.23294 | 0.65836 | 0.37399 | 0.19839 | 0.75583 | 279.45 | 114.425 | 1166.025 | 2779.55 | 0 | 9598.425 | 399.6081 | 930.1808 | 12.8754 | 68.234 | 30.9098 | 1.3438 | 2.8428 | 12272.1743 | 0.59949 | -2911.509
494 | C-SOK-TOU-FC-FP-HC-R60 | 28.5 | 1.425 | 366.8074 | 0.24863 | 0.6576 | 0.42563 | 0.24181 | 0.77619 | 279.3 | 123.425 | 1166.025 | 2795.425 | 0 | 9001.6897 | 396.1294 | 930.0651 | 12.9856 | 67.4022 | 31.2044 | 1.3885 | 2.8434 | 12300.5476 | 0.62181 | -2846.353
495 | C-SOK-TOU-FC-FP-HC-R60 | 28.5 | 2.138 | 380.3046 | 0.25778 | 0.65737 | 0.46079 | 0.26258 | 0.78468 | 279.375 | 133.2 | 1166.025 | 2791.025 | 0 | 8686.0562 | 399.2934 | 929.965 | 12.7294 | 66.9171 | 31.0097 | 1.4118 | 2.8445 | 12308.1948 | 0.62975 | -2765.4268
496 | C-SOK-TOU-FC-FP-WC-OFF0 | 18 | 0.45 | 418.1981 | 0.28347 | 0.59143 | 0.26596 | 0.21903 | 1 | 1117.925 | 310.925 | 1821 | 2793.1 | 20.1604 | 10791.4564 | 771.761 | 2375.5064 | 9.4947 | 68.118 | 13.2348 | 1.0342 | 2.7551 | 4097.4792 | 0.48463 | 3879.5091
497 | C-SOK-TOU-FC-FP-WC-OFF0 | 18 | 0.9 | 430.8897 | 0.29207 | 0.59117 | 0.26488 | 0.27629 | 1 | 1119.3 | 312.575 | 1821 | 2805.1 | 20.1643 | 10571.4575 | 767.9943 | 2375.6175 | 9.5241 | 68.091 | 13.2998 | 1.0619 | 2.755 | 4097.4792 | 0.49931 | 3883.3212
498 | C-SOK-TOU-FC-FP-WC-OFF0 | 18 | 1.35 | 438.2849 | 0.29708 | 0.59084 | 0.26595 | 0.30455 | 1 | 1120.625 | 315.275 | 1821 | 2806.9 | 20.1713 | 10448.6869 | 766.4895 | 2375.6257 | 9.5318 | 68.2384 | 13.3258 | 1.0794 | 2.755 | 4097.4792 | 0.50717 | 3887.9603
499 | C-SOK-TOU-FC-FP-WC-OFF0 | 24.5 | 0.6 | 370.5445 | 0.25116 | 0.58818 | 0.35387 | 0.30964 | 1 | 1120.025 | 404.6 | 1821 | 2928.55 | 20.2077 | 9547.8985 | 765.5784 | 2375.5007 | 9.4928 | 67.7245 | 13.3416 | 1.1005 | 2.7551 | 4097.4792 | 0.54511 | 4129.674
500 | C-SOK-TOU-FC-FP-WC-OFF0 | 24.5 | 1.25 | 385.8433 | 0.26153 | 0.58752 | 0.36254 | 0.38087 | 1 | 1121.625 | 415.6 | 1821 | 2919.85 | 20.215 | 9172.5687 | 761.71 | 2375.5506 | 9.5126 | 68.3859 | 13.4084 | 1.1429 | 2.7547 | 4097.4792 | 0.56431 | 4118.6381
501 | C-SOK-TOU-FC-FP-WC-OFF0 | 24.5 | 1.85 | 393.9603 | 0.26704 | 0.58708 | 0.36812 | 0.4128 | 1 | 1123.425 | 422.8 | 1821 | 2914.5 | 20.2265 | 8990.425 | 760.1055 | 2375.1051 | 9.5211 | 68.9272 | 13.439 | 1.1682 | 2.756 | 4097.4792 | 0.57266 | 4124.7109
502 | C-SOK-TOU-FC-FP-WC-OFF0 | 31 | 0.8 | 320.8268 | 0.21746 | 0.58766 | 0.42491 | 0.38713 | 1 | 1108.95 | 467.075 | 1821 | 3072.425 | 20.1971 | 8497.3522 | 757.0208 | 2375.8302 | 9.5119 | 67.2827 | 13.493 | 1.1619 | 2.7549 | 4097.4792 | 0.6042 | 3936.4356
503 | C-SOK-TOU-FC-FP-WC-OFF0 | 31 | 1.55 | 338.6919 | 0.22957 | 0.58679 | 0.44274 | 0.46412 | 1 | 1111.225 | 491.025 | 1821 | 3042.975 | 20.212 | 8004.8207 | 754.3374 | 2375.8305 | 9.5227 | 68.4541 | 13.541 | 1.2193 | 2.7549 | 4097.4792 | 0.6207 | 3982.4109
504 | C-SOK-TOU-FC-FP-WC-OFF0 | 31 | 2.35 | 347.0007 | 0.23521 | 0.58611 | 0.45544 | 0.49643 | 1 | 1113.525 | 508.525 | 1821 | 3036.35 | 20.2246 | 7746.5665 | 752.4557 | 2375.7152 | 9.5281 | 69.0415 | 13.5746 | 1.2488 | 2.755 | 4097.4792 | 0.63096 | 3969.8134
505 | C-SOK-TOU-FC-FP-WC-OFF | 38 | 0.95 | 282.7944 | 0.19169 | 0.58636 | 0.48015 | 0.44788 | 1 | 1105.55 | 519.9 | 1821 | 3194.125 | 20.2126 | 7684.2651 | 756.0229 | 2375.9582 | 9.4774 | 67.0401 | 13.509 | 1.2108 | 2.7541 | 4097.4792 | 0.63679 | 3903.1049
506 | C-SOK-TOU-FC-FP-WC-OFF | 38 | 1.9 | 305.1298 | 0.20683 | 0.58526 | 0.51739 | 0.54253 | 1 | 1107.825 | 566.55 | 1821 | 3152.3 | 20.2287 | 6917.2215 | 752.7906 | 2375.5903 | 9.4872 | 68.6811 | 13.5666 | 1.2979 | 2.7544 | 4097.4792 | 0.65797 | 3965.8191
507 | C-SOK-TOU-FC-FP-WC-OFF | 38 | 2.85 | 315.1168 | 0.21359 | 0.58481 | 0.53573 | 0.57147 | 1 | 1108.975 | 593.525 | 1821 | 3145.575 | 20.2386 | 6611.1918 | 752.3308 | 2375.4935 | 9.4841 | 69.2004 | 13.5755 | 1.3245 | 2.7548 | 4097.4792 | 0.66342 | 4030.3017
508 | C-SOK-TOU-FC-FP-WC-OFF | 44.5 | 1.1 | 257.1055 | 0.17427 | 0.58605 | 0.5262 | 0.5086 | 1 | 1097.975 | 557.125 | 1821 | 3283.95 | 20.2137 | 6958.998 | 754.3278 | 2375.852 | 9.4759 | 66.9403 | 13.5415 | 1.2645 | 2.755 | 4097.4792 | 0.66222 | 3864.6522
509 | C-SOK-TOU-FC-FP-WC-OFF | 44.5 | 2.25 | 281.9355 | 0.1911 | 0.58432 | 0.58386 | 0.60679 | 1 | 1102.225 | 631.65 | 1821 | 3234.05 | 20.2312 | 5966.6338 | 752.1587 | 2375.0675 | 9.4728 | 68.2336 | 13.5784 | 1.364 | 2.7552 | 4097.4792 | 0.68524 | 3949.0111
510 | C-SOK-TOU-FC-FP-WC-OFF | 44.5 | 3.35 | 291.3654 | 0.1975 | 0.58302 | 0.60407 | 0.63948 | 1 | 1104.775 | 665.2 | 1821 | 3225 | 20.2623 | 5630.5235 | 751.2642 | 2375.3657 | 9.4727 | 69.0953 | 13.5949 | 1.405 | 2.755 | 4097.4792 | 0.69082 | 4008.7838
511 | C-SOK-TOU-FC-FP-WC-R100 | 18 | 0.45 | 509.0434 | 0.34339 | 0.55928 | 0.16769 | 0.082642 | 0.60045 | 572.925 | 106.125 | 1024.225 | 2353.05 | 9.1263 | 25993.7929 | 579.0456 | 1194.3615 | 9.4333 | 128.9219 | 45.7127 | 1.1646 | 2.7623 | 26748.6411 | 0.61254 | -10495.9751
512 | C-SOK-TOU-FC-FP-WC-R100 | 18 | 0.9 | 546.0848 | 0.36838 | 0.55977 | 0.16737 | 0.10168 | 0.64251 | 572.025 | 107.1 | 1024.225 | 2311.525 | 9.1253 | 25383.7678 | 580.9457 | 1194.2071 | 9.4519 | 126.2242 | 45.6471 | 1.1841 | 2.763 | 26792.7629 | 0.63716 | -10391.6284
513 | C-SOK-TOU-FC-FP-WC-R100 | 18 | 1.35 | 561.627 | 0.37886 | 0.55944 | 0.1734 | 0.11123 | 0.65225 | 572.125 | 112.875 | 1024.225 | 2301.575 | 9.1292 | 25104.6534 | 581.1305 | 1194.2672 | 9.4426 | 125.2742 | 45.6533 | 1.1965 | 2.7631 | 26805.031 | 0.64867 | -10391.2346
514 | C-SOK-TOU-FC-FP-WC-R100 | 24.5 | 0.6 | 445.8793 | 0.30078 | 0.55804 | 0.2485 | 0.12238 | 0.64134 | 569.175 | 147 | 1024.225 | 2507.45 | 9.1313 | 24563.9464 | 574.4015 | 1194.2879 | 9.4347 | 125.4794 | 46.1425 | 1.2087 | 2.7634 | 26810.5331 | 0.65146 | -10205.842
515 | C-SOK-TOU-FC-FP-WC-R100 | 24.5 | 1.25 | 481.8752 | 0.32506 | 0.55833 | 0.25866 | 0.14947 | 0.67477 | 568.5 | 155.325 | 1024.225 | 2475.725 | 9.129 | 23767.5128 | 574.5283 | 1194.2736 | 9.4623 | 123.2411 | 46.1989 | 1.2397 | 2.7629 | 26853.0246 | 0.67356 | -10106.6238
516 | C-SOK-TOU-FC-FP-WC-R100 | 24.5 | 1.85 | 493.4303 | 0.33286 | 0.55734 | 0.26789 | 0.16044 | 0.68298 | 570.025 | 161.9 | 1024.225 | 2474.775 | 9.1404 | 23450.901 | 574.1492 | 1194.3622 | 9.4531 | 122.4411 | 46.2356 | 1.2528 | 2.7633 | 26858.3291 | 0.68523 | -10127.8246
517 | C-SOK-TOU-FC-FP-WC-R100 | 31 | 0.8 | 397.3053 | 0.26801 | 0.56151 | 0.31351 | 0.1618 | 0.67144 | 557 | 173.45 | 1024.225 | 2636.625 | 9.0899 | 23233.2902 | 568.7086 | 1194.1831 | 9.5468 | 122.4933 | 46.634 | 1.2536 | 2.7639 | 26859.3598 | 0.68741 | -10144.8123
518 | C-SOK-TOU-FC-FP-WC-R100 | 31 | 1.55 | 427.2291 | 0.2882 | 0.56248 | 0.3358 | 0.19006 | 0.69735 | 554.1 | 187.625 | 1024.225 | 2621.5 | 9.0808 | 22382.1204 | 566.8476 | 1194.2442 | 9.6046 | 120.8595 | 46.8197 | 1.2875 | 2.7637 | 26890.0029 | 0.7052 | -10041.3939
519 | C-SOK-TOU-FC-FP-WC-R100 | 31 | 2.35 | 441.3395 | 0.29772 | 0.56102 | 0.35747 | 0.20387 | 0.70859 | 556.225 | 202.05 | 1024.225 | 2625.15 | 9.0967 | 21930.4314 | 565.6624 | 1194.5146 | 9.5928 | 120.447 | 46.9204 | 1.3099 | 2.7638 | 26897.2145 | 0.71723 | -10038.7357
520 | C-SOK-TOU-FC-FP-WC-R10 | 38 | 0.95 | 355.4999 | 0.23981 | 0.56052 | 0.36228 | 0.19672 | 0.69109 | 555.2 | 196.825 | 1024.225 | 2753.85 | 9.1023 | 22153.3658 | 570.0908 | 1194.3064 | 9.5298 | 119.8558 | 46.5824 | 1.2887 | 2.7644 | 26890.1397 | 0.70968 | -10056.3433
521 | C-SOK-TOU-FC-FP-WC-R10 | 38 | 1.9 | 385.4778 | 0.26003 | 0.56054 | 0.4065 | 0.2302 | 0.71928 | 553.025 | 223.95 | 1024.225 | 2739.25 | 9.0987 | 21076.1962 | 566.9851 | 1194.408 | 9.5857 | 118.7182 | 46.8703 | 1.3408 | 2.7643 | 26927.4228 | 0.73058 | -9987.316
522 | C-SOK-TOU-FC-FP-WC-R10 | 38 | 2.85 | 399.7368 | 0.26965 | 0.56041 | 0.42883 | 0.24838 | 0.7257 | 551.825 | 237.45 | 1024.225 | 2730.675 | 9.0996 | 20541.75 | 566.1245 | 1194.4144 | 9.6124 | 117.6497 | 46.9456 | 1.3594 | 2.7642 | 26934.6841 | 0.74025 | -9974.4322
523 | C-SOK-TOU-FC-FP-WC-R10 | 44.5 | 1.1 | 325.4272 | 0.21953 | 0.55881 | 0.41047 | 0.22581 | 0.7072 | 554.8 | 220.4 | 1024.225 | 2848.45 | 9.1087 | 21219.0011 | 572.3757 | 1194.1936 | 9.5126 | 117.6278 | 46.4512 | 1.3248 | 2.7642 | 26913.4801 | 0.72912 | -10035.7811
524 | C-SOK-TOU-FC-FP-WC-R10 | 44.5 | 2.25 | 354.088 | 0.23886 | 0.55963 | 0.46459 | 0.2627 | 0.73601 | 550.2 | 252.825 | 1024.225 | 2848.925 | 9.0984 | 20010.5301 | 567.4551 | 1194.2273 | 9.6101 | 116.5376 | 46.8732 | 1.3803 | 2.7636 | 26952.4828 | 0.74876 | -9955.5003
525 | C-SOK-TOU-FC-FP-WC-R10 | 44.5 | 3.35 | 368.3971 | 0.24851 | 0.56095 | 0.50048 | 0.28072 | 0.73836 | 544.95 | 272.725 | 1024.225 | 2844.625 | 9.0889 | 19429.1464 | 564.8975 | 1194.3046 | 9.6785 | 116.0427 | 47.0782 | 1.408 | 2.764 | 26961.2951 | 0.75505 | -9909.8535
526 | C-SOK-TOU-FC-FP-WC-R600 | 18 | 0.45 | 497.4978 | 0.33722 | 0.56153 | 0.15422 | 0.073479 | 0.6494 | 696.025 | 118.75 | 1166.025 | 2355.2 | 11.1105 | 19050.9764 | 615.5925 | 1380.6115 | 9.3529 | 106.7166 | 32.1484 | 1.1351 | 2.7969 | 18566.0384 | 0.60829 | -14308.8905
527 | C-SOK-TOU-FC-FP-WC-R600 | 18 | 0.9 | 527.1285 | 0.3573 | 0.5615 | 0.14894 | 0.0917 | 0.69465 | 696.85 | 116.175 | 1166.025 | 2335.15 | 11.1136 | 18617.4461 | 617.4628 | 1380.6546 | 9.3516 | 104.8428 | 32.165 | 1.1517 | 2.7968 | 18637.5152 | 0.62735 | -14260.2474
528 | C-SOK-TOU-FC-FP-WC-R600 | 18 | 1.35 | 538.0633 | 0.36471 | 0.5617 | 0.1499 | 0.09945 | 0.70589 | 696.175 | 118.825 | 1166.025 | 2336.25 | 11.1122 | 18452.5678 | 617.5013 | 1380.7896 | 9.359 | 104.1678 | 32.1945 | 1.1586 | 2.7966 | 18658.7319 | 0.63363 | -14252.5953
529 | C-SOK-TOU-FC-FP-WC-R600 | 24.5 | 0.6 | 430.4404 | 0.29176 | 0.56084 | 0.22591 | 0.11528 | 0.69405 | 692.1 | 162.625 | 1166.025 | 2520.275 | 11.1146 | 17867.9243 | 610.9597 | 1380.7874 | 9.3492 | 103.4706 | 32.4995 | 1.1774 | 2.7974 | 18653.4852 | 0.63789 | -14031.618
530 | C-SOK-TOU-FC-FP-WC-R600 | 24.5 | 1.25 | 459.8021 | 0.31167 | 0.56054 | 0.23924 | 0.14187 | 0.72679 | 691.85 | 175.325 | 1166.025 | 2510.4 | 11.1158 | 17278.9933 | 611.1514 | 1380.6506 | 9.3515 | 101.8558 | 32.5941 | 1.2044 | 2.797 | 18724.5628 | 0.65588 | -14015.5654
531 | C-SOK-TOU-FC-FP-WC-R600 | 24.5 | 1.85 | 469.6086 | 0.31831 | 0.56054 | 0.2434 | 0.15598 | 0.73237 | 692 | 181.175 | 1166.025 | 2522.4 | 11.1226 | 17043.8945 | 609.9694 | 1380.6148 | 9.3604 | 101.2503 | 32.6784 | 1.2169 | 2.7976 | 18742.4365 | 0.66426 | -14054.1163
532 | C-SOK-TOU-FC-FP-WC-R600 | 31 | 0.8 | 377.2576 | 0.25572 | 0.56242 | 0.28033 | 0.15606 | 0.72545 | 681.35 | 192.175 | 1166.025 | 2670.8 | 11.0712 | 16836.7176 | 605.9653 | 1380.7923 | 9.3831 | 101.0143 | 32.8359 | 1.2188 | 2.7932 | 18722.0668 | 0.66705 | -13998.0203
533 | C-SOK-TOU-FC-FP-WC-R600 | 31 | 1.55 | 401.3259 | 0.27203 | 0.56273 | 0.3135 | 0.1864 | 0.74665 | 679.3 | 215.025 | 1166.025 | 2676.875 | 11.0853 | 16142.4089 | 602.8559 | 1380.8072 | 9.4418 | 99.5423 | 33.0805 | 1.2505 | 2.7975 | 18778.2856 | 0.68785 | -14064.9807
534 | C-SOK-TOU-FC-FP-WC-R600 | 31 | 2.35 | 414.4635 | 0.28093 | 0.56272 | 0.33093 | 0.20416 | 0.75241 | 678.55 | 229.65 | 1166.025 | 2676.25 | 11.081 | 15775.9389 | 602.4427 | 1380.8329 | 9.439 | 98.7372 | 33.1207 | 1.267 | 2.796 | 18793.1988 | 0.6955 | -14050.0003
535 | C-SOK-TOU-FC-FP-WC-R60 | 38 | 0.95 | 333.7207 | 0.22621 | 0.56219 | 0.34337 | 0.192 | 0.74598 | 676.15 | 226.975 | 1166.025 | 2802.1 | 11.0826 | 15896.4118 | 604.3893 | 1380.699 | 9.4091 | 98.7026 | 32.9833 | 1.2558 | 2.7979 | 18763.7432 | 0.69353 | -14020.1956
536 | C-SOK-TOU-FC-FP-WC-R60 | 38 | 1.9 | 358.8187 | 0.24322 | 0.56144 | 0.38436 | 0.22965 | 0.76552 | 676.3 | 260.15 | 1166.025 | 2810.55 | 11.0955 | 15066.9511 | 602.0362 | 1380.8309 | 9.4349 | 97.2917 | 33.1751 | 1.2945 | 2.7976 | 18814.1218 | 0.71014 | -14000.3458
537 | C-SOK-TOU-FC-FP-WC-R60 | 38 | 2.85 | 371.0941 | 0.25154 | 0.56228 | 0.41046 | 0.25052 | 0.77036 | 672.8 | 277.325 | 1166.025 | 2815.7 | 11.088 | 14609.5405 | 599.3492 | 1380.7502 | 9.471 | 96.7496 | 33.3319 | 1.3203 | 2.7975 | 18829.6475 | 0.71951 | -14017.7987
538 | C-SOK-TOU-FC-FP-WC-R60 | 44.5 | 1.1 | 302.8788 | 0.2053 | 0.56069 | 0.38761 | 0.22373 | 0.76085 | 676.175 | 255.05 | 1166.025 | 2906.675 | 11.094 | 15152.2947 | 606.28 | 1380.8382 | 9.3934 | 96.6001 | 32.938 | 1.2847 | 2.7976 | 18795.636 | 0.7113 | -14030.4607
539 | C-SOK-TOU-FC-FP-WC-R60 | 44.5 | 2.25 | 328.7441 | 0.22283 | 0.56127 | 0.44683 | 0.26827 | 0.77964 | 671 | 298.35 | 1166.025 | 2908.05 | 11.0922 | 14116.6882 | 602.2057 | 1380.7986 | 9.4596 | 95.1722 | 33.2037 | 1.3383 | 2.7976 | 18838.9402 | 0.72866 | -13979.0028
540 | C-SOK-TOU-FC-FP-WC-R60 | 44.5 | 3.35 | 341.0787 | 0.23119 | 0.56139 | 0.47778 | 0.29067 | 0.78785 | 668.8 | 319.85 | 1166.025 | 2903.175 | 11.0933 | 13594.9346 | 600.2079 | 1380.8731 | 9.4938 | 94.4456 | 33.323 | 1.366 | 2.7973 | 18852.1988 | 0.73745 | -13957.2393
541 | C-SOK-TOU-CC-FP-WC-R600 | 23 | 0.6 | 475.5551 | 0.32234 | 0.69574 | 0.20762 | 0.082094 | 0.65006 | 565.025 | 124.725 | 1048.625 | 2410.875 | 12.6943 | 24109.2551 | 588.9494 | 1580.3835 | 13.5928 | 135.473 | 45.1136 | 1.168 | 3.1161 | 25192.2346 | 0.66852 | -29603.4113
542 | C-SOK-TOU-CC-FP-WC-R600 | 23 | 1.15 | 503.7796 | 0.34148 | 0.69625 | 0.20307 | 0.099745 | 0.68591 | 563.975 | 126.625 | 1048.625 | 2384.825 | 12.6929 | 23591.1691 | 591.4818 | 1580.4711 | 13.6032 | 132.9136 | 45.0743 | 1.1845 | 3.1166 | 25279.7527 | 0.68304 | -29722.1511
543 | C-SOK-TOU-CC-FP-WC-R600 | 23 | 1.75 | 515.4272 | 0.34937 | 0.69557 | 0.20577 | 0.10912 | 0.69328 | 565.375 | 131.8 | 1048.625 | 2395.65 | 12.7039 | 23365.0913 | 591.9009 | 1580.3898 | 13.5874 | 131.7192 | 45.0883 | 1.191 | 3.1169 | 25307.6682 | 0.68957 | -29794.8758
544 | C-SOK-TOU-CC-FP-WC-R600 | 32 | 0.8 | 398.7401 | 0.27028 | 0.69384 | 0.28051 | 0.12475 | 0.69085 | 562.8 | 165.775 | 1048.625 | 2603.825 | 12.6997 | 22639.1627 | 588.9393 | 1580.2435 | 13.5065 | 130.4233 | 45.2931 | 1.2123 | 3.1137 | 25313.1451 | 0.69865 | -29672.9403
545 | C-SOK-TOU-CC-FP-WC-R600 | 32 | 1.6 | 426.4351 | 0.28905 | 0.69484 | 0.30869 | 0.14872 | 0.71606 | 559.525 | 183.2 | 1048.625 | 2604.6 | 12.7057 | 21870.6223 | 589.0272 | 1580.4242 | 13.5251 | 128.0918 | 45.4258 | 1.2387 | 3.1165 | 25399.4369 | 0.71574 | -29867.1845
546 | C-SOK-TOU-CC-FP-WC-R600 | 32 | 2.4 | 439.7435 | 0.29807 | 0.69463 | 0.32428 | 0.16473 | 0.71886 | 559.05 | 193.95 | 1048.625 | 2601.225 | 12.708 | 21466.1188 | 588.9251 | 1580.3247 | 13.5137 | 126.7453 | 45.4568 | 1.2542 | 3.1158 | 25416.4819 | 0.72403 | -29922.9929
547 | C-SOK-TOU-CC-FP-WC-R600 | 40.5 | 1 | 348.4218 | 0.23617 | 0.69269 | 0.35458 | 0.16147 | 0.71448 | 558.225 | 201.5 | 1048.625 | 2756.9 | 12.7082 | 21369.6065 | 590.0089 | 1580.3919 | 13.4938 | 126.0816 | 45.33 | 1.2504 | 3.1157 | 25382.5378 | 0.72769 | -29835.3103
548 | C-SOK-TOU-CC-FP-WC-R600 | 40.5 | 2.05 | 375.8527 | 0.25476 | 0.692 | 0.39371 | 0.1936 | 0.73503 | 557.425 | 226.45 | 1048.625 | 2753.125 | 12.7274 | 20417.5067 | 589.8057 | 1580.3401 | 13.5096 | 123.6861 | 45.4659 | 1.2859 | 3.1164 | 25461.5165 | 0.74281 | -29986.6812
549 | C-SOK-TOU-CC-FP-WC-R600 | 40.5 | 3.05 | 391.4814 | 0.26536 | 0.69129 | 0.42321 | 0.21349 | 0.73841 | 558.1 | 246.975 | 1048.625 | 2748.875 | 12.7379 | 19853.1372 | 590.1943 | 1580.3667 | 13.477 | 122.3813 | 45.4625 | 1.3077 | 3.116 | 25477.4908 | 0.75011 | -29990.156
550 | C-SOK-TOU-CC-FP-WC-R60 | 49 | 1.25 | 312.9959 | 0.21216 | 0.69035 | 0.4229 | 0.19578 | 0.73572 | 555.725 | 235.9 | 1048.625 | 2875.625 | 12.7347 | 20195.6073 | 593.9618 | 1580.5279 | 13.4982 | 121.8719 | 45.1525 | 1.2887 | 3.118 | 25440.9516 | 0.75163 | -29990.879
551 | C-SOK-TOU-CC-FP-WC-R60 | 49 | 2.45 | 338.6536 | 0.22955 | 0.68911 | 0.48154 | 0.23202 | 0.75152 | 555.6 | 274.3 | 1048.625 | 2871.9 | 12.749 | 19070.5257 | 594.3399 | 1580.3483 | 13.4685 | 119.2848 | 45.2077 | 1.3291 | 3.1169 | 25496.556 | 0.76633 | -30068.7203
552 | C-SOK-TOU-CC-FP-WC-R60 | 49 | 3.7 | 353.5886 | 0.23967 | 0.68722 | 0.52081 | 0.25696 | 0.75383 | 558.225 | 297.95 | 1048.625 | 2872.45 | 12.7826 | 18365.4916 | 594.079 | 1580.4806 | 13.4379 | 117.9338 | 45.2539 | 1.3589 | 3.1177 | 25513.795 | 0.77676 | -30142.3422
553 | C-SOK-TOU-CC-FP-WC-R60 | 58 | 1.45 | 282.8205 | 0.1917 | 0.68789 | 0.47173 | 0.22675 | 0.75027 | 555.825 | 264.6 | 1048.625 | 2986.9 | 12.7544 | 19240.2017 | 602.6277 | 1580.5216 | 13.445 | 117.6422 | 44.6223 | 1.3187 | 3.1179 | 25478.2416 | 0.76461 | -30008.3967
554 | C-SOK-TOU-CC-FP-WC-R60 | 58 | 2.9 | 307.781 | 0.20862 | 0.68509 | 0.54344 | 0.27033 | 0.76661 | 558.575 | 311.35 | 1048.625 | 2980.65 | 12.7968 | 17898.981 | 603.1166 | 1580.4929 | 13.3994 | 114.9193 | 44.6657 | 1.3721 | 3.1184 | 25528.3771 | 0.78204 | -30094.2404
555 | C-SOK-TOU-CC-FP-WC-R60 | 58 | 4.35 | 321.9854 | 0.21825 | 0.68259 | 0.58974 | 0.29631 | 0.7722 | 561.5 | 339.375 | 1048.625 | 2972.825 | 12.8167 | 17101.7752 | 604.0595 | 1580.3625 | 13.3205 | 113.4985 | 44.6168 | 1.4062 | 3.1165 | 25540.8375 | 0.79189 | -30115.8987
556 | C-SOK-TOU-FC-ET-WC-OFF0 | 18 | 0.45 | 551.2265 | 0.37364 | 0.58783 | 0.39987 | 0.28595 | 1 | 1118.375 | 453.05 | 1821 | 2184.55 | 20.2266 | 9171.3938 | 787.6377 | 2375.7429 | 9.397 | 64.4412 | 12.9692 | 1.1034 | 2.7553 | 4097.4792 | 0.5375 | 4589.0017
557 | C-SOK-TOU-FC-ET-WC-OFF0 | 18 | 0.9 | 565.914 | 0.38359 | 0.58712 | 0.40555 | 0.33308 | 1 | 1121.125 | 462.15 | 1821 | 2148.75 | 20.2401 | 8926.129 | 787.3016 | 2375.4177 | 9.3947 | 64.4082 | 12.9741 | 1.131 | 2.7554 | 4097.4792 | 0.54877 | 4596.4156
558 | C-SOK-TOU-FC-ET-WC-OFF0 | 18 | 1.35 | 575.2565 | 0.38992 | 0.58688 | 0.41205 | 0.35364 | 1 | 1121.775 | 470.375 | 1821 | 2128.5 | 20.2426 | 8776.4513 | 787.2446 | 2375.2654 | 9.3916 | 64.4978 | 12.9747 | 1.1503 | 2.7555 | 4097.4792 | 0.55469 | 4610.9961
559 | C-SOK-TOU-FC-ET-WC-OFF0 | 24.5 | 0.6 | 492.499 | 0.33383 | 0.58403 | 0.5131 | 0.39283 | 1 | 1117.375 | 574.3 | 1821 | 2341.35 | 20.2878 | 7587.9076 | 780.1488 | 2375.4042 | 9.4382 | 63.8886 | 13.0935 | 1.195 | 2.7556 | 4097.4792 | 0.57881 | 5082.1986
560 | C-SOK-TOU-FC-ET-WC-OFF0 | 24.5 | 1.25 | 508.6889 | 0.3448 | 0.58232 | 0.54015 | 0.45325 | 1 | 1121.225 | 603.975 | 1821 | 2294.775 | 20.3139 | 7071.2695 | 778.8892 | 2375.647 | 9.4184 | 63.9384 | 13.1149 | 1.2465 | 2.7554 | 4097.4792 | 0.60434 | 4931.1145
561 | C-SOK-TOU-FC-ET-WC-OFF0 | 24.5 | 1.85 | 515.583 | 0.34948 | 0.5816 | 0.55015 | 0.46573 | 1 | 1123.325 | 616.675 | 1821 | 2275.85 | 20.3202 | 6920.3581 | 779.5936 | 2375.7839 | 9.4086 | 63.7024 | 13.1021 | 1.2559 | 2.7549 | 4097.4792 | 0.60912 | 4937.4503
562 | C-SOK-TOU-FC-ET-WC-OFF0 | 31 | 0.8 | 430.0353 | 0.29149 | 0.58347 | 0.60646 | 0.491 | 1 | 1101.6 | 658.525 | 1821 | 2507 | 20.2701 | 6211.562 | 770.0297 | 2375.5721 | 9.4825 | 63.2012 | 13.2654 | 1.2896 | 2.7553 | 4097.4792 | 0.62787 | 4960.8956
563 | C-SOK-TOU-FC-ET-WC-OFF0 | 31 | 1.55 | 446.3523 | 0.30255 | 0.58121 | 0.63821 | 0.54334 | 1 | 1107.325 | 695.2 | 1821 | 2459.1 | 20.3091 | 5679.2191 | 770.0394 | 2375.5598 | 9.4626 | 63.1885 | 13.2656 | 1.3426 | 2.7555 | 4097.4792 | 0.64638 | 4893.0528
564 | C-SOK-TOU-FC-ET-WC-OFF0 | 31 | 2.35 | 457.3396 | 0.31 | 0.58037 | 0.66563 | 0.56832 | 1 | 1106.625 | 727.05 | 1821 | 2428.4 | 20.3099 | 5292.5694 | 769.3437 | 2375.4907 | 9.4674 | 62.3914 | 13.276 | 1.3702 | 2.755 | 4097.4792 | 0.65904 | 4833.9948
565 | C-SOK-TOU-FC-ET-WC-OFF | 38 | 0.95 | 374.8912 | 0.25411 | 0.58391 | 0.68558 | 0.57307 | 1 | 1081.7 | 721.475 | 1821 | 2673.175 | 20.237 | 5042.951 | 760.7455 | 2375.3309 | 9.5438 | 62.0062 | 13.4263 | 1.3715 | 2.7553 | 4097.4792 | 0.66894 | 4716.2235
566 | C-SOK-TOU-FC-ET-WC-OFF | 38 | 1.9 | 394.1564 | 0.26717 | 0.5814 | 0.73104 | 0.63559 | 1 | 1087.775 | 778.925 | 1821 | 2612.275 | 20.2801 | 4323.1326 | 761.7244 | 2375.7494 | 9.5206 | 61.6762 | 13.4102 | 1.4471 | 2.7552 | 4097.4792 | 0.68742 | 4681.7667
567 | C-SOK-TOU-FC-ET-WC-OFF | 38 | 2.85 | 407.316 | 0.27609 | 0.57944 | 0.7664 | 0.66207 | 1 | 1093.65 | 828.95 | 1821 | 2577.675 | 20.3114 | 3850.9539 | 762.5369 | 2375.2906 | 9.519 | 60.5356 | 13.3961 | 1.4942 | 2.7558 | 4097.4792 | 0.69804 | 4673.7141
568 | C-SOK-TOU-FC-ET-WC-OFF | 44.5 | 1.1 | 338.0184 | 0.22912 | 0.58307 | 0.74236 | 0.64397 | 1 | 1071.125 | 769.35 | 1821 | 2791.425 | 20.2306 | 4161.6915 | 755.7161 | 2374.9975 | 9.589 | 61.3754 | 13.516 | 1.4501 | 2.7558 | 4097.4792 | 0.69317 | 4615.3403
569 | C-SOK-TOU-FC-ET-WC-OFF | 44.5 | 2.25 | 359.8517 | 0.24392 | 0.57977 | 0.80347 | 0.71746 | 1 | 1079.45 | 853.95 | 1821 | 2725.425 | 20.2881 | 3231.1494 | 757.1503 | 2375.3378 | 9.5652 | 60.5126 | 13.4902 | 1.5575 | 2.7553 | 4097.4792 | 0.71293 | 4597.0068
570 | C-SOK-TOU-FC-ET-WC-OFF | 44.5 | 3.35 | 368.8978 | 0.25005 | 0.58017 | 0.82547 | 0.74911 | 1 | 1074.75 | 879.025 | 1821 | 2696 | 20.2704 | 2867.7119 | 755.8722 | 2375.3811 | 9.5902 | 60.2961 | 13.5116 | 1.6025 | 2.7548 | 4097.4792 | 0.71703 | 4645.181
571 | C-SOK-TOU-FC-ET-WC-R100 | 18 | 0.45 | 521.6137 | 0.35187 | 0.55999 | 0.19157 | 0.072554 | 0.60672 | 570.9 | 120 | 1024.225 | 2099.125 | 9.1214 | 26070.3914 | 590.4464 | 1194.2938 | 9.3894 | 129.504 | 44.9561 | 1.1605 | 2.7622 | 26773.789 | 0.59158 | -10250.7601
572 | C-SOK-TOU-FC-ET-WC-R100 | 18 | 0.9 | 549.8784 | 0.37094 | 0.55993 | 0.20133 | 0.084038 | 0.63973 | 570.85 | 125.925 | 1024.225 | 2023.2 | 9.1238 | 25621.3263 | 594.9217 | 1194.2347 | 9.377 | 127.2062 | 44.7083 | 1.1736 | 2.7623 | 26811.3433 | 0.61038 | -10167.3499
573 | C-SOK-TOU-FC-ET-WC-R100 | 18 | 1.35 | 561.5751 | 0.37883 | 0.55907 | 0.20819 | 0.089891 | 0.64559 | 572.4 | 131.175 | 1024.225 | 1990.7 | 9.1362 | 25442.7812 | 597.0414 | 1194.2963 | 9.3575 | 126.2754 | 44.5863 | 1.1809 | 2.763 | 26824.471 | 0.61751 | -10164.049
574 | C-SOK-TOU-FC-ET-WC-R100 | 24.5 | 0.6 | 463.5045 | 0.31267 | 0.55789 | 0.30449 | 0.11217 | 0.64613 | 567.9 | 177.45 | 1024.225 | 2263.575 | 9.1359 | 24499.4625 | 584.3156 | 1194.168 | 9.3628 | 125.7692 | 45.4803 | 1.2096 | 2.7635 | 26837.9309 | 0.63485 | -9918.2997
575 | C-SOK-TOU-FC-ET-WC-R100 | 24.5 | 1.25 | 491.7667 | 0.33173 | 0.55719 | 0.32986 | 0.12914 | 0.67256 | 567.8 | 193.825 | 1024.225 | 2173.025 | 9.1427 | 23887.2885 | 588.7955 | 1194.3735 | 9.3494 | 123.4227 | 45.2196 | 1.2313 | 2.763 | 26870.9894 | 0.65244 | -9833.4903
576 | C-SOK-TOU-FC-ET-WC-R100 | 24.5 | 1.85 | 503.1814 | 0.33943 | 0.55598 | 0.35273 | 0.1354 | 0.67906 | 569.075 | 208.025 | 1024.225 | 2139.375 | 9.1548 | 23613.7398 | 591.1162 | 1194.2814 | 9.3109 | 122.4521 | 45.0618 | 1.24 | 2.7634 | 26872.164 | 0.66081 | -9809.4128
577 | C-SOK-TOU-FC-ET-WC-R100 | 31 | 0.8 | 416.3178 | 0.28084 | 0.56001 | 0.39232 | 0.15064 | 0.6776 | 555.825 | 215.05 | 1024.225 | 2398.225 | 9.1057 | 23077.9341 | 578.4938 | 1194.1394 | 9.4511 | 122.519 | 45.962 | 1.2548 | 2.763 | 26883.8765 | 0.67081 | -9781.9859
578 | C-SOK-TOU-FC-ET-WC-R100 | 31 | 1.55 | 439.7064 | 0.29662 | 0.55946 | 0.428 | 0.16845 | 0.69855 | 555.075 | 237.6 | 1024.225 | 2319.75 | 9.1131 | 22421.4658 | 581.7835 | 1194.2665 | 9.4477 | 120.676 | 45.7692 | 1.282 | 2.764 | 26909.0104 | 0.68566 | -9706.3599
579 | C-SOK-TOU-FC-ET-WC-R100 | 31 | 2.35 | 451.8197 | 0.30479 | 0.55823 | 0.44585 | 0.17828 | 0.70627 | 555.95 | 251.15 | 1024.225 | 2280.525 | 9.1291 | 22089.7489 | 583.5971 | 1194.4687 | 9.4421 | 119.6639 | 45.6555 | 1.2954 | 2.7634 | 26918.1851 | 0.69237 | -9667.3853
580 | C-SOK-TOU-FC-ET-WC-R10 | 38 | 0.95 | 373.2517 | 0.25179 | 0.55839 | 0.46256 | 0.18601 | 0.69731 | 552.225 | 249.575 | 1024.225 | 2533.325 | 9.1134 | 21884.7945 | 575.8878 | 1194.285 | 9.5058 | 119.9457 | 46.1967 | 1.2958 | 2.7649 | 26912.4146 | 0.69779 | -9720.3049
581 | C-SOK-TOU-FC-ET-WC-R10 | 38 | 1.9 | 398.6294 | 0.26891 | 0.55821 | 0.51253 | 0.20805 | 0.71872 | 549.675 | 280.375 | 1024.225 | 2442.3 | 9.1147 | 21062.6566 | 579.612 | 1194.2151 | 9.5155 | 118.0325 | 45.986 | 1.3329 | 2.7649 | 26948.6858 | 0.71012 | -9602.8762
582 | C-SOK-TOU-FC-ET-WC-R10 | 38 | 2.85 | 410.716 | 0.27706 | 0.55851 | 0.54752 | 0.22004 | 0.71999 | 547.275 | 301.775 | 1024.225 | 2401.575 | 9.1153 | 20625.6369 | 581.2364 | 1194.3896 | 9.5226 | 116.7567 | 45.8825 | 1.3489 | 2.7642 | 26956.6156 | 0.71754 | -9600.3171
583 | C-SOK-TOU-FC-ET-WC-R10 | 44.5 | 1.1 | 342.0414 | 0.23073 | 0.55751 | 0.51347 | 0.21598 | 0.71156 | 548.85 | 274.625 | 1024.225 | 2638.375 | 9.1141 | 20922.2691 | 576.6723 | 1194.0811 | 9.5304 | 117.6461 | 46.1769 | 1.3306 | 2.7656 | 26935.7228 | 0.71554 | -9666.3245
584 | C-SOK-TOU-FC-ET-WC-R10 | 44.5 | 2.25 | 366.9058 | 0.24751 | 0.55763 | 0.5794 | 0.24247 | 0.72911 | 545 | 315.35 | 1024.225 | 2544.375 | 9.115 | 19943.7321 | 579.7223 | 1194.2815 | 9.5718 | 115.4934 | 46.0182 | 1.3764 | 2.7655 | 26973.7306 | 0.72929 | -9587.1383
585 | C-SOK-TOU-FC-ET-WC-R10 | 44.5 | 3.35 | 376.9572 | 0.25429 | 0.55761 | 0.61401 | 0.25429 | 0.73321 | 541.525 | 333.725 | 1024.225 | 2508.75 | 9.118 | 19497.714 | 580.8233 | 1194.1821 | 9.5909 | 114.3182 | 45.9467 | 1.3942 | 2.7661 | 26977.9566 | 0.73672 | -9580.6292
586 | C-SOK-STR-FC-FP-WC-OFF0 | 18 | 0.45 | 296.9596 | 0.25816 | 0.59554 | 0.18472 | 0.055958 | 1 | 876 | 176.025 | 1446.5 | 3077.625 | 15.5384 | 15652.5519 | 671.8325 | 1887.0567 | 9.8973 | 80.8556 | 21.4417 | 0.99987 | 2.842 | 9572.9904 | 0.38062 | 3310.7603
587 | C-SOK-STR-FC-FP-WC-OFF0 | 18 | 0.9 | 303.7379 | 0.26405 | 0.59542 | 0.18431 | 0.069046 | 1 | 876.675 | 177.45 | 1446.5 | 3105.75 | 15.5401 | 15531.5357 | 669.971 | 1886.9818 | 9.9068 | 80.416 | 21.5008 | 1.0069 | 2.8419 | 9572.9904 | 0.39447 | 3310.607
588 | C-SOK-STR-FC-FP-WC-OFF0 | 18 | 1.35 | 307.615 | 0.26742 | 0.5947 | 0.1836 | 0.075307 | 1 | 878.85 | 179.475 | 1446.5 | 3106.325 | 15.5518 | 15484.4244 | 670.2616 | 1886.8839 | 9.8996 | 80.2293 | 21.4905 | 1.0103 | 2.8417 | 9572.9904 | 0.39957 | 3324.6435
589 | C-SOK-STR-FC-FP-WC-OFF0 | 24.5 | 0.6 | 267.4463 | 0.2325 | 0.59199 | 0.2641 | 0.09454 | 1 | 880 | 240.125 | 1446.5 | 3162.175 | 15.5854 | 14674.1329 | 670.2995 | 1886.9413 | 9.8544 | 78.7463 | 21.4898 | 1.0366 | 2.8418 | 9572.9904 | 0.46708 | 3491.9498
590 | C-SOK-STR-FC-FP-WC-OFF0 | 24.5 | 1.25 | 276.0185 | 0.23996 | 0.5918 | 0.26929 | 0.1123 | 1 | 879.875 | 247.475 | 1446.5 | 3184.95 | 15.5865 | 14463.8086 | 667.7634 | 1887.0305 | 9.8773 | 78.2984 | 21.5716 | 1.046 | 2.8418 | 9572.9904 | 0.4841 | 3488.7406
591 | C-SOK-STR-FC-FP-WC-OFF0 | 24.5 | 1.85 | 281.5578 | 0.24477 | 0.59064 | 0.27684 | 0.12487 | 1 | 883.075 | 256.85 | 1446.5 | 3183.4 | 15.6058 | 14293.4547 | 667.5543 | 1887.0117 | 9.8575 | 77.9986 | 21.5784 | 1.0553 | 2.8418 | 9572.9904 | 0.50159 | 3438.0927
592 | C-SOK-STR-FC-FP-WC-OFF0 | 31 | 0.8 | 233.9598 | 0.20339 | 0.59164 | 0.31903 | 0.13085 | 1 | 874.55 | 278.125 | 1446.5 | 3279.05 | 15.5831 | 13881.6685 | 665.6667 | 1887.1499 | 9.8623 | 77.2126 | 21.6396 | 1.0673 | 2.8416 | 9572.9904 | 0.53194 | 3394.7149
593 | C-SOK-STR-FC-FP-WC-OFF0 | 31 | 1.55 | 245.2108 | 0.21317 | 0.59062 | 0.33643 | 0.15112 | 1 | 876.5 | 297.825 | 1446.5 | 3281.125 | 15.5998 | 13554.5124 | 664.1184 | 1886.8364 | 9.8613 | 77.0975 | 21.6896 | 1.0881 | 2.8419 | 9572.9904 | 0.55236 | 3402.7843
594 | C-SOK-STR-FC-FP-WC-OFF0 | 31 | 2.35 | 253.4811 | 0.22036 | 0.59028 | 0.34869 | 0.16711 | 1 | 876.775 | 312.925 | 1446.5 | 3263.625 | 15.6071 | 13304.4685 | 663.6353 | 1886.7595 | 9.8654 | 76.7677 | 21.7056 | 1.1018 | 2.8421 | 9572.9904 | 0.5668 | 3404.0535
595 | C-SOK-STR-FC-FP-WC-OFF | 38 | 0.95 | 209.9265 | 0.1825 | 0.59056 | 0.37044 | 0.16345 | 1 | 872.975 | 314.55 | 1446.5 | 3371.85 | 15.5973 | 13159.9079 | 664.6028 | 1886.9208 | 9.8479 | 76.1969 | 21.6752 | 1.1002 | 2.8423 | 9572.9904 | 0.57613 | 3381.314
596 | C-SOK-STR-FC-FP-WC-OFF | 38 | 1.9 | 225.5438 | 0.19608 | 0.59029 | 0.40139 | 0.1939 | 1 | 872 | 344.75 | 1446.5 | 3350.125 | 15.5949 | 12616.5317 | 662.5378 | 1886.8931 | 9.8765 | 75.7287 | 21.7416 | 1.1309 | 2.8419 | 9572.9904 | 0.59991 | 3429.0267
597 | C-SOK-STR-FC-FP-WC-OFF | 38 | 2.85 | 235.5758 | 0.2048 | 0.5893 | 0.42781 | 0.2111 | 1 | 873.2 | 374.925 | 1446.5 | 3330.05 | 15.6107 | 12243.4592 | 662.1415 | 1886.8025 | 9.8827 | 75.1266 | 21.7546 | 1.1477 | 2.8421 | 9572.9904 | 0.61758 | 3423.3664
598 | C-SOK-STR-FC-FP-WC-OFF | 44.5 | 1.1 | 194.5693 | 0.16915 | 0.58982 | 0.42007 | 0.19057 | 1 | 869.775 | 349.125 | 1446.5 | 3429.975 | 15.5951 | 12499.6554 | 664.2904 | 1886.8595 | 9.8611 | 75.1018 | 21.6848 | 1.1318 | 2.8422 | 9572.9904 | 0.60817 | 3392.6065
599 | C-SOK-STR-FC-FP-WC-OFF | 44.5 | 2.25 | 212.4838 | 0.18472 | 0.58863 | 0.46684 | 0.22939 | 1 | 870.45 | 396.8 | 1446.5 | 3401.65 | 15.6125 | 11753.7833 | 663.4417 | 1886.8205 | 9.8737 | 74.1721 | 21.7125 | 1.1695 | 2.8422 | 9572.9904 | 0.63752 | 3427.412
600 | C-SOK-STR-FC-FP-WC-OFF | 44.5 | 3.35 | 220.2267 | 0.19145 | 0.58712 | 0.48829 | 0.24487 | 1 | 873 | 422.725 | 1446.5 | 3395.475 | 15.6379 | 11440.2162 | 663.0292 | 1886.8795 | 9.8757 | 73.8284 | 21.726 | 1.1849 | 2.8422 | 9572.9904 | 0.64925 | 3437.3329
601 | C-SOK-TOU-CC-ET-WC-R100 | 23 | 0.6 | 497.2097 | 0.33541 | 0.69117 | 0.26504 | 0.079295 | 0.61234 | 444.225 | 127.825 | 850.5 | 2168.35 | 9.8841 | 33003.6765 | 558.7375 | 1296.4819 | 13.3657 | 163.3988 | 62.3781 | 1.1904 | 3.0737 | 35603.8985 | 0.64955 | -20904.2414
602 | C-SOK-TOU-CC-ET-WC-R100 | 23 | 1.15 | 524.9777 | 0.35414 | 0.68971 | 0.28429 | 0.091662 | 0.63689 | 446.2 | 139.925 | 850.5 | 2086.5 | 9.8991 | 32417.3648 | 564.4192 | 1296.458 | 13.2864 | 160.1482 | 61.8829 | 1.2061 | 3.0741 | 35645.9331 | 0.66813 | -20918.3821
603 | C-SOK-TOU-CC-ET-WC-R100 | 23 | 1.75 | 536.1824 | 0.3617 | 0.68905 | 0.2914 | 0.098066 | 0.63978 | 446.225 | 146.075 | 850.5 | 2055.625 | 9.9078 | 32185.9904 | 566.7793 | 1296.5249 | 13.2583 | 158.5503 | 61.6754 | 1.2122 | 3.0748 | 35659.9243 | 0.67455 | -20949.3164
604 | C-SOK-TOU-CC-ET-WC-R100 | 32 | 0.8 | 428.5606 | 0.2891 | 0.68808 | 0.38522 | 0.12153 | 0.64712 | 440.85 | 175.75 | 850.5 | 2365.75 | 9.8953 | 31006.4 | 555.9645 | 1296.3767 | 13.279 | 157.2113 | 62.7851 | 1.2427 | 3.0716 | 35686.5 | 0.69462 | -20833.8697
605 | C-SOK-TOU-CC-ET-WC-R100 | 32 | 1.6 | 455.6528 | 0.30737 | 0.68786 | 0.41408 | 0.13834 | 0.66838 | 440.825 | 192.65 | 850.5 | 2280.325 | 9.906 | 30253.4486 | 562.1756 | 1296.4533 | 13.2084 | 153.9922 | 62.2295 | 1.2645 | 3.072 | 35727.009 | 0.70791 | -20788.0231
606 | C-SOK-TOU-CC-ET-WC-R100 | 32 | 2.4 | 468.3468 | 0.31594 | 0.6868 | 0.43994 | 0.14647 | 0.67332 | 441.175 | 206.325 | 850.5 | 2242.575 | 9.91 | 29859.4639 | 564.3756 | 1296.3814 | 13.1659 | 152.5211 | 62.0044 | 1.2767 | 3.0707 | 35723.7378 | 0.71513 | -20733.2603
607 | C-SOK-TOU-CC-ET-WC-R100 | 40.5 | 1 | 382.697 | 0.25816 | 0.68572 | 0.48318 | 0.15762 | 0.67279 | 437.375 | 214.1 | 850.5 | 2510.375 | 9.9161 | 29338.1062 | 556.7061 | 1296.5651 | 13.3238 | 151.9271 | 62.7965 | 1.285 | 3.0761 | 35734.6793 | 0.72694 | -20816.8731
608 | C-SOK-TOU-CC-ET-WC-R100 | 40.5 | 2.05 | 410.2652 | 0.27676 | 0.68469 | 0.52998 | 0.17905 | 0.69256 | 437.5 | 240.325 | 850.5 | 2412.95 | 9.9307 | 28368.5123 | 563.8076 | 1296.4924 | 13.2142 | 148.7557 | 62.1453 | 1.3189 | 3.0742 | 35773.0701 | 0.739 | -20736.6791
609 | C-SOK-TOU-CC-ET-WC-R100 | 40.5 | 3.05 | 422.6697 | 0.28512 | 0.68345 | 0.56027 | 0.18852 | 0.69907 | 438.35 | 257 | 850.5 | 2374.025 | 9.9401 | 27906.9644 | 567.5053 | 1296.4771 | 13.1407 | 147.0329 | 61.7931 | 1.3302 | 3.0736 | 35780.5361 | 0.74518 | -20698.7337
610 | C-SOK-TOU-CC-ET-WC-R10 | 49 | 1.25 | 348.4013 | 0.23502 | 0.68244 | 0.56005 | 0.19232 | 0.69253 | 435.075 | 246.55 | 850.5 | 2627.35 | 9.9285 | 27841.3275 | 560.3811 | 1296.5963 | 13.3643 | 146.9142 | 62.4911 | 1.3281 | 3.0754 | 35774.9192 | 0.75134 | -20835.7546
611 | C-SOK-TOU-CC-ET-WC-R10 | 49 | 2.45 | 373.2126 | 0.25176 | 0.68099 | 0.62081 | 0.21564 | 0.71009 | 435.85 | 276.7 | 850.5 | 2534.875 | 9.9561 | 26764.1019 | 568.8133 | 1296.6959 | 13.214 | 143.5857 | 61.7323 | 1.3648 | 3.0763 | 35819.1994 | 0.76339 | -20813.6912
612 | C-SOK-TOU-CC-ET-WC-R10 | 49 | 3.7 | 384.8293 | 0.2596 | 0.6792 | 0.66103 | 0.22469 | 0.71351 | 437.325 | 298.375 | 850.5 | 2490.225 | 9.9686 | 26285.1873 | 573.2461 | 1296.5996 | 13.132 | 141.9908 | 61.3159 | 1.3777 | 3.0752 | 35828.347 | 0.76679 | -20756.8265
613 | C-SOK-TOU-CC-ET-WC-R10 | 58 | 1.45 | 318.3439 | 0.21475 | 0.67914 | 0.62377 | 0.22352 | 0.70584 | 434.55 | 273.375 | 850.5 | 2738.775 | 9.9563 | 26547.0782 | 569.1027 | 1296.7079 | 13.3277 | 141.7547 | 61.6841 | 1.3649 | 3.0773 | 35805.4229 | 0.76791 | -20829.1137
614 | C-SOK-TOU-CC-ET-WC-R10 | 58 | 2.9 | 341.4128 | 0.23031 | 0.67657 | 0.69069 | 0.24934 | 0.72165 | 437.05 | 309.925 | 850.5 | 2648.65 | 9.9785 | 25374.9837 | 578.0847 | 1296.601 | 13.1728 | 138.3611 | 60.8884 | 1.4067 | 3.0763 | 35848.6774 | 0.77824 | -20789.2901
615 | C-SOK-TOU-CC-ET-WC-R10 | 58 | 4.35 | 351.6953 | 0.23725 | 0.67581 | 0.7327 | 0.25949 | 0.72486 | 437.275 | 328.55 | 850.5 | 2605 | 9.999 | 24853.1832 | 582.4317 | 1296.6564 | 13.105 | 136.8471 | 60.4951 | 1.4245 | 3.0773 | 35857.294 | 0.78185 | -20743.3714
616 | C-SOK-TOU-CC-FP-WC-R100 | 23 | 0.6 | 484.194 | 0.32663 | 0.69083 | 0.23132 | 0.089236 | 0.60533 | 445.125 | 110.325 | 850.5 | 2413.875 | 9.8853 | 32905.8394 | 546.7145 | 1296.5685 | 13.5066 | 162.3489 | 63.5421 | 1.1943 | 3.0741 | 35565.837 | 0.67268 | -21158.229
617 | C-SOK-TOU-CC-FP-WC-R100 | 23 | 1.15 | 520.659 | 0.35122 | 0.69087 | 0.23542 | 0.10775 | 0.63865 | 444.8 | 115.2 | 850.5 | 2373.15 | 9.8838 | 32153.2751 | 549.0778 | 1296.5227 | 13.5205 | 158.9531 | 63.3792 | 1.2158 | 3.0737 | 35616.4999 | 0.69256 | -21116.0754
618 | C-SOK-TOU-CC-FP-WC-R100 | 23 | 1.75 | 537.22 | 0.3624 | 0.69033 | 0.24295 | 0.11847 | 0.64374 | 445.15 | 121.325 | 850.5 | 2364.2 | 9.8893 | 31778.9813 | 549.5726 | 1296.5934 | 13.5084 | 157.2789 | 63.3542 | 1.228 | 3.0739 | 35631.9946 | 0.70311 | -21158.9308
619 | C-SOK-TOU-CC-FP-WC-R100 | 32 | 0.8 | 412.4245 | 0.27821 | 0.68988 | 0.31363 | 0.12912 | 0.64293 | 441.625 | 144.325 | 850.5 | 2595.8 | 9.8831 | 31136.656 | 546.3192 | 1296.5513 | 13.4609 | 156.8129 | 63.7196 | 1.2397 | 3.0721 | 35651.5589 | 0.70844 | -21061.9731
620 | C-SOK-TOU-CC-FP-WC-R100 | 32 | 1.6 | 448.6637 | 0.30266 | 0.68963 | 0.34408 | 0.15658 | 0.66892 | 440.225 | 159.65 | 850.5 | 2567.075 | 9.8861 | 30036.9849 | 547.0372 | 1296.4031 | 13.4708 | 153.4601 | 63.726 | 1.2735 | 3.0719 | 35701.927 | 0.73137 | -21088.0574
621 | C-SOK-TOU-CC-FP-WC-R100 | 32 | 2.4 | 464.1148 | 0.31308 | 0.6892 | 0.36069 | 0.16818 | 0.67637 | 440.75 | 170.525 | 850.5 | 2552.775 | 9.8945 | 29571.8695 | 547.8168 | 1296.5369 | 13.4471 | 152.2721 | 63.6474 | 1.2894 | 3.0726 | 35702.2457 | 0.73868 | -21017.7187
622 | C-SOK-TOU-CC-FP-WC-R100 | 40.5 | 1 | 366.4501 | 0.2472 | 0.68799 | 0.38946 | 0.16507 | 0.66707 | 438 | 173.75 | 850.5 | 2721.95 | 9.8695 | 29583.9676 | 548.4421 | 1296.3568 | 13.4637 | 151.7151 | 63.5777 | 1.2821 | 3.068 | 35704.7353 | 0.73858 | -21087.8706
623 | C-SOK-TOU-CC-FP-WC-R100 | 40.5 | 2.05 | 400.5981 | 0.27023 | 0.68775 | 0.43011 | 0.19782 | 0.69108 | 437.325 | 194.2 | 850.5 | 2701.05 | 9.9066 | 28294.4771 | 549.9868 | 1296.601 | 13.4537 | 148.4925 | 63.5016 | 1.3206 | 3.0749 | 35747.8582 | 0.75861 | -21067.7724
624 | C-SOK-TOU-CC-FP-WC-R100 | 40.5 | 3.05 | 415.9232 | 0.28057 | 0.68557 | 0.45077 | 0.21224 | 0.70035 | 439.65 | 206.025 | 850.5 | 2696.525 | 9.9153 | 27719.9058 | 549.9561 | 1296.5452 | 13.4157 | 147.6885 | 63.5106 | 1.343 | 3.0727 | 35754.0842 | 0.76583 | -21004.7236
625 | C-SOK-TOU-CC-FP-WC-R10 | 49 | 1.25 | 334.0797 | 0.22536 | 0.68603 | 0.46106 | 0.20091 | 0.68669 | 435.45 | 200.15 | 850.5 | 2826.625 | 9.91 | 28088.4434 | 554.8081 | 1296.6287 | 13.4703 | 146.0139 | 63.0043 | 1.3199 | 3.0766 | 35743.5635 | 0.7651 | -21150.118
626 | C-SOK-TOU-CC-FP-WC-R10 | 49 | 2.45 | 363.4156 | 0.24515 | 0.68469 | 0.51026 | 0.23359 | 0.71032 | 435.375 | 227.1 | 850.5 | 2816.45 | 9.9326 | 26756.3066 | 554.5901 | 1296.6038 | 13.4357 | 144.3133 | 63.0986 | 1.374 | 3.0772 | 35787.6938 | 0.78121 | -21120.4291
627 | C-SOK-TOU-CC-FP-WC-R10 | 49 | 3.7 | 378.157 | 0.2551 | 0.68195 | 0.54784 | 0.25064 | 0.71654 | 438.55 | 244.825 | 850.5 | 2806.225 | 9.9502 | 26043.1634 | 556.0401 | 1296.6401 | 13.3734 | 142.6238 | 62.9652 | 1.3914 | 3.0763 | 35797.2358 | 0.79074 | -21136.1461
628 | C-SOK-TOU-CC-FP-WC-R10 | 58 | 1.45 | 304.8546 | 0.20565 | 0.6832 | 0.50856 | 0.23112 | 0.70221 | 436.075 | 223.15 | 850.5 | 2925.65 | 9.922 | 26888.5147 | 564.1332 | 1296.6067 | 13.437 | 141.0564 | 62.1146 | 1.3579 | 3.0758 | 35771.8387 | 0.77886 | -21096.6985
629 | C-SOK-TOU-CC-FP-WC-R10 | 58 | 2.9 | 332.1254 | 0.22404 | 0.68112 | 0.5684 | 0.26731 | 0.72829 | 436.525 | 253.825 | 850.5 | 2918.9 | 9.9455 | 25385.7822 | 563.8434 | 1296.5051 | 13.4115 | 138.991 | 62.2212 | 1.4137 | 3.0757 | 35821.3445 | 0.79623 | -21106.4268
630 | C-SOK-TOU-CC-FP-WC-R10 | 58 | 4.35 | 346.5987 | 0.23381 | 0.67896 | 0.61674 | 0.28659 | 0.73018 | 439 | 276.075 | 850.5 | 2918.5 | 9.971 | 24580.082 | 564.8728 | 1296.6222 | 13.3127 | 137.9872 | 62.1374 | 1.4424 | 3.0772 | 35830.637 | 0.80444 | -21124.2433
631 | C-SOK-TOU-CC-ET-WC-R600 | 23 | 0.6 | 539.9383 | 0.36598 | 0.69458 | 0.28663 | 0.09517 | 0.67385 | 562.325 | 167.875 | 1048.625 | 2258.05 | 12.7068 | 23251.4661 | 588.5992 | 1580.44 | 13.5349 | 134.1354 | 45.2782 | 1.1887 | 3.117 | 25282.8077 | 0.66615 | -29348.2868
632 | C-SOK-TOU-CC-ET-WC-R600 | 23 | 1.15 | 569.2397 | 0.38585 | 0.69338 | 0.30806 | 0.10959 | 0.69871 | 563.45 | 184.7 | 1048.625 | 2171.175 | 12.7152 | 22714.492 | 593.9412 | 1580.3695 | 13.487 | 131.6655 | 45.0562 | 1.2048 | 3.1159 | 25380.0718 | 0.68094 | -29601.5714
633 | C-SOK-TOU-CC-ET-WC-R600 | 23 | 1.75 | 581.7148 | 0.3943 | 0.69271 | 0.31845 | 0.11782 | 0.70099 | 564.525 | 195 | 1048.625 | 2135.125 | 12.7294 | 22495.3232 | 597.0048 | 1580.4452 | 13.4422 | 130.4113 | 44.8834 | 1.2111 | 3.1166 | 25402.358 | 0.68496 | -29652.9757
634 | C-SOK-TOU-CC-ET-WC-R600 | 32 | 0.8 | 454.4109 | 0.30801 | 0.69125 | 0.39519 | 0.14393 | 0.7078 | 559.075 | 226.75 | 1048.625 | 2481.8 | 12.7297 | 21494.7463 | 583.2597 | 1580.4684 | 13.5041 | 129.7073 | 45.818 | 1.2421 | 3.1162 | 25392.2118 | 0.69923 | -29397.6624
635 | C-SOK-TOU-CC-ET-WC-R600 | 32 | 1.6 | 481.8917 | 0.32664 | 0.6899 | 0.43744 | 0.16655 | 0.72454 | 559.175 | 255.35 | 1048.625 | 2397.575 | 12.7483 | 20724.3787 | 588.1511 | 1580.3994 | 13.4418 | 127.1254 | 45.586 | 1.2709 | 3.1163 | 25464.8095 | 0.7148 | -29594.9057
636 | C-SOK-TOU-CC-ET-WC-R600 | 32 | 2.4 | 495.9387 | 0.33616 | 0.68921 | 0.46657 | 0.17882 | 0.72562 | 559.4 | 273.6 | 1048.625 | 2355.15 | 12.765 | 20318.2219 | 590.5963 | 1580.4005 | 13.4064 | 125.8181 | 45.4409 | 1.2872 | 3.1171 | 25479.9856 | 0.7216 | -29638.1919
637 | C-SOK-TOU-CC-ET-WC-R600 | 40.5 | 1 | 397.1525 | 0.2692 | 0.68738 | 0.48167 | 0.18824 | 0.72916 | 555.85 | 272.075 | 1048.625 | 2651.25 | 12.7317 | 20021.6276 | 579.4173 | 1580.2976 | 13.5635 | 125.9964 | 46.1761 | 1.291 | 3.1121 | 25453.3993 | 0.72914 | -29549.1143
638 | C-SOK-TOU-CC-ET-WC-R600 | 40.5 | 2.05 | 425.1318 | 0.28817 | 0.68603 | 0.54452 | 0.21826 | 0.74439 | 555.525 | 311.925 | 1048.625 | 2561.65 | 12.7637 | 18990.443 | 584.4996 | 1580.3437 | 13.5215 | 122.8642 | 45.9043 | 1.3294 | 3.1143 | 25508.1992 | 0.74522 | -29665.774
639 | C-SOK-TOU-CC-ET-WC-R600 | 40.5 | 3.05 | 439.6887 | 0.29803 | 0.68593 | 0.58048 | 0.23465 | 0.7446 | 555.2 | 335.475 | 1048.625 | 2512.825 | 12.7987 | 18469.7832 | 589.0079 | 1580.4347 | 13.4461 | 121.2598 | 45.6141 | 1.35 | 3.1183 | 25519.3241 | 0.75094 | -29668.0721
640 | C-SOK-TOU-CC-ET-WC-R60 | 49 | 1.25 | 357.4667 | 0.2423 | 0.6851 | 0.55742 | 0.23077 | 0.75135 | 551.875 | 310.1 | 1048.625 | 2776.75 | 12.7789 | 18636.4044 | 581.0214 | 1580.4624 | 13.6178 | 122.0302 | 46.1509 | 1.3378 | 3.1185 | 25501.7502 | 0.75339 | -29652.204
641 | C-SOK-TOU-CC-ET-WC-R60 | 49 | 2.45 | 382.2524 | 0.2591 | 0.68354 | 0.62695 | 0.26414 | 0.76212 | 551.6 | 355.025 | 1048.625 | 2693.575 | 12.8009 | 17523.5293 | 586.3518 | 1580.4264 | 13.5626 | 118.8801 | 45.8321 | 1.3817 | 3.1177 | 25541.2113 | 0.76673 | -29708.4212
642 | C-SOK-TOU-CC-ET-WC-R60 | 49 | 3.7 | 396.7364 | 0.26892 | 0.68151 | 0.67176 | 0.2815 | 0.76608 | 554.675 | 382.925 | 1048.625 | 2646.725 | 12.841 | 16903.8832 | 590.7331 | 1580.4651 | 13.4895 | 117.1897 | 45.5489 | 1.4069 | 3.1186 | 25554.7273 | 0.77239 | -29686.9419
643 | C-SOK-TOU-CC-ET-WC-R60 | 58 | 1.45 | 323.279 | 0.21913 | 0.6824 | 0.61119 | 0.27141 | 0.76584 | 551.45 | 340 | 1048.625 | 2890.725 | 12.7978 | 17467.4169 | 585.7618 | 1580.5549 | 13.6417 | 118.1424 | 45.8673 | 1.3811 | 3.1184 | 25535.6734 | 0.7693 | -29698.9395
644 | C-SOK-TOU-CC-ET-WC-R60 | 58 | 2.9 | 348.9545 | 0.23653 | 0.67985 | 0.69535 | 0.31003 | 0.78056 | 552.825 | 393.775 | 1048.625 | 2801.325 | 12.8375 | 16136.0917 | 592.9672 | 1580.4764 | 13.5624 | 114.549 | 45.4233 | 1.4351 | 3.1179 | 25574.7295 | 0.78152 | -29676.704
645 | C-SOK-TOU-CC-ET-WC-R60 | 58 | 4.35 | 362.3025 | 0.24558 | 0.67677 | 0.74024 | 0.32966 | 0.78505 | 557.8 | 422.925 | 1048.625 | 2755.575 | 12.8818 | 15470.4167 | 597.65 | 1580.5395 | 13.4744 | 113.0442 | 45.1289 | 1.4692 | 3.1184 | 25591.2242 | 0.78663 | -29658.7078
646 | C-SOK-TOU-FC-ET-WC-R600 | 18 | 0.45 | 564.567 | 0.38268 | 0.56058 | 0.22124 | 0.086439 | 0.67443 | 693.225 | 160.575 | 1166.025 | 2192.875 | 11.1155 | 18375.6709 | 615.2729 | 1380.7402 | 9.3353 | 105.4001 | 32.26 | 1.1549 | 2.7966 | 18631.6922 | 0.60993 | -13926.0331
647 | C-SOK-TOU-FC-ET-WC-R600 | 18 | 0.9 | 596.6287 | 0.40441 | 0.56053 | 0.23301 | 0.1 | 0.70976 | 693.4 | 169.45 | 1166.025 | 2104.475 | 11.1168 | 17955.7412 | 620.4809 | 1380.8127 | 9.3157 | 103.7235 | 32.1331 | 1.17 | 2.7965 | 18712.6237 | 0.62385 | -13910.9232
648 | C-SOK-TOU-FC-ET-WC-R600 | 18 | 1.35 | 608.9879 | 0.41279 | 0.5602 | 0.24327 | 0.1082 | 0.71393 | 693.825 | 178.675 | 1166.025 | 2070.7 | 11.1249 | 17772.126 | 622.498 | 1380.7868 | 9.2986 | 102.925 | 32.065 | 1.1779 | 2.7968 | 18730.3565 | 0.62991 | -13926.4558
649 | C-SOK-TOU-FC-ET-WC-R600 | 24.5 | 0.6 | 491.7586 | 0.33333 | 0.55943 | 0.32092 | 0.13503 | 0.71246 | 686.875 | 221.85 | 1166.025 | 2378.45 | 11.1226 | 16971.4024 | 606.0594 | 1380.6634 | 9.3775 | 102.5016 | 32.8332 | 1.2064 | 2.7978 | 18718.2351 | 0.63939 | -13608.485
650 | C-SOK-TOU-FC-ET-WC-R600 | 24.5 | 1.25 | 520.9131 | 0.35309 | 0.55871 | 0.35201 | 0.15634 | 0.7354 | 686.85 | 244.8 | 1166.025 | 2290.325 | 11.1271 | 16400.2207 | 609.6789 | 1380.9433 | 9.3692 | 100.9068 | 32.7546 | 1.2335 | 2.7969 | 18784.362 | 0.6541 | -13617.3921
651 | C-SOK-TOU-FC-ET-WC-R600 | 24.5 | 1.85 | 534.104 | 0.36203 | 0.55902 | 0.37073 | 0.16837 | 0.73804 | 685.2 | 260.9 | 1166.025 | 2249.725 | 11.1237 | 16116.8924 | 610.5683 | 1380.8319 | 9.3815 | 100.0669 | 32.7273 | 1.2472 | 2.7971 | 18795.0524 | 0.66015 | -13603.2836
652 | C-SOK-TOU-FC-ET-WC-R600 | 31 | 0.8 | 432.0443 | 0.29285 | 0.5626 | 0.39687 | 0.18305 | 0.74022 | 669.65 | 260.825 | 1166.025 | 2537.55 | 11.0718 | 15729.1781 | 596.5151 | 1380.731 | 9.4902 | 100.3368 | 33.3963 | 1.258 | 2.797 | 18778.4413 | 0.6698 | -13563.1935
653 | C-SOK-TOU-FC-ET-WC-R600 | 31 | 1.55 | 455.7283 | 0.30891 | 0.55983 | 0.44336 | 0.21043 | 0.75652 | 673.475 | 296.65 | 1166.025 | 2463.525 | 11.1076 | 15030.3736 | 599.4035 | 1380.7092 | 9.4643 | 98.5734 | 33.313 | 1.2917 | 2.7982 | 18818.1968 | 0.68952 | -13630.7187
654 | C-SOK-TOU-FC-ET-WC-R600 | 31 | 2.35 | 470.915 | 0.3192 | 0.56084 | 0.47256 | 0.22643 | 0.75829 | 669.475 | 317.95 | 1166.025 | 2417.75 | 11.0988 | 14634.5464 | 600.3822 | 1380.6753 | 9.4941 | 97.4787 | 33.2822 | 1.3092 | 2.7983 | 18830.2196 | 0.69448 | -13584.4968
655 | C-SOK-TOU-FC-ET-WC-R60 | 38 | 0.95 | 381.4648 | 0.25857 | 0.56197 | 0.47176 | 0.22738 | 0.76131 | 661.625 | 299.9 | 1166.025 | 2690.375 | 11.0677 | 14599.8746 | 590.172 | 1380.6609 | 9.5751 | 98.2182 | 33.7761 | 1.3037 | 2.7987 | 18813.7692 | 0.6999 | -13625.4926
656 | C-SOK-TOU-FC-ET-WC-R60 | 38 | 1.9 | 407.1258 | 0.27596 | 0.56164 | 0.52817 | 0.26387 | 0.77598 | 658.675 | 342.825 | 1166.025 | 2605.05 | 11.0716 | 13713.1789 | 591.7417 | 1380.664 | 9.6085 | 96.3187 | 33.7464 | 1.351 | 2.7986 | 18847.3669 | 0.71548 | -13594.1717
657 | C-SOK-TOU-FC-ET-WC-R60 | 38 | 2.85 | 420.9957 | 0.28536 | 0.56009 | 0.57128 | 0.27952 | 0.78095 | 659.55 | 375.35 | 1166.025 | 2558.425 | 11.099 | 13234.1526 | 593.7149 | 1380.8397 | 9.6055 | 95.1205 | 33.6647 | 1.3745 | 2.7984 | 18859.8349 | 0.72369 | -13585.4923
658 | C-SOK-TOU-FC-ET-WC-R60 | 44.5 | 1.1 | 346.2887 | 0.23472 | 0.56139 | 0.51521 | 0.26784 | 0.7759 | 656.9 | 324.8 | 1166.025 | 2801.2 | 11.0691 | 13738.678 | 587.9007 | 1380.8313 | 9.6295 | 96.753 | 33.9356 | 1.3459 | 2.7983 | 18841.2745 | 0.71645 | -13607.8952
659 | C-SOK-TOU-FC-ET-WC-R60 | 44.5 | 2.25 | 372.2231 | 0.2523 | 0.56214 | 0.58796 | 0.30787 | 0.79366 | 650.7 | 376.35 | 1166.025 | 2711.05 | 11.0607 | 12684.3586 | 589.5714 | 1380.7193 | 9.6822 | 94.4765 | 33.8988 | 1.4021 | 2.7982 | 18874.3997 | 0.73164 | -13532.3171
660 | C-SOK-TOU-FC-ET-WC-R60 | 44.5 | 3.35 | 385.6271 | 0.26139 | 0.56073 | 0.63313 | 0.32721 | 0.79878 | 651.075 | 410.325 | 1166.025 | 2669.075 | 11.0833 | 12142.4933 | 590.8841 | 1380.6986 | 9.689 | 93.4373 | 33.8523 | 1.4354 | 2.7984 | 18888.1138 | 0.73949 | -13519.4518
Note on S1: bnienbor: with electricity for pumps in solar circuit (weightened), with electricity for boiler (weightened), without cold water pump
Note on T1: bnienbor: with electricity for pumps in solar circuit (weightened), with electricity for boiler (weightened), without cold water pump

## Yearly Data
CODE | SYSTEM | CHILLER | LOCATION | COLD | COLLECTOR | HEAT | BUILDING | F_SCAL | A_COLLECTOR | V_STORAGE | TIME | PS1/2 | PB | PELBOILER | PDHW | PH | PC | PHR | PCW | PELCHILLER | PELCT | TIME | Q_IRR | Q_COLL | Q_AUX_SUMMER | Q_AUX_WINTER | Q_AUX_DHW | Q_AUX_HEAT | Q_AUX_COOL | Q_LOSS_STORE | Q_SOLAR_COOL | Q_LOSS_PIPES | TIME | Q_COLD | Q_COLD_AUX | Q_COLD_SOLAR | Q_COLD_DEMAND | Q_HEAT_DEMAND | Q_DHW_DEMAND | Q_HR | Q_CHILLER_TOT | Q_DHW_SUMMER | Q_SOLARTOSYSTEM | TIME | V_WATER | SOLARCOOLINGTIME | AUXCOOLINGTIME | COOLINGDEMANDTIME | PELREFCHILLER | PELREFBOILER | STAGNATION TIME
| SCHEME |  |  | DISTRIBUTION | TYPE | REJECTION
1 | C | SOK | NAP | CC | ET | HC | R100 | 2.9609 | 16.5 | 0.413 | 8760 | 166290.2175 | 0 | 141883.7968 | 65533.1035 | 103333.9419 | 41061 | 95809 | 92387.25 | 82122 | 26561.5967 | 8760 | 1720.1251 | 11994.5748 | 0 | 0 | 1114.8526 | 7194.305 | 5850.395 | -1276.7949 | 3052.9243 | 3320.083 | 8760 | 6309.9758 | 4202.1829 | 2107.7929 | 6320.3721 | 8635.9087 | 4239.2217 | 14759.3795 | 8696.5604 | 0 | 9443.1019 | 8760 | 0 | 252.65 | 431.7 | 1854.725 | 2040772.678 | 178372.614 | 2091 | -51.4639
2 | C | SOK | NAP | CC | ET | HC | R100 | 2.9609 | 16.5 | 0.825 | 8760 | 173353.2594 | 0 | 139213.2248 | 65533.1035 | 103333.9419 | 41250 | 96250 | 92812.5 | 82500 | 23990.5843 | 8760 | 1720.1251 | 12599.8039 | 0 | 0 | 1005.8556 | 6955.8852 | 5792.7386 | -1331.0739 | 3112.3795 | 3311.3141 | 8760 | 6311.5666 | 4151.212 | 2160.3546 | 6320.3721 | 8635.9087 | 4289.5536 | 14771.3417 | 8703.4872 | 0 | 10037.0336 | 8760 | 0 | 255.875 | 431.625 | 1854.725 | 2040795.3105 | 178372.614 | 1996.95 | -43.5096
3 | C | SOK | NAP | CC | ET | HC | R100 | 2.9609 | 16.5 | 1.238 | 8760 | 176373.5417 | 0 | 138335.7834 | 65533.1035 | 103333.9419 | 41325 | 96425 | 92981.25 | 82650 | 23266.8637 | 8760 | 1720.1251 | 12842.6517 | 0 | 0 | 1002.1166 | 6854.7391 | 5719.9147 | -1350.7282 | 3180.523 | 3313.6646 | 8760 | 6311.1113 | 4091.2088 | 2219.9025 | 6320.3721 | 8635.9087 | 4300.1333 | 14770.8895 | 8704.9189 | 0 | 10277.4051 | 8760 | 0 | 258.6 | 430.15 | 1854.725 | 2040792.5819 | 178372.614 | 1957.775 | -43.5107
4 | C | SOK | NAP | CC | ET | HC | R100 | 2.9609 | 22.5 | 0.563 | 8760 | 163456.6016 | 0 | 133519.6045 | 65533.1035 | 103333.9419 | 39966 | 93254 | 89923.5 | 79932 | 12399.4656 | 8760 | 1720.1251 | 14402.8421 | 0 | 0 | 953.354 | 6533.2814 | 4875.5287 | -1356.4711 | 4021.0125 | 3433.3485 | 8760 | 6312.5078 | 3529.9213 | 2782.5866 | 6320.3721 | 8635.9087 | 4297.4714 | 14795.9456 | 8711.6338 | 0 | 11634.645 | 8760 | 0 | 320.7 | 345.4 | 1854.725 | 2040865.7531 | 178372.614 | 2318 | -15.7591
5 | C | SOK | NAP | CC | ET | HC | R100 | 2.9609 | 22.5 | 1.125 | 8760 | 171452.7007 | 0 | 129911.595 | 65533.1035 | 103333.9419 | 39981 | 93289 | 89957.25 | 79962 | 11712.3605 | 8760 | 1720.1251 | 15246.1461 | 0 | 0 | 852.083 | 6211.2099 | 4600.616 | -1408.3595 | 4275.6744 | 3431.4197 | 8760 | 6312.0097 | 3327.6806 | 2984.3291 | 6320.3721 | 8635.9087 | 4331.9568 | 14794.929 | 8716.1327 | 0 | 12455.5418 | 8760 | 0 | 334.5 | 331.85 | 1854.725 | 2040788.7389 | 178372.614 | 2219.15 | -15.1134
6 | C | SOK | NAP | CC | ET | HC | R100 | 2.9609 | 22.5 | 1.688 | 8760 | 174836.5505 | 0 | 128739.4232 | 65533.1035 | 103333.9419 | 40009.5 | 93355.5 | 90021.375 | 80019 | 11641.1102 | 8760 | 1720.1251 | 15588.6078 | 0 | 0 | 864.3286 | 6061.1103 | 4402.1781 | -1421.7536 | 4470.0283 | 3426.2974 | 8760 | 6313.1284 | 3176.4377 | 3136.6907 | 6320.3721 | 8635.9087 | 4336.3551 | 14798.2029 | 8720.9586 | 0 | 12800.6305 | 8760 | 0 | 345.625 | 321.2 | 1854.725 | 2040905.4477 | 178372.614 | 2180.825 | -17.0089
7 | C | SOK | NAP | CC | ET | HC | R100 | 2.9609 | 29 | 0.725 | 8760 | 156455.7988 | 0 | 127421.0111 | 65533.1035 | 103333.9419 | 39388.5 | 91906.5 | 88624.125 | 78777 | 18308.9757 | 8760 | 1720.1251 | 15631.5216 | 0 | 0 | 833.9265 | 5907.5367 | 4445.1231 | -1416.3897 | 4484.7382 | 3493.4909 | 8760 | 6314.9177 | 3188.5581 | 3126.3597 | 6320.3721 | 8635.9087 | 4335.2284 | 14744.2974 | 8707.5064 | 0 | 12759.512 | 8760 | 0 | 347.95 | 308.525 | 1854.725 | 2040886.2673 | 178372.614 | 2566.55 | -109.627
8 | C | SOK | NAP | CC | ET | HC | R100 | 2.9609 | 29 | 1.45 | 8760 | 165770.2803 | 0 | 122720.3245 | 65533.1035 | 103333.9419 | 39145.5 | 91339.5 | 88077.375 | 78291 | 14368.9968 | 8760 | 1720.1251 | 16759.5129 | 0 | 0 | 748.7456 | 5474.5384 | 3877.242 | -1461.4974 | 5005.0097 | 3494.1723 | 8760 | 6315.587 | 2799.3852 | 3516.2018 | 6320.3721 | 8635.9087 | 4360.8087 | 14775.5073 | 8719.6227 | 0 | 13843.3655 | 8760 | 0 | 379.05 | 273.375 | 1854.725 | 2040894.9617 | 178372.614 | 2461.65 | -70.4192
9 | C | SOK | NAP | CC | ET | HC | R100 | 2.9609 | 29 | 2.175 | 8760 | 171194.2651 | 0 | 120213.9916 | 65533.1035 | 103333.9419 | 39169.5 | 91395.5 | 88131.375 | 78339 | 17958.8146 | 8760 | 1720.1251 | 17418.4016 | 0 | 0 | 772.1879 | 5238.7803 | 3487.1456 | -1469.566 | 5387.677 | 3483.8294 | 8760 | 6317.4005 | 2501.471 | 3815.9295 | 6320.3721 | 8635.9087 | 4358.2099 | 14780.8739 | 8726.587 | 0 | 14513.3091 | 8760 | 0 | 401.675 | 251.15 | 1854.725 | 2040952.3251 | 178372.614 | 2406.2 | -71.6861
10 | C | SOK | NAP | CC | ET | HC | R10 | 2.9609 | 35 | 0.875 | 8760 | 152280.2805 | 0 | 122148.8626 | 65533.1035 | 103333.9419 | 38473.5 | 89771.5 | 86565.375 | 76947 | 19292.4493 | 8760 | 1720.1251 | 16400.6233 | 0 | 0 | 756.1546 | 5374.0058 | 3908.8602 | -1454.747 | 4956.2725 | 3528.8583 | 8760 | 6318.8656 | 2857.0906 | 3461.775 | 6320.3721 | 8635.9087 | 4358.4886 | 14818.7694 | 8721.293 | 0 | 13448.6141 | 8760 | 0 | 371.75 | 269.475 | 1854.725 | 2040999.3576 | 178372.614 | 2752.575 | -26.8569
11 | C | SOK | NAP | CC | ET | HC | R10 | 2.9609 | 35 | 1.75 | 8760 | 164305.0526 | 0 | 116804.7189 | 65533.1035 | 103333.9419 | 38344.5 | 89470.5 | 86275.125 | 76689 | 17967.0328 | 8760 | 1720.1251 | 17992.6568 | 0 | 0 | 673.0013 | 4887.521 | 3269.9234 | -1501.2234 | 5568.8849 | 3527.7882 | 8760 | 6319.2328 | 2390.4593 | 3928.7735 | 6320.3721 | 8635.9087 | 4382.3512 | 14819.6837 | 8729.1983 | 0 | 14984.4172 | 8760 | 0 | 410.025 | 229.05 | 1854.725 | 2041013.6598 | 178372.614 | 2634.625 | -27.5509
12 | C | SOK | NAP | CC | ET | HC | R10 | 2.9609 | 35 | 2.625 | 8760 | 171499.5614 | 0 | 113591.9331 | 65533.1035 | 103333.9419 | 38352 | 89488 | 86292 | 76704 | 21211.6906 | 8760 | 1720.1251 | 18953.2736 | 0 | 0 | 659.5897 | 4593.7879 | 2741.3825 | -1509.5122 | 6080.8279 | 3507.869 | 8760 | 6319.1949 | 1994.0661 | 4325.1288 | 6320.3721 | 8635.9087 | 4378.754 | 14819.281 | 8734.9224 | 0 | 15961.9809 | 8760 | 0 | 441.475 | 197.725 | 1854.725 | 2041024.9772 | 178372.614 | 2568.275 | -29.616
13 | C | SOK | NAP | CC | ET | HC | R10 | 2.9609 | 41 | 1.025 | 8760 | 152370.5715 | 0 | 117811.9017 | 65533.1035 | 103333.9419 | 38017.5 | 88707.5 | 85539.375 | 76035 | 25723.8962 | 8760 | 1720.1251 | 17257.0137 | 0 | 0 | 679.5812 | 4919.338 | 3565.9683 | -1486.1415 | 5272.217 | 3539.5582 | 8760 | 6318.851 | 2623.3297 | 3695.5213 | 6320.3721 | 8635.9087 | 4377.1868 | 14826.8852 | 8723.3735 | 0 | 14259.6489 | 8760 | 0 | 388.65 | 244.975 | 1854.725 | 2040977.5637 | 178372.614 | 2889.325 | -12.7406
14 | C | SOK | NAP | CC | ET | HC | R10 | 2.9609 | 41 | 2.05 | 8760 | 165409.8207 | 0 | 112266.0215 | 65533.1035 | 103333.9419 | 37921.5 | 88483.5 | 85323.375 | 75843 | 22929.6641 | 8760 | 1720.1251 | 19067.7173 | 0 | 0 | 600.6025 | 4400.0521 | 2781.8799 | -1535.5051 | 6037.7174 | 3537.1857 | 8760 | 6319.3841 | 2041.275 | 4278.1091 | 6320.3721 | 8635.9087 | 4405.6148 | 14832.5489 | 8732.4463 | 0 | 16008.9703 | 8760 | 0 | 437.4 | 194.625 | 1854.725 | 2041083.6736 | 178372.614 | 2771.875 | -10.2882
15 | C | SOK | NAP | CC | ET | HC | R10 | 2.9609 | 41 | 3.075 | 8760 | 173606.0635 | 0 | 108685.7602 | 65533.1035 | 103333.9419 | 37812 | 88228 | 85077 | 75624 | 21673.792 | 8760 | 1720.1251 | 20204.0143 | 0 | 0 | 590.2388 | 4007.3864 | 2171.5373 | -1545.7482 | 6635.067 | 3519.9049 | 8760 | 6319.0299 | 1586.0594 | 4732.9705 | 6320.3721 | 8635.9087 | 4403.395 | 14835.3503 | 8741.4221 | 0 | 17158.1613 | 8760 | 0 | 474.55 | 155.65 | 1854.725 | 2040988.8735 | 178372.614 | 2700.475 | -14.3851
16 | C | SOK | NAP | CC | ET | HC | R600 | 3.4774 | 16.5 | 0.413 | 8760 | 168288.5741 | 0 | 127019.0379 | 65533.1035 | 61057.895 | 45118.5 | 105276.5 | 101516.625 | 90237 | 25631.9107 | 8760 | 1720.1251 | 12115.6345 | 0 | 0 | 979.4479 | 3670.9708 | 6714.8097 | -1331.1383 | 3205.9095 | 3291.3444 | 8760 | 7059.0544 | 4839.2129 | 2219.8415 | 7066.0392 | 4399.3257 | 4802.1719 | 16478.7636 | 9682.3978 | 0 | 9505.3059 | 8760 | 0 | 262.975 | 489 | 2104.7 | 2265085.0118 | 155104.6653 | 2069.075 | -46.8648
17 | C | SOK | NAP | CC | ET | HC | R600 | 3.4774 | 16.5 | 0.825 | 8760 | 175303.6279 | 0 | 124733.1903 | 65533.1035 | 61057.895 | 45318 | 105742 | 101965.5 | 90636 | 22290.2109 | 8760 | 1720.1251 | 12728.2758 | 0 | 0 | 857.04 | 3505.1681 | 6670.9068 | -1393.8752 | 3248.2982 | 3298.6294 | 8760 | 7058.4197 | 4796.0577 | 2262.362 | 7066.0392 | 4399.3257 | 4884.844 | 16483.1013 | 9685.3706 | 0 | 10083.0397 | 8760 | 0 | 264.675 | 490.625 | 2104.7 | 2265136.3718 | 155104.6653 | 1976.55 | -39.1454
18 | C | SOK | NAP | CC | ET | HC | R600 | 3.4774 | 16.5 | 1.238 | 8760 | 178741.2365 | 0 | 123351.7824 | 65533.1035 | 61057.895 | 45366 | 105854 | 102073.5 | 90732 | 21693.199 | 8760 | 1720.1251 | 13007.7141 | 0 | 0 | 865.8042 | 3394.6981 | 6568.3609 | -1411.2558 | 3348.0238 | 3302.1075 | 8760 | 7058.1114 | 4712.3768 | 2345.7347 | 7066.0392 | 4399.3257 | 4898.6964 | 16481.5913 | 9687.01 | 0 | 10359.3392 | 8760 | 0 | 268.975 | 487.125 | 2104.7 | 2265133.548 | 155104.6653 | 1931.175 | -38.9357
19 | C | SOK | NAP | CC | ET | HC | R600 | 3.4774 | 22.5 | 0.563 | 8760 | 164806.5403 | 0 | 119828.5173 | 65533.1035 | 61057.895 | 43914 | 102466 | 98806.5 | 87828 | 12332.658 | 8760 | 1720.1251 | 14438.2502 | 0 | 0 | 807.1308 | 3262.712 | 5683.4952 | -1424.3952 | 4224.0275 | 3420.3896 | 8760 | 7057.8874 | 4125.9701 | 2931.9173 | 7066.0392 | 4399.3257 | 4892.6607 | 16501.1676 | 9691.0573 | 0 | 11592.8337 | 8760 | 0 | 333.825 | 398.075 | 2104.7 | 2265166.2293 | 155104.6653 | 2306.8 | -16.9472
20 | C | SOK | NAP | CC | ET | HC | R600 | 3.4774 | 22.5 | 1.125 | 8760 | 173097.6452 | 0 | 116141.0131 | 65533.1035 | 61057.895 | 43969.5 | 102595.5 | 98931.375 | 87939 | 11331.8867 | 8760 | 1720.1251 | 15316.7245 | 0 | 0 | 700.0912 | 3026.9153 | 5351.5938 | -1483.3799 | 4535.9793 | 3434.3082 | 8760 | 7058.5389 | 3881.6897 | 3176.8492 | 7066.0392 | 4399.3257 | 4950.7045 | 16503.3667 | 9697.9094 | 0 | 12429.3773 | 8760 | 0 | 352.025 | 380.8 | 2104.7 | 2265075.9532 | 155104.6653 | 2205.7 | -13.0657
21 | C | SOK | NAP | CC | ET | HC | R600 | 3.4774 | 22.5 | 1.688 | 8760 | 177623.0146 | 0 | 114104.1489 | 65533.1035 | 61057.895 | 43932 | 102508 | 98847 | 87864 | 11399.0024 | 8760 | 1720.1251 | 15777.4212 | 0 | 0 | 693.9406 | 2858.1712 | 5079.962 | -1495.5788 | 4796.1832 | 3432.9062 | 8760 | 7059.7676 | 3676.866 | 3382.9016 | 7066.0392 | 4399.3257 | 4954.7097 | 16503.4388 | 9702.4635 | 0 | 12888.7028 | 8760 | 0 | 365.55 | 366.65 | 2104.7 | 2265212.3802 | 155104.6653 | 2151.25 | -18.5414
22 | C | SOK | NAP | CC | ET | HC | R600 | 3.4774 | 29 | 0.725 | 8760 | 156459.2756 | 0 | 114377.1307 | 65533.1035 | 61057.895 | 43369.5 | 101195.5 | 97581.375 | 86739 | 18136.3614 | 8760 | 1720.1251 | 15515.2351 | 0 | 0 | 673.3757 | 2897.6917 | 5194.4766 | -1489.6963 | 4765.2592 | 3485.2583 | 8760 | 7061.1517 | 3729.4615 | 3331.6902 | 7066.0392 | 4399.3257 | 4949.5824 | 16468.6619 | 9691.1508 | 0 | 12562.8735 | 8760 | 0 | 366.775 | 356.05 | 2104.7 | 2265197.6672 | 155104.6653 | 2574.025 | -87.5513
23 | C | SOK | NAP | CC | ET | HC | R600 | 3.4774 | 29 | 1.45 | 8760 | 166757.615 | 0 | 109669.6946 | 65533.1035 | 61057.895 | 43095 | 100555 | 96963.75 | 86190 | 13721.5016 | 8760 | 1720.1251 | 16720.6585 | 0 | 0 | 597.232 | 2597.759 | 4531.0346 | -1544.1912 | 5369.7117 | 3503.0761 | 8760 | 7061.4053 | 3271.8509 | 3789.5544 | 7066.0392 | 4399.3257 | 4997.1963 | 16482.3187 | 9702.0309 | 0 | 13700.2336 | 8760 | 0 | 402.425 | 315.825 | 2104.7 | 2265122.6967 | 155104.6653 | 2460.875 | -70.5336
24 | C | SOK | NAP | CC | ET | HC | R600 | 3.4774 | 29 | 2.175 | 8760 | 172697.2935 | 0 | 106825.1342 | 65533.1035 | 61057.895 | 43098 | 100562 | 96970.5 | 86196 | 15646.3169 | 8760 | 1720.1251 | 17445.5595 | 0 | 0 | 579.851 | 2379.4795 | 4099.2769 | -1557.5429 | 5790.1249 | 3498.7051 | 8760 | 7062.0818 | 2945.7433 | 4116.3385 | 7066.0392 | 4399.3257 | 5002.0827 | 16474.3454 | 9707.2639 | 0 | 14426.5466 | 8760 | 0 | 427.875 | 290.425 | 2104.7 | 2265188.5049 | 155104.6653 | 2399.825 | -85.1391
25 | C | SOK | NAP | CC | ET | HC | R60 | 3.4774 | 35 | 0.875 | 8760 | 151316.3951 | 0 | 109844.4329 | 65533.1035 | 61057.895 | 42349.5 | 98815.5 | 95286.375 | 84699 | 19348.9696 | 8760 | 1720.1251 | 16133.4192 | 0 | 0 | 587.6329 | 2590.192 | 4572.6603 | -1531.9525 | 5293.6535 | 3517.2347 | 8760 | 7064.6418 | 3354.611 | 3710.0308 | 7066.0392 | 4399.3257 | 4983.8433 | 16527.5019 | 9703.4525 | 0 | 13102.2331 | 8760 | 0 | 393.525 | 312.3 | 2104.7 | 2265252.7319 | 155104.6653 | 2773.175 | -24.6165
26 | C | SOK | NAP | CC | ET | HC | R60 | 3.4774 | 35 | 1.75 | 8760 | 163777.3766 | 0 | 104805.5188 | 65533.1035 | 61057.895 | 42163.5 | 98381.5 | 94867.875 | 84327 | 14844.6081 | 8760 | 1720.1251 | 17722.9591 | 0 | 0 | 512.3277 | 2246.6308 | 3817.913 | -1581.8718 | 6027.1514 | 3530.7592 | 8760 | 7064.7458 | 2796.5522 | 4268.1936 | 7066.0392 | 4399.3257 | 5021.2783 | 16533.3464 | 9713.5743 | 0 | 14617.9092 | 8760 | 0 | 438.65 | 264.075 | 2104.7 | 2265258.658 | 155104.6653 | 2650.925 | -17.5252
27 | C | SOK | NAP | CC | ET | HC | R60 | 3.4774 | 35 | 2.625 | 8760 | 171754.884 | 0 | 101477.9907 | 65533.1035 | 61057.895 | 42138 | 98322 | 94810.5 | 84276 | 18826.3035 | 8760 | 1720.1251 | 18761.1451 | 0 | 0 | 479.8371 | 2019.8435 | 3225.1285 | -1595.4083 | 6607.1848 | 3528.7198 | 8760 | 7064.8067 | 2348.9514 | 4715.8553 | 7066.0392 | 4399.3257 | 5027.8152 | 16527.3742 | 9719.2014 | 0 | 15652.8195 | 8760 | 0 | 474.4 | 227.9 | 2104.7 | 2265189.2493 | 155104.6653 | 2576.775 | -26.4216
28 | C | SOK | NAP | CC | ET | HC | R60 | 3.4774 | 41 | 1.025 | 8760 | 150999.1033 | 0 | 106423.911 | 65533.1035 | 61057.895 | 41944.5 | 97870.5 | 94375.125 | 83889 | 27247.8607 | 8760 | 1720.1251 | 16877.9773 | 0 | 0 | 508.3172 | 2329.9778 | 4213.2243 | -1567.227 | 5635.7941 | 3522.8928 | 8760 | 7064.3703 | 3098.8829 | 3965.4874 | 7066.0392 | 4399.3257 | 5013.2202 | 16534.4667 | 9704.3578 | 0 | 13807.6989 | 8760 | 0 | 412.4 | 286.675 | 2104.7 | 2265287.1115 | 155104.6653 | 2912.525 | -11.6224
29 | C | SOK | NAP | CC | ET | HC | R60 | 3.4774 | 41 | 2.05 | 8760 | 163641.484 | 0 | 101009.2719 | 65533.1035 | 61057.895 | 41725.5 | 97359.5 | 93882.375 | 83451 | 20503.1511 | 8760 | 1720.1251 | 18605.6072 | 0 | 0 | 438.9199 | 1926.6624 | 3311.9335 | -1610.2451 | 6511.1144 | 3532.9813 | 8760 | 7064.5697 | 2435.5335 | 4629.0362 | 7066.0392 | 4399.3257 | 5040.0663 | 16539.4519 | 9716.9582 | 0 | 15460.2059 | 8760 | 0 | 466.8 | 228.625 | 2104.7 | 2265254.1491 | 155104.6653 | 2800.775 | -9.7784
30 | C | SOK | NAP | CC | ET | HC | R60 | 3.4774 | 41 | 3.075 | 8760 | 172465.9342 | 0 | 97674.2443 | 65533.1035 | 61057.895 | 41602.5 | 97072.5 | 93605.625 | 83205 | 20394.4707 | 8760 | 1720.1251 | 19831.0249 | 0 | 0 | 394.3172 | 1702.6164 | 2608.3623 | -1628.0982 | 7203.6492 | 3537.9857 | 8760 | 7065.7175 | 1906.3558 | 5159.3616 | 7066.0392 | 4399.3257 | 5053.4147 | 16545.2964 | 9726.9021 | 0 | 16670.5597 | 8760 | 0 | 508.95 | 184.425 | 2104.7 | 2265358.3481 | 155104.6653 | 2726.025 | -13.3511
31 | C | SOK | NAP | CC | ET | WC | R100 | 4.1884 | 23 | 0.6 | 8760 | 183236.9578 | 0 | 149486.7899 | 65533.1035 | 121436.5822 | 64561.5 | 204444.75 | 145263.375 | 129123 | 162311.6622 | 8760 | 1720.1251 | 15019.849 | 0 | 0 | 1402.687 | 10029.1947 | 8425.5424 | -1307.8812 | 4387.333 | 3311.1554 | 8760 | 8931.5675 | 5887.7694 | 3043.7981 | 8940.7124 | 12216.2389 | 5513.0763 | 21699.2099 | 12612.9585 | 0 | 12585.4934 | 8760 | 25846.4739 | 364.025 | 712 | 1854.725 | 2920478.0268 | 178372.614 | 2111.95
32 | C | SOK | NAP | CC | ET | WC | R100 | 4.1884 | 23 | 1.15 | 8760 | 189943.6077 | 0 | 146185.51 | 65533.1035 | 121436.5822 | 64636.5 | 204682.25 | 145432.125 | 129273 | 164279.6912 | 8760 | 1720.1251 | 15683.9711 | 0 | 0 | 1300.0792 | 9707.3804 | 8271.6693 | -1349.2123 | 4525.6819 | 3298.4587 | 8760 | 8931.5877 | 5821.481 | 3110.1067 | 8940.7124 | 12216.2389 | 5568.1642 | 21702.6522 | 12617.8031 | 0 | 13262.4611 | 8760 | 25859.4377 | 387.075 | 690.2 | 1854.725 | 2920470.4918 | 178372.614 | 2033.65
33 | C | SOK | NAP | CC | ET | WC | R100 | 4.1884 | 23 | 1.75 | 8760 | 192890.1105 | 0 | 145081.5836 | 65533.1035 | 121436.5822 | 64807.5 | 205223.75 | 145816.875 | 129615 | 164448.9371 | 8760 | 1720.1251 | 15954.7479 | 0 | 0 | 1301.9514 | 9549.0919 | 8217.3492 | -1366.2372 | 4589.2368 | 3296.1491 | 8760 | 8931.567 | 5810.1523 | 3121.4147 | 8940.7124 | 12216.2389 | 5581.6619 | 21718.8102 | 12635.26 | 0 | 13533.6138 | 8760 | 25881.4743 | 401.5 | 678.625 | 1854.725 | 2920454.0687 | 178372.614 | 2000.95
34 | C | SOK | NAP | CC | ET | WC | R100 | 4.1884 | 32 | 0.8 | 8760 | 183236.502 | 0 | 140775.3707 | 65533.1035 | 121436.5822 | 64294.5 | 203599.25 | 144662.625 | 128589 | 158143.2954 | 8760 | 1720.1251 | 17502.4355 | 0 | 0 | 1221.1865 | 9117.5865 | 7265.361 | -1383.7791 | 5601.9236 | 3415.1352 | 8760 | 8931.536 | 5093.3966 | 3838.1394 | 8940.7124 | 12216.2389 | 5594.6528 | 21784.6708 | 12695.3838 | 0 | 14917.5579 | 8760 | 25896.5663 | 462.175 | 609.4 | 1854.725 | 2920533.8086 | 178372.614 | 2380.1
35 | C | SOK | NAP | CC | ET | WC | R100 | 4.1884 | 32 | 1.6 | 8760 | 192397.8436 | 0 | 136131.6803 | 65533.1035 | 121436.5822 | 64419 | 203993.5 | 144942.75 | 128838 | 161555.0484 | 8760 | 1720.1251 | 18593.6953 | 0 | 0 | 1110.8733 | 8613.8504 | 6875.411 | -1425.1905 | 5974.0402 | 3406.6647 | 8760 | 8936.6531 | 4900.272 | 4036.3811 | 8940.7124 | 12216.2389 | 5634.7321 | 21815.1099 | 12725.0751 | 0 | 16018.1133 | 8760 | 25943.6511 | 512.475 | 561.175 | 1854.725 | 2920700.6559 | 178372.614 | 2286.25
36 | C | SOK | NAP | CC | ET | WC | R100 | 4.1884 | 32 | 2.4 | 8760 | 197143.6295 | 0 | 134079.0672 | 65533.1035 | 121436.5822 | 64530 | 204345 | 145192.5 | 129060 | 161529.7318 | 8760 | 1720.1251 | 19142.1529 | 0 | 0 | 1126.0499 | 8412.7281 | 6559.1929 | -1437.0509 | 6291.3389 | 3395.8484 | 8760 | 8937.5017 | 4715.015 | 4222.4866 | 8940.7124 | 12216.2389 | 5637.5153 | 21825.2691 | 12737.9111 | 0 | 16572.1578 | 8760 | 25971.1708 | 552.125 | 523.375 | 1854.725 | 2920666.0753 | 178372.614 | 2241.6
37 | C | SOK | NAP | CC | ET | WC | R100 | 4.1884 | 40.5 | 1 | 8760 | 185632.534 | 0 | 134413.5449 | 65533.1035 | 121436.5822 | 63832.5 | 202136.25 | 143623.125 | 127665 | 152952.9822 | 8760 | 1720.1251 | 19070.6261 | 0 | 0 | 1091.2469 | 8332.4037 | 6519.9923 | -1431.5277 | 6369.5868 | 3460.692 | 8760 | 8936.7034 | 4606.6156 | 4330.0877 | 8940.7124 | 12216.2389 | 5638.8893 | 21852.2576 | 12763.4564 | 0 | 16405.0284 | 8760 | 25934.0314 | 520.45 | 543.425 | 1854.725 | 2920676.4343 | 178372.614 | 2584.575
38 | C | SOK | NAP | CC | ET | WC | R100 | 4.1884 | 40.5 | 2.05 | 8760 | 197675.1007 | 0 | 128580.4338 | 65533.1035 | 121436.5822 | 64084.5 | 202934.25 | 144190.125 | 128169 | 156366.9521 | 8760 | 1720.1251 | 20628.8237 | 0 | 0 | 984.3652 | 7705.631 | 5863.6625 | -1472.8728 | 7034.8928 | 3452.3312 | 8760 | 8936.486 | 4223.2751 | 4713.2109 | 8940.7124 | 12216.2389 | 5674.9616 | 21882.6423 | 12799.4433 | 0 | 17967.6326 | 8760 | 25988.9993 | 602.65 | 465.425 | 1854.725 | 2920732.9218 | 178372.614 | 2475.475
39 | C | SOK | NAP | CC | ET | WC | R100 | 4.1884 | 40.5 | 3.05 | 8760 | 204220.9974 | 0 | 124917.678 | 65533.1035 | 121436.5822 | 64099.5 | 202981.75 | 144223.875 | 128199 | 157105.2674 | 8760 | 1720.1251 | 21493.4711 | 0 | 0 | 1011.5856 | 7417.7705 | 5329.2378 | -1481.1361 | 7576.8826 | 3435.8815 | 8760 | 8940.4773 | 3874.6661 | 5065.8112 | 8940.7124 | 12216.2389 | 5669.2888 | 21905.0823 | 12817.0272 | 0 | 18841.057 | 8760 | 26042.5278 | 657.65 | 410.675 | 1854.725 | 2920768.6403 | 178372.614 | 2421.75
40 | C | SOK | NAP | CC | ET | WC | R10 | 4.1884 | 49 | 1.25 | 8760 | 193260.2019 | 0 | 128606.682 | 65533.1035 | 121436.5822 | 63547.5 | 201233.75 | 142981.875 | 127095 | 148533.8743 | 8760 | 1720.1251 | 20530.5539 | 0 | 0 | 982.0313 | 7588.1447 | 5960.1622 | -1472.4399 | 6961.8972 | 3486.7359 | 8760 | 8939.6308 | 4239.2647 | 4700.3661 | 8940.7124 | 12216.2389 | 5677.8626 | 21900.1108 | 12811.6464 | 0 | 17807.7408 | 8760 | 25972.3023 | 570.55 | 488.575 | 1854.725 | 2920828.7584 | 178372.614 | 2728.725
41 | C | SOK | NAP | CC | ET | WC | R10 | 4.1884 | 49 | 2.45 | 8760 | 206475.657 | 0 | 122117.3647 | 65533.1035 | 121436.5822 | 63784.5 | 201984.25 | 143515.125 | 127569 | 150068.5087 | 8760 | 1720.1251 | 22343.8743 | 0 | 0 | 904.5593 | 6902.3574 | 5120.167 | -1509.2844 | 7817.0048 | 3468.2071 | 8760 | 8939.4196 | 3712.3829 | 5227.0367 | 8940.7124 | 12216.2389 | 5703.731 | 21931.4779 | 12848.5736 | 0 | 19634.1523 | 8760 | 26034.0322 | 665.8 | 397.275 | 1854.725 | 2920865.79 | 178372.614 | 2625.475
42 | C | SOK | NAP | CC | ET | WC | R10 | 4.1884 | 49 | 3.7 | 8760 | 215123.981 | 0 | 117850.1492 | 65533.1035 | 121436.5822 | 64072.5 | 202896.25 | 144163.125 | 128145 | 151032.1454 | 8760 | 1720.1251 | 23530.4313 | 0 | 0 | 879.0462 | 6518.2447 | 4420.4942 | -1516.386 | 8531.2847 | 3448.2178 | 8760 | 8940.0992 | 3239.8453 | 5700.254 | 8940.7124 | 12216.2389 | 5696.5865 | 21964.6223 | 12883.5173 | 0 | 20828.9698 | 8760 | 26100.7002 | 734.425 | 333.45 | 1854.725 | 2920841.4996 | 178372.614 | 2559.65
43 | C | SOK | NAP | CC | ET | WC | R10 | 4.1884 | 58 | 1.45 | 8760 | 203562.3569 | 0 | 124045.4861 | 65533.1035 | 121436.5822 | 63508.5 | 201110.25 | 142894.125 | 127017 | 144129.7365 | 8760 | 1720.1251 | 21789.5821 | 0 | 0 | 890.2363 | 6960.1853 | 5551.6743 | -1502.8372 | 7397.127 | 3481.3316 | 8760 | 8939.5676 | 3966.2029 | 4973.3648 | 8940.7124 | 12216.2389 | 5705.0032 | 21935.1026 | 12848.4402 | 0 | 19043.7341 | 8760 | 26010.0625 | 608.625 | 449.85 | 1854.725 | 2920833.0051 | 178372.614 | 2861.15
44 | C | SOK | NAP | CC | ET | WC | R10 | 4.1884 | 58 | 2.9 | 8760 | 219088.5872 | 0 | 116744.7229 | 65533.1035 | 121436.5822 | 63825 | 202112.5 | 143606.25 | 127650 | 145390.1564 | 8760 | 1720.1251 | 23936.8176 | 0 | 0 | 794.1125 | 6205.1369 | 4498.1483 | -1543.1504 | 8472.0985 | 3473.4444 | 8760 | 8940.819 | 3283.4049 | 5657.4141 | 8940.7124 | 12216.2389 | 5735.4118 | 21978.3448 | 12899.2972 | 0 | 21192.9751 | 8760 | 26088.2136 | 720.175 | 343.575 | 1854.725 | 2920952.0373 | 178372.614 | 2753.625
45 | C | SOK | NAP | CC | ET | WC | R10 | 4.1884 | 58 | 4.35 | 8760 | 229810.9886 | 0 | 112574.2509 | 65533.1035 | 121436.5822 | 64339.5 | 203741.75 | 144763.875 | 128679 | 145904.2851 | 8760 | 1720.1251 | 25406.9091 | 0 | 0 | 768.7101 | 5705.9024 | 3646.3679 | -1552.693 | 9351.886 | 3459.2458 | 8760 | 8940.1244 | 2687.0136 | 6253.1108 | 8940.7124 | 12216.2389 | 5733.6573 | 22027.4568 | 12951.7391 | 0 | 22666.5838 | 8760 | 26176.5348 | 799.125 | 273.2 | 1854.725 | 2920792.0614 | 178372.614 | 2680.6
46 | C | SOK | NAP | CC | ET | WC | R600 | 4.9191 | 23 | 0.6 | 8760 | 185683.9316 | 0 | 136556.152 | 65533.1035 | 70239.375 | 72817.5 | 230588.75 | 163839.375 | 145635 | 170870.8435 | 8760 | 1720.1251 | 15133.6311 | 0 | 0 | 1193.517 | 5084.9899 | 9716.9378 | -1368.3226 | 4642.6289 | 3293.5931 | 8760 | 9992.0186 | 6777.9932 | 3214.0254 | 9995.5229 | 6223.2263 | 6206.0727 | 24286.7844 | 14133.7778 | 0 | 12636.9986 | 8760 | 28820.3706 | 386.8 | 826.825 | 2104.7 | 3240421.5196 | 155104.6653 | 2089.5
47 | C | SOK | NAP | CC | ET | WC | R600 | 4.9191 | 23 | 1.15 | 8760 | 192155.4391 | 0 | 133498.6058 | 65533.1035 | 70239.375 | 72810 | 230565 | 163822.5 | 145620 | 174402.9181 | 8760 | 1720.1251 | 15762.3948 | 0 | 0 | 1098.1862 | 4829.2601 | 9583.4652 | -1417.4551 | 4760.4229 | 3294.946 | 8760 | 9990.5121 | 6725.7913 | 3264.7208 | 9995.5229 | 6223.2263 | 6288.0296 | 24284.7152 | 14134.187 | 0 | 13262.7206 | 8760 | 28826.2534 | 407.975 | 805.525 | 2104.7 | 3240449.9065 | 155104.6653 | 2013.025
48 | C | SOK | NAP | CC | ET | WC | R600 | 4.9191 | 23 | 1.75 | 8760 | 195603.8765 | 0 | 131445.9927 | 65533.1035 | 70239.375 | 72987 | 231125.5 | 164220.75 | 145974 | 175117.8755 | 8760 | 1720.1251 | 16084.3449 | 0 | 0 | 1112.902 | 4661.2646 | 9482.6611 | -1431.6277 | 4865.6452 | 3296.1884 | 8760 | 9991.1497 | 6693.7633 | 3297.3865 | 9995.5229 | 6223.2263 | 6295.8594 | 24300.9978 | 14152.0334 | 0 | 13581.2324 | 8760 | 28850.597 | 429.075 | 787.375 | 2104.7 | 3240450.1149 | 155104.6653 | 1973.8
49 | C | SOK | NAP | CC | ET | WC | R600 | 4.9191 | 32 | 0.8 | 8760 | 184365.2677 | 0 | 128667.428 | 65533.1035 | 70239.375 | 72535.5 | 229695.75 | 163204.875 | 145071 | 166977.0766 | 8760 | 1720.1251 | 17399.4617 | 0 | 0 | 1017.2875 | 4507.2345 | 8513.6396 | -1454.2212 | 5908.3121 | 3406.6303 | 8760 | 9988.453 | 5954.228 | 4034.225 | 9995.5229 | 6223.2263 | 6317.7371 | 24370.5622 | 14219.6439 | 0 | 14742.2507 | 8760 | 28861.7162 | 490.575 | 718.35 | 2104.7 | 3240468.1312 | 155104.6653 | 2373.725
50 | C | SOK | NAP | CC | ET | WC | R600 | 4.9191 | 32 | 1.6 | 8760 | 193966.6827 | 0 | 124051.4857 | 65533.1035 | 70239.375 | 72594 | 229881 | 163336.5 | 145188 | 170606.8556 | 8760 | 1720.1251 | 18496.5243 | 0 | 0 | 903.0165 | 4157.2821 | 8006.5749 | -1505.6351 | 6397.1763 | 3417.3312 | 8760 | 9992.0756 | 5683.262 | 4308.8136 | 9995.5229 | 6223.2263 | 6378.4601 | 24399.84 | 14249.4718 | 0 | 15829.9624 | 8760 | 28911.3853 | 551.55 | 658.35 | 2104.7 | 3240518.8243 | 155104.6653 | 2275.425
51 | C | SOK | NAP | CC | ET | WC | R600 | 4.9191 | 32 | 2.4 | 8760 | 199986.4671 | 0 | 120921.9444 | 65533.1035 | 70239.375 | 72543 | 229719.5 | 163221.75 | 145086 | 171576.3214 | 8760 | 1720.1251 | 19201.3252 | 0 | 0 | 879.0286 | 3930.5644 | 7644.7752 | -1516.1905 | 6740.4572 | 3415.4171 | 8760 | 9993.7614 | 5479.9299 | 4513.8316 | 9995.5229 | 6223.2263 | 6378.8853 | 24405.322 | 14254.34 | 0 | 16529.1556 | 8760 | 28936.9666 | 593.6 | 615.45 | 2104.7 | 3240533.8997 | 155104.6653 | 2217.525
52 | C | SOK | NAP | CC | ET | WC | R600 | 4.9191 | 40.5 | 1 | 8760 | 185767.1979 | 0 | 122775.0708 | 65533.1035 | 70239.375 | 71994 | 227981 | 161986.5 | 143988 | 161811.7392 | 8760 | 1720.1251 | 18770.1325 | 0 | 0 | 878.3163 | 4066.2589 | 7643.0509 | -1509.3962 | 6798.6514 | 3459.2235 | 8760 | 9992.2445 | 5385.4607 | 4606.7838 | 9995.5229 | 6223.2263 | 6381.1983 | 24439.616 | 14290.0827 | 0 | 16025.2991 | 8760 | 28903.727 | 559.275 | 640.625 | 2104.7 | 3240535.5956 | 155104.6653 | 2591.15
53 | C | SOK | NAP | CC | ET | WC | R600 | 4.9191 | 40.5 | 2.05 | 8760 | 198199.9265 | 0 | 116525.7375 | 65533.1035 | 70239.375 | 72133.5 | 228422.75 | 162300.375 | 144267 | 165502.0715 | 8760 | 1720.1251 | 20306.7611 | 0 | 0 | 781.3672 | 3604.4983 | 6884.5769 | -1558.0727 | 7564.9909 | 3468.6254 | 8760 | 9992.8438 | 4933.2789 | 5059.5649 | 9995.5229 | 6223.2263 | 6434.7326 | 24470.5927 | 14323.5312 | 0 | 17547.0392 | 8760 | 28959.2022 | 650.25 | 551.975 | 2104.7 | 3240636.1645 | 155104.6653 | 2479.075
54 | C | SOK | NAP | CC | ET | WC | R600 | 4.9191 | 40.5 | 3.05 | 8760 | 206571.3917 | 0 | 112378.5139 | 65533.1035 | 70239.375 | 72180 | 228570 | 162405 | 144360 | 166141.6101 | 8760 | 1720.1251 | 21381.1971 | 0 | 0 | 759.0082 | 3295.6807 | 6271.8464 | -1567.2455 | 8182.1133 | 3461.4558 | 8760 | 9995.1367 | 4536.7454 | 5458.3914 | 9995.5229 | 6223.2263 | 6434.8144 | 24487.9027 | 14341.6784 | 0 | 18617.9956 | 8760 | 29007.1972 | 714.075 | 488.925 | 2104.7 | 3240607.8434 | 155104.6653 | 2407.95
55 | C | SOK | NAP | CC | ET | WC | R60 | 4.9191 | 49 | 1.25 | 8760 | 192127.3003 | 0 | 117898.146 | 65533.1035 | 70239.375 | 71892 | 227658 | 161757 | 143784 | 157482.5944 | 8760 | 1720.1251 | 19996.2517 | 0 | 0 | 766.3911 | 3642.9003 | 7006.8023 | -1553.6222 | 7474.6335 | 3483.0842 | 8760 | 9993.6687 | 4969.4471 | 5024.2217 | 9995.5229 | 6223.2263 | 6432.6967 | 24499.6524 | 14352.2479 | 0 | 17196.4 | 8760 | 28958.0301 | 618.975 | 579.225 | 2104.7 | 3240681.7754 | 155104.6653 | 2746.75
56 | C | SOK | NAP | CC | ET | WC | R60 | 4.9191 | 49 | 2.45 | 8760 | 206106.0107 | 0 | 111064.6016 | 65533.1035 | 70239.375 | 71898 | 227677 | 161770.5 | 143796 | 158479.6088 | 8760 | 1720.1251 | 21809.5738 | 0 | 0 | 682.3407 | 3141.5894 | 6047.4185 | -1592.7146 | 8441.2154 | 3489.7123 | 8760 | 9994.5818 | 4367.9848 | 5626.597 | 9995.5229 | 6223.2263 | 6466.7814 | 24521.6804 | 14380.4875 | 0 | 18994.3918 | 8760 | 29007.347 | 724.525 | 473.775 | 2104.7 | 3240531.882 | 155104.6653 | 2637.05
57 | C | SOK | NAP | CC | ET | WC | R60 | 4.9191 | 49 | 3.7 | 8760 | 216064.163 | 0 | 106468.9079 | 65533.1035 | 70239.375 | 72262.5 | 228831.25 | 162590.625 | 144525 | 159812.8656 | 8760 | 1720.1251 | 23117.4018 | 0 | 0 | 633.6092 | 2833.2332 | 5205.3211 | -1605.1664 | 9301.45 | 3479.5007 | 8760 | 9994.568 | 3797.6656 | 6196.9024 | 9995.5229 | 6223.2263 | 6473.8887 | 24562.9335 | 14423.1411 | 0 | 20301.2737 | 8760 | 29086.3192 | 806.775 | 397.6 | 2104.7 | 3240605.4996 | 155104.6653 | 2562.375
58 | C | SOK | NAP | CC | ET | WC | R60 | 4.9191 | 58 | 1.45 | 8760 | 201574.6644 | 0 | 113709.6752 | 65533.1035 | 70239.375 | 71769 | 227268.5 | 161480.25 | 143538 | 152371.7699 | 8760 | 1720.1251 | 21085.0769 | 0 | 0 | 676.9781 | 3270.2461 | 6523.263 | -1584.3744 | 7984.5858 | 3480.5878 | 8760 | 9995.9683 | 4652.0012 | 5343.9671 | 9995.5229 | 6223.2263 | 6467.2903 | 24539.594 | 14392.1466 | 0 | 18259.2036 | 8760 | 29001.9531 | 664.125 | 532.025 | 2104.7 | 3240629.874 | 155104.6653 | 2885.6
59 | C | SOK | NAP | CC | ET | WC | R60 | 4.9191 | 58 | 2.9 | 8760 | 218216.5748 | 0 | 106507.1554 | 65533.1035 | 70239.375 | 71971.5 | 227909.75 | 161935.875 | 143943 | 153460.3084 | 8760 | 1720.1251 | 23228.7925 | 0 | 0 | 576.4978 | 2698.4558 | 5319.1715 | -1620.9156 | 9204.4557 | 3482.2365 | 8760 | 9996.2137 | 3869.5918 | 6126.6218 | 9995.5229 | 6223.2263 | 6491.306 | 24580.1441 | 14439.174 | 0 | 20395.0351 | 8760 | 29078.0732 | 788.925 | 410.6 | 2104.7 | 3240664.7422 | 155104.6653 | 2769.175
60 | C | SOK | NAP | CC | ET | WC | R60 | 4.9191 | 58 | 4.35 | 8760 | 229361.9487 | 0 | 102089.1999 | 65533.1035 | 70239.375 | 72528 | 229672 | 163188 | 145056 | 153447.8636 | 8760 | 1720.1251 | 24739.2176 | 0 | 0 | 524.4031 | 2393.1537 | 4327.7258 | -1636.6473 | 10236.2577 | 3484.0185 | 8760 | 9995.6904 | 3165.5454 | 6830.145 | 9995.5229 | 6223.2263 | 6508.9208 | 24635.9362 | 14498.0907 | 0 | 21890.1502 | 8760 | 29174.9671 | 879.9 | 328.9 | 2104.7 | 3240643.8624 | 155104.6653 | 2696.4
61 | C | SOK | NAP | CC | FP | HC | R100 | 2.9609 | 16.5 | 0.413 | 8760 | 166705.5897 | 0 | 145806.0353 | 65533.1035 | 103333.9419 | 41742 | 97398 | 93919.5 | 83484 | 30436.2897 | 8760 | 1720.1251 | 10291.6127 | 0 | 0 | 1185.7815 | 7396.8985 | 6595.9217 | -1214.5924 | 2336.7292 | 2849.1976 | 8760 | 6309.9144 | 4704.7155 | 1605.1989 | 6320.3721 | 8635.9087 | 4209.025 | 14804.9632 | 8694.1879 | 0 | 8318.8216 | 8760 | 0 | 198.625 | 497.075 | 1854.725 | 2040823.7801 | 178372.614 | 2212.125 | -50.6992
62 | C | SOK | NAP | CC | FP | HC | R100 | 2.9609 | 16.5 | 0.825 | 8760 | 171203.1851 | 0 | 142731.9902 | 65533.1035 | 103333.9419 | 41815.5 | 97569.5 | 94084.875 | 83631 | 28838.8091 | 8760 | 1720.1251 | 10806.9893 | 0 | 0 | 1055.4487 | 7108.2346 | 6591.4097 | -1279.1513 | 2338.1939 | 2811.6316 | 8760 | 6309.3616 | 4692.7605 | 1616.6011 | 6320.3721 | 8635.9087 | 4261.6063 | 14806.8892 | 8696.2915 | 0 | 8870.7936 | 8760 | 0 | 195.675 | 501.25 | 1854.725 | 2040801.8881 | 178372.614 | 2180.825 | -47.246
63 | C | SOK | NAP | CC | FP | HC | R100 | 2.9609 | 16.5 | 1.238 | 8760 | 172529.3926 | 0 | 141406.0787 | 65533.1035 | 103333.9419 | 41883 | 97727 | 94236.75 | 83766 | 27822.5041 | 8760 | 1720.1251 | 11025.4133 | 0 | 0 | 1031.1986 | 6968.6363 | 6560.8591 | -1299.3729 | 2370.4936 | 2783.7352 | 8760 | 6309.4693 | 4662.9503 | 1646.519 | 6320.3721 | 8635.9087 | 4272.2001 | 14807.211 | 8697.7304 | 0 | 9113.2034 | 8760 | 0 | 196.6 | 501.45 | 1854.725 | 2040821.5162 | 178372.614 | 2181.25 | -47.8049
64 | C | SOK | NAP | CC | FP | HC | R100 | 2.9609 | 22.5 | 0.563 | 8760 | 168431.4937 | 0 | 138605.0154 | 65533.1035 | 103333.9419 | 40899 | 95431 | 92022.75 | 81798 | 17659.5105 | 8760 | 1720.1251 | 12260.9633 | 0 | 0 | 1022.7093 | 6820.5949 | 5768.2757 | -1299.8571 | 3146.3217 | 2919.2898 | 8760 | 6311.349 | 4148.1874 | 2163.1616 | 6320.3721 | 8635.9087 | 4268.4661 | 14829.7968 | 8705.1371 | 0 | 10167.6293 | 8760 | 0 | 259.45 | 422.2 | 1854.725 | 2040819.1236 | 178372.614 | 2387.075 | -23.8696
65 | C | SOK | NAP | CC | FP | HC | R100 | 2.9609 | 22.5 | 1.125 | 8760 | 172792.8762 | 0 | 134383.5469 | 65533.1035 | 103333.9419 | 40887 | 95403 | 91995.75 | 81774 | 17625.9658 | 8760 | 1720.1251 | 12977.4261 | 0 | 0 | 899.8921 | 6462.89 | 5598.2316 | -1361.0619 | 3308.5086 | 2877.783 | 8760 | 6310.6403 | 4012.9715 | 2297.6688 | 6320.3721 | 8635.9087 | 4305.193 | 14829.4288 | 8707.3968 | 0 | 10923.4118 | 8760 | 0 | 265.675 | 415.775 | 1854.725 | 2040875.5876 | 178372.614 | 2370.725 | -22.499
66 | C | SOK | NAP | CC | FP | HC | R100 | 2.9609 | 22.5 | 1.688 | 8760 | 174529.0655 | 0 | 132522.171 | 65533.1035 | 103333.9419 | 40924.5 | 95490.5 | 92080.125 | 81849 | 16317.4726 | 8760 | 1720.1251 | 13315.1704 | 0 | 0 | 883.638 | 6281.044 | 5446.6633 | -1378.9368 | 3458.3925 | 2850.0789 | 8760 | 6311.9393 | 3894.8771 | 2417.0622 | 6320.3721 | 8635.9087 | 4311.3655 | 14838.0144 | 8713.3617 | 0 | 11286.0758 | 8760 | 0 | 273.3 | 408.775 | 1854.725 | 2040861.66 | 178372.614 | 2371.15 | -18.3959
67 | C | SOK | NAP | CC | FP | HC | R100 | 2.9609 | 29 | 0.725 | 8760 | 167739.155 | 0 | 132495.1728 | 65533.1035 | 103333.9419 | 40444.5 | 94370.5 | 91000.125 | 80889 | 21312.7894 | 8760 | 1720.1251 | 13429.9133 | 0 | 0 | 894.8856 | 6268.6118 | 5289.6727 | -1363.6693 | 3636.9846 | 2961.3063 | 8760 | 6313.5381 | 3797.5321 | 2516.006 | 6320.3721 | 8635.9087 | 4307.7116 | 14808.6881 | 8705.2374 | 0 | 11260.4659 | 8760 | 0 | 293.775 | 380.3 | 1854.725 | 2040843.6088 | 178372.614 | 2578.4 | -66.1575
68 | C | SOK | NAP | CC | FP | HC | R100 | 2.9609 | 29 | 1.45 | 8760 | 172698.1949 | 0 | 127580.0005 | 65533.1035 | 103333.9419 | 40300.5 | 94034.5 | 90676.125 | 80601 | 20540.3133 | 8760 | 1720.1251 | 14395.0365 | 0 | 0 | 780.2572 | 5850.592 | 4882.2223 | -1420.8175 | 4011.4174 | 2913.0502 | 8760 | 6314.6247 | 3511.0358 | 2803.5888 | 6320.3721 | 8635.9087 | 4338.3074 | 14822.0803 | 8713.6116 | 0 | 12270.5658 | 8760 | 0 | 314.5 | 357.175 | 1854.725 | 2040866.8336 | 178372.614 | 2564.3 | -53.3789
69 | C | SOK | NAP | CC | FP | HC | R100 | 2.9609 | 29 | 2.175 | 8760 | 175693.6573 | 0 | 125475.6408 | 65533.1035 | 103333.9419 | 40300.5 | 94034.5 | 90676.125 | 80601 | 22625.806 | 8760 | 1720.1251 | 14939.4696 | 0 | 0 | 784.8332 | 5585.719 | 4621.9808 | -1435.8668 | 4268.0938 | 2881.7622 | 8760 | 6314.5821 | 3309.0256 | 3005.5566 | 6320.3721 | 8635.9087 | 4341.0707 | 14825.3186 | 8717.5173 | 0 | 12841.5165 | 8760 | 0 | 328.575 | 343.1 | 1854.725 | 2040820.8208 | 178372.614 | 2549.75 | -51.7047
70 | C | SOK | NAP | CC | FP | HC | R10 | 2.9609 | 35 | 0.875 | 8760 | 168264.5763 | 0 | 127875.4808 | 65533.1035 | 103333.9419 | 39829.5 | 92935.5 | 89616.375 | 79659 | 21058.8713 | 8760 | 1720.1251 | 14272.4611 | 0 | 0 | 811.5716 | 5848.6574 | 4811.3469 | -1406.5426 | 4061.0375 | 2968.4532 | 8760 | 6316.6529 | 3500.8666 | 2815.7863 | 6320.3721 | 8635.9087 | 4333.4412 | 14853.6313 | 8715.3212 | 0 | 12067.0968 | 8760 | 0 | 320.1 | 343.725 | 1854.725 | 2040985.7928 | 178372.614 | 2738.8 | -15.4781
71 | C | SOK | NAP | CC | FP | HC | R10 | 2.9609 | 35 | 1.75 | 8760 | 176064.619 | 0 | 122347.5993 | 65533.1035 | 103333.9419 | 39691.5 | 92613.5 | 89305.875 | 79383 | 19469.1873 | 8760 | 1720.1251 | 15617.8424 | 0 | 0 | 709.6924 | 5336.7536 | 4224.9981 | -1462.3583 | 4632.5624 | 2928.3919 | 8760 | 6317.9969 | 3064.8002 | 3253.1966 | 6320.3721 | 8635.9087 | 4360.9859 | 14853.9928 | 8724.3815 | 0 | 13448.0371 | 8760 | 0 | 354.175 | 307.35 | 1854.725 | 2040953.0954 | 178372.614 | 2694.25 | -21.0145
72 | C | SOK | NAP | CC | FP | HC | R10 | 2.9609 | 35 | 2.625 | 8760 | 180192.2568 | 0 | 118677.344 | 65533.1035 | 103333.9419 | 39658.5 | 92536.5 | 89231.625 | 79317 | 22782.3615 | 8760 | 1720.1251 | 16431.0195 | 0 | 0 | 707.6516 | 5010.1128 | 3801.2534 | -1474.4337 | 5040.0642 | 2889.8995 | 8760 | 6315.4954 | 2742.8875 | 3572.6079 | 6320.3721 | 8635.9087 | 4358.1756 | 14851.9079 | 8725.3719 | 0 | 14293.191 | 8760 | 0 | 377.325 | 283.65 | 1854.725 | 2040928.0448 | 178372.614 | 2674.45 | -18.0614
73 | C | SOK | NAP | CC | FP | HC | R10 | 2.9609 | 41 | 1.025 | 8760 | 172309.1892 | 0 | 124044.7362 | 65533.1035 | 103333.9419 | 39442.5 | 92032.5 | 88745.625 | 78885 | 21919.1633 | 8760 | 1720.1251 | 15115.4116 | 0 | 0 | 743.5011 | 5465.1955 | 4494.1057 | -1441.2247 | 4372.9584 | 2970.2908 | 8760 | 6318.2902 | 3277.0274 | 3041.2628 | 6320.3721 | 8635.9087 | 4354.5856 | 14863.4576 | 8719.5324 | 0 | 12885.464 | 8760 | 0 | 338.775 | 318.6 | 1854.725 | 2041016.3467 | 178372.614 | 2852.275 | -11.4517
74 | C | SOK | NAP | CC | FP | HC | R10 | 2.9609 | 41 | 2.05 | 8760 | 181517.6929 | 0 | 117760.1552 | 65533.1035 | 103333.9419 | 39235.5 | 91549.5 | 88279.875 | 78471 | 18483.0118 | 8760 | 1720.1251 | 16715.7155 | 0 | 0 | 646.6703 | 4902.4378 | 3699.52 | -1496.9148 | 5138.3576 | 2928.939 | 8760 | 6318.3018 | 2695.4459 | 3622.8559 | 6320.3721 | 8635.9087 | 4378.1487 | 14868.0645 | 8729.8058 | 0 | 14522.1552 | 8760 | 0 | 385.8 | 268.125 | 1854.725 | 2041049.8534 | 178372.614 | 2801.075 | -8.4125
75 | C | SOK | NAP | CC | FP | HC | R10 | 2.9609 | 41 | 3.075 | 8760 | 185635.2264 | 0 | 114202.3924 | 65533.1035 | 103333.9419 | 39213 | 91497 | 88229.25 | 78426 | 18215.1155 | 8760 | 1720.1251 | 17669.9861 | 0 | 0 | 623.7898 | 4554.474 | 3166.3788 | -1507.2115 | 5647.3285 | 2886.5093 | 8760 | 6317.6092 | 2301.7266 | 4015.8826 | 6320.3721 | 8635.9087 | 4373.6365 | 14869.5733 | 8736.9443 | 0 | 15509.3475 | 8760 | 0 | 416.475 | 237.075 | 1854.725 | 2041006.1911 | 178372.614 | 2788.3 | -11.8605
76 | C | SOK | NAP | CC | FP | HC | R600 | 3.4774 | 16.5 | 0.413 | 8760 | 168758.0202 | 0 | 130846.0327 | 65533.1035 | 61057.895 | 45835.5 | 106949.5 | 103129.875 | 91671 | 30332.1957 | 8760 | 1720.1251 | 10321.2074 | 0 | 0 | 1085.5661 | 3818.1148 | 7516.9637 | -1257.7017 | 2433.0942 | 2804.4122 | 8760 | 7057.7476 | 5380.9547 | 1676.7929 | 7066.0392 | 4399.3257 | 4750.4231 | 16524.442 | 9677.2114 | 0 | 8309.7014 | 8760 | 0 | 205 | 558.925 | 2104.7 | 2265113.3928 | 155104.6653 | 2192.125 | -47.1659
77 | C | SOK | NAP | CC | FP | HC | R600 | 3.4774 | 16.5 | 0.825 | 8760 | 173031.2454 | 0 | 128668.9279 | 65533.1035 | 61057.895 | 45936 | 107184 | 103356 | 91872 | 28083.6411 | 8760 | 1720.1251 | 10808.8632 | 0 | 0 | 904.42 | 3659.8509 | 7517.1928 | -1327.3807 | 2429.0793 | 2776.2861 | 8760 | 7056.8096 | 5370.944 | 1685.8657 | 7066.0392 | 4399.3257 | 4832.9689 | 16523.0871 | 9679.1572 | 0 | 8823.7362 | 8760 | 0 | 201.3 | 564.3 | 2104.7 | 2265079.8826 | 155104.6653 | 2165.975 | -43.9037
78 | C | SOK | NAP | CC | FP | HC | R600 | 3.4774 | 16.5 | 1.238 | 8760 | 173897.2125 | 0 | 127031.0371 | 65533.1035 | 61057.895 | 45967.5 | 107257.5 | 103426.875 | 91935 | 28314.176 | 8760 | 1720.1251 | 11003.9172 | 0 | 0 | 896.1423 | 3542.9094 | 7479.7777 | -1348.6224 | 2471.1841 | 2745.2989 | 8760 | 7056.6751 | 5332.68 | 1723.9951 | 7066.0392 | 4399.3257 | 4850.5112 | 16520.6684 | 9679.8049 | 0 | 9044.5485 | 8760 | 0 | 202.15 | 563.975 | 2104.7 | 2265047.7558 | 155104.6653 | 2179.2 | -46.0482
79 | C | SOK | NAP | CC | FP | HC | R600 | 3.4774 | 22.5 | 0.563 | 8760 | 169992.0941 | 0 | 125010.6718 | 65533.1035 | 61057.895 | 44935.5 | 104849.5 | 101104.875 | 89871 | 19215.5205 | 8760 | 1720.1251 | 12198.7492 | 0 | 0 | 881.1509 | 3497.3425 | 6630.821 | -1353.8243 | 3300.5581 | 2885.6537 | 8760 | 7058.7998 | 4780.6932 | 2278.1067 | 7066.0392 | 4399.3257 | 4841.9035 | 16543.279 | 9686.6816 | 0 | 10054.9497 | 8760 | 0 | 269.525 | 479.4 | 2104.7 | 2265106.8787 | 155104.6653 | 2378.55 | -24.0892
80 | C | SOK | NAP | CC | FP | HC | R600 | 3.4774 | 22.5 | 1.125 | 8760 | 174490.4768 | 0 | 121140.9298 | 65533.1035 | 61057.895 | 44914.5 | 104800.5 | 101057.625 | 89829 | 18796.2324 | 8760 | 1720.1251 | 12884.7166 | 0 | 0 | 756.2274 | 3260.0189 | 6427.513 | -1422.041 | 3493.6009 | 2850.5054 | 8760 | 7059.2995 | 4623.8155 | 2435.484 | 7066.0392 | 4399.3257 | 4907.73 | 16544.4973 | 9691.2966 | 0 | 10774.143 | 8760 | 0 | 277.525 | 471.05 | 2104.7 | 2265130.5731 | 155104.6653 | 2362.625 | -23.171
81 | C | SOK | NAP | CC | FP | HC | R600 | 3.4774 | 22.5 | 1.688 | 8760 | 176318.1349 | 0 | 119409.2952 | 65533.1035 | 61057.895 | 44932.5 | 104842.5 | 101098.125 | 89865 | 18353.1536 | 8760 | 1720.1251 | 13223.9719 | 0 | 0 | 740.1026 | 3091.9857 | 6266.4657 | -1438.5602 | 3647.1803 | 2819.5027 | 8760 | 7058.7123 | 4499.7275 | 2558.9848 | 7066.0392 | 4399.3257 | 4915.6679 | 16546.4365 | 9693.6853 | 0 | 11139.9515 | 8760 | 0 | 285.1 | 463.775 | 2104.7 | 2265163.1779 | 155104.6653 | 2362.25 | -20.0298
82 | C | SOK | NAP | CC | FP | HC | R600 | 3.4774 | 29 | 0.725 | 8760 | 168191.204 | 0 | 120076.7507 | 65533.1035 | 61057.895 | 44478 | 103782 | 100075.5 | 88956 | 22998.1355 | 8760 | 1720.1251 | 13207.5057 | 0 | 0 | 754.2267 | 3187.9387 | 6145.0508 | -1424.2643 | 3805.6713 | 2926.0711 | 8760 | 7058.9883 | 4417.8763 | 2641.1119 | 7066.0392 | 4399.3257 | 4905.4618 | 16517.9902 | 9683.805 | 0 | 10987.6267 | 8760 | 0 | 305.3 | 436 | 2104.7 | 2265128.4191 | 155104.6653 | 2585.65 | -64.1973
83 | C | SOK | NAP | CC | FP | HC | R600 | 3.4774 | 29 | 1.45 | 8760 | 174019.7928 | 0 | 115229.8239 | 65533.1035 | 61057.895 | 44268 | 103292 | 99603 | 88536 | 21981.6594 | 8760 | 1720.1251 | 14145.9283 | 0 | 0 | 646.4781 | 2905.7822 | 5639.9245 | -1488.5257 | 4262.1871 | 2891.5013 | 8760 | 7061.3729 | 4073.3595 | 2988.0134 | 7066.0392 | 4399.3257 | 4954.8646 | 16539.7908 | 9695.3488 | 0 | 11958.9381 | 8760 | 0 | 331.125 | 406.675 | 2104.7 | 2265162.5016 | 155104.6653 | 2562.85 | -44.3335
84 | C | SOK | NAP | CC | FP | HC | R600 | 3.4774 | 29 | 2.175 | 8760 | 177520.5867 | 0 | 112323.7676 | 65533.1035 | 61057.895 | 44305.5 | 103379.5 | 99687.375 | 88611 | 24695.7233 | 8760 | 1720.1251 | 14775.1276 | 0 | 0 | 628.6001 | 2645.5594 | 5362.3414 | -1501.5147 | 4538.1963 | 2852.4619 | 8760 | 7059.6231 | 3850.3826 | 3209.2406 | 7066.0392 | 4399.3257 | 4958.2655 | 16527.8887 | 9696.7411 | 0 | 12618.6334 | 8760 | 0 | 345.775 | 392.65 | 2104.7 | 2265027.8388 | 155104.6653 | 2545.3 | -57.7078
85 | C | SOK | NAP | CC | FP | HC | R60 | 3.4774 | 35 | 0.875 | 8760 | 168937.6273 | 0 | 115865.0315 | 65533.1035 | 61057.895 | 43788 | 102172 | 98523 | 87576 | 19687.8276 | 8760 | 1720.1251 | 13927.3281 | 0 | 0 | 671.5146 | 2945.7916 | 5587.5064 | -1472.1841 | 4306.0432 | 2942.4494 | 8760 | 7061.9965 | 4068.1923 | 2993.8041 | 7066.0392 | 4399.3257 | 4945.4857 | 16563.4384 | 9694.8231 | 0 | 11663.6457 | 8760 | 0 | 336.925 | 392.875 | 2104.7 | 2265256.4453 | 155104.6653 | 2740.5 | -16.6151
86 | C | SOK | NAP | CC | FP | HC | R60 | 3.4774 | 35 | 1.75 | 8760 | 175922.6917 | 0 | 110604.8822 | 65533.1035 | 61057.895 | 43635 | 101815 | 98178.75 | 87270 | 20757.4643 | 8760 | 1720.1251 | 15210.8072 | 0 | 0 | 584.7109 | 2599.1246 | 4936.37 | -1530.4873 | 4926.4249 | 2895.6474 | 8760 | 7063.8237 | 3594.4935 | 3469.3302 | 7066.0392 | 4399.3257 | 4986.6879 | 16566.5704 | 9704.6653 | 0 | 12987.4115 | 8760 | 0 | 373.925 | 353.325 | 2104.7 | 2265179.7713 | 155104.6653 | 2716.85 | -15.5734
87 | C | SOK | NAP | CC | FP | HC | R60 | 3.4774 | 35 | 2.625 | 8760 | 180933.4063 | 0 | 107029.1206 | 65533.1035 | 61057.895 | 43623 | 101787 | 98151.75 | 87246 | 22221.481 | 8760 | 1720.1251 | 16073.5268 | 0 | 0 | 553.9742 | 2327.4536 | 4464.1867 | -1543.7949 | 5394.0213 | 2862.3446 | 8760 | 7062.9937 | 3227.7457 | 3835.2479 | 7066.0392 | 4399.3257 | 4987.0323 | 16568.1776 | 9709.5558 | 0 | 13873.3396 | 8760 | 0 | 400.55 | 326.5 | 2104.7 | 2265233.6313 | 155104.6653 | 2687.975 | -15.8151
88 | C | SOK | NAP | CC | FP | HC | R60 | 3.4774 | 41 | 1.025 | 8760 | 172172.8011 | 0 | 112667.9947 | 65533.1035 | 61057.895 | 43342.5 | 101132.5 | 97520.625 | 86685 | 25161.9838 | 8760 | 1720.1251 | 14663.0754 | 0 | 0 | 613.294 | 2739.3562 | 5210.5173 | -1507.7168 | 4656.1318 | 2940.1197 | 8760 | 7063.2531 | 3811.0936 | 3252.1595 | 7066.0392 | 4399.3257 | 4974.1295 | 16565.5886 | 9696.9274 | 0 | 12377.1965 | 8760 | 0 | 357.15 | 365.225 | 2104.7 | 2265184.1228 | 155104.6653 | 2866.75 | -18.1243
89 | C | SOK | NAP | CC | FP | HC | R60 | 3.4774 | 41 | 2.05 | 8760 | 180409.8885 | 0 | 107173.111 | 65533.1035 | 61057.895 | 43167 | 100723 | 97125.75 | 86334 | 19534.443 | 8760 | 1720.1251 | 16169.3896 | 0 | 0 | 526.3879 | 2349.1157 | 4378.1318 | -1562.5686 | 5469.1001 | 2897.6422 | 8760 | 7064.8655 | 3197.1555 | 3867.71 | 7066.0392 | 4399.3257 | 5008.1758 | 16579.3058 | 9712.2377 | 0 | 13917.6943 | 8760 | 0 | 407.425 | 312.025 | 2104.7 | 2265269.7158 | 155104.6653 | 2835.175 | -10.1203
90 | C | SOK | NAP | CC | FP | HC | R60 | 3.4774 | 41 | 3.075 | 8760 | 186241.2818 | 0 | 102836.1502 | 65533.1035 | 61057.895 | 43075.5 | 100509.5 | 96919.875 | 86151 | 19342.0847 | 8760 | 1720.1251 | 17196.2446 | 0 | 0 | 483.7254 | 2049.242 | 3754.7252 | -1578.9076 | 6077.8057 | 2860.5791 | 8760 | 7064.3114 | 2727.6898 | 4336.6216 | 7066.0392 | 4399.3257 | 5014.1061 | 16582.517 | 9720.5067 | 0 | 14972.1641 | 8760 | 0 | 443.375 | 274.55 | 2104.7 | 2265314.1788 | 155104.6653 | 2803.7 | -10.6149
91 | C | SOK | NAP | CC | FP | WC | R100 | 4.1884 | 23 | 0.6 | 8760 | 179114.1729 | 0 | 152750.5723 | 65533.1035 | 121436.5822 | 64639.5 | 204691.75 | 145438.875 | 129279 | 161088.6392 | 8760 | 1720.1251 | 13583.7259 | 0 | 0 | 1458.7344 | 10229.5625 | 9128.6273 | -1263.1897 | 3689.7475 | 2904.5479 | 8760 | 8933.5532 | 6362.0082 | 2571.545 | 8940.7124 | 12216.2389 | 5477.6797 | 21686.13 | 12594.6162 | 0 | 11537.1011 | 8760 | 25828.3016 | 302.325 | 775 | 1854.725 | 2920645.481 | 178372.614 | 2282.475
92 | C | SOK | NAP | CC | FP | WC | R100 | 4.1884 | 23 | 1.15 | 8760 | 183304.9414 | 0 | 149456.7919 | 65533.1035 | 121436.5822 | 64632 | 204668 | 145422 | 129264 | 164289.0642 | 8760 | 1720.1251 | 14235.507 | 0 | 0 | 1323.8864 | 9830.3355 | 9100.2202 | -1318.0794 | 3710.0458 | 2866.1157 | 8760 | 8933.4599 | 6370.796 | 2562.6639 | 8940.7124 | 12216.2389 | 5541.7981 | 21688.1819 | 12597.3141 | 0 | 12222.9134 | 8760 | 25834.6531 | 311.175 | 766.025 | 1854.725 | 2920587.0577 | 178372.614 | 2260.625
93 | C | SOK | NAP | CC | FP | WC | R100 | 4.1884 | 23 | 1.75 | 8760 | 184702.8094 | 0 | 147472.4242 | 65533.1035 | 121436.5822 | 64662 | 204763 | 145489.5 | 129324 | 163870.527 | 8760 | 1720.1251 | 14515.317 | 0 | 0 | 1307.7934 | 9594.5633 | 9080.6592 | -1335.3631 | 3728.0463 | 2838.4716 | 8760 | 8935.5298 | 6381.0665 | 2554.4633 | 8940.7124 | 12216.2389 | 5554.9374 | 21699.1085 | 12606.8026 | 0 | 12526.9189 | 8760 | 25847.6521 | 318.275 | 759.425 | 1854.725 | 2920607.6535 | 178372.614 | 2258.55
94 | C | SOK | NAP | CC | FP | WC | R100 | 4.1884 | 32 | 0.8 | 8760 | 183205.9784 | 0 | 144902.3455 | 65533.1035 | 121436.5822 | 64446 | 204079 | 145003.5 | 128892 | 158879.5705 | 8760 | 1720.1251 | 15734.0105 | 0 | 0 | 1279.6155 | 9365.5096 | 8163.3441 | -1338.5643 | 4687.4374 | 2957.2521 | 8760 | 8933.555 | 5707.185 | 3226.37 | 8940.7124 | 12216.2389 | 5556.4719 | 21746.5361 | 12653.3882 | 0 | 13591.2219 | 8760 | 25860.3602 | 385.575 | 688.525 | 1854.725 | 2920619.7663 | 178372.614 | 2508.8
95 | C | SOK | NAP | CC | FP | WC | R100 | 4.1884 | 32 | 1.6 | 8760 | 188523.1535 | 0 | 139853.6821 | 65533.1035 | 121436.5822 | 64429.5 | 204026.75 | 144966.375 | 128859 | 161906.9781 | 8760 | 1720.1251 | 16796.4112 | 0 | 0 | 1133.056 | 8839.4858 | 7864.1778 | -1392.3489 | 4962.6803 | 2916.7888 | 8760 | 8935.7948 | 5572.1206 | 3363.6742 | 8940.7124 | 12216.2389 | 5605.6717 | 21762.5267 | 12669.2456 | 0 | 14686.6758 | 8760 | 25890.3339 | 425.925 | 647.9 | 1854.725 | 2920737.2182 | 178372.614 | 2488.725
96 | C | SOK | NAP | CC | FP | WC | R100 | 4.1884 | 32 | 2.4 | 8760 | 191336.0623 | 0 | 137300.8524 | 65533.1035 | 121436.5822 | 64492.5 | 204226.25 | 145108.125 | 128985 | 161687.3803 | 8760 | 1720.1251 | 17363.892 | 0 | 0 | 1114.5201 | 8577.2449 | 7640.4985 | -1409.2578 | 5187.0571 | 2885.5975 | 8760 | 8938.1067 | 5441.1775 | 3496.9292 | 8940.7124 | 12216.2389 | 5613.8558 | 21771.6361 | 12678.5822 | 0 | 15275.9152 | 8760 | 25914.9085 | 453.525 | 621.35 | 1854.725 | 2920674.2371 | 178372.614 | 2478.825
97 | C | SOK | NAP | CC | FP | WC | R100 | 4.1884 | 40.5 | 1 | 8760 | 190037.3782 | 0 | 138925.2441 | 65533.1035 | 121436.5822 | 64053 | 202834.5 | 144119.25 | 128106 | 156044.4087 | 8760 | 1720.1251 | 17272.145 | 0 | 0 | 1144.7173 | 8673.0811 | 7468.9838 | -1389.8836 | 5375.2256 | 2981.7898 | 8760 | 8937.9658 | 5269.0843 | 3668.8814 | 8940.7124 | 12216.2389 | 5604.2961 | 21796.6744 | 12701.536 | 0 | 15072.4726 | 8760 | 25890.3002 | 442.075 | 625.475 | 1854.725 | 2920791.3781 | 178372.614 | 2678.025
98 | C | SOK | NAP | CC | FP | WC | R100 | 4.1884 | 40.5 | 2.05 | 8760 | 197084.5907 | 0 | 132514.6715 | 65533.1035 | 121436.5822 | 64144.5 | 203124.25 | 144325.125 | 128289 | 158889.9617 | 8760 | 1720.1251 | 18745.788 | 0 | 0 | 1000.5052 | 8024.6606 | 6910.7142 | -1444.4194 | 5944.5062 | 2931.0873 | 8760 | 8937.8557 | 4943.1335 | 3994.7221 | 8940.7124 | 12216.2389 | 5649.3021 | 21816.6203 | 12724.5395 | 0 | 16583.5527 | 8760 | 25931.7819 | 513.15 | 555.925 | 1854.725 | 2920829.2965 | 178372.614 | 2651.275
99 | C | SOK | NAP | CC | FP | WC | R100 | 4.1884 | 40.5 | 3.05 | 8760 | 200906.4842 | 0 | 129055.9021 | 65533.1035 | 121436.5822 | 64356 | 203794 | 144801 | 128712 | 158704.0378 | 8760 | 1720.1251 | 19654.9257 | 0 | 0 | 1008.3502 | 7651.3739 | 6458.8525 | -1455.6872 | 6408.5531 | 2889.1359 | 8760 | 8938.0227 | 4652.789 | 4285.2336 | 8940.7124 | 12216.2389 | 5649.6176 | 21841.4853 | 12749.5258 | 0 | 17521.2492 | 8760 | 25981.6525 | 562.975 | 509.625 | 1854.725 | 2920810.6019 | 178372.614 | 2638.675
100 | C | SOK | NAP | CC | FP | WC | R10 | 4.1884 | 49 | 1.25 | 8760 | 198835.4036 | 0 | 133682.3436 | 65533.1035 | 121436.5822 | 63690 | 201685 | 143302.5 | 127380 | 152839.0905 | 8760 | 1720.1251 | 18561.3184 | 0 | 0 | 1034.9037 | 8042.4138 | 6976.262 | -1432.315 | 5892.5209 | 2972.3658 | 8760 | 8938.2735 | 4944.0769 | 3994.1966 | 8940.7124 | 12216.2389 | 5645.1173 | 21826.9082 | 12734.1264 | 0 | 16336.8344 | 8760 | 25906.4542 | 485.425 | 576.075 | 1854.725 | 2920785.5943 | 178372.614 | 2830.7
101 | C | SOK | NAP | CC | FP | WC | R10 | 4.1884 | 49 | 2.45 | 8760 | 208404.6153 | 0 | 126627.564 | 65533.1035 | 121436.5822 | 64084.5 | 202934.25 | 144190.125 | 128169 | 154555.6371 | 8760 | 1720.1251 | 20389.82 | 0 | 0 | 908.9283 | 7340.219 | 6178.233 | -1483.7883 | 6702.6934 | 2935.5054 | 8760 | 8938.249 | 4463.4464 | 4474.8026 | 8940.7124 | 12216.2389 | 5683.9851 | 21870.3633 | 12781.3995 | 0 | 18191.4776 | 8760 | 25981.7886 | 580.775 | 487.3 | 1854.725 | 2920730.4793 | 178372.614 | 2783.075
102 | C | SOK | NAP | CC | FP | WC | R10 | 4.1884 | 49 | 3.7 | 8760 | 213410.1155 | 0 | 121741.6397 | 65533.1035 | 121436.5822 | 64465.5 | 204140.75 | 145047.375 | 128931 | 153723.4398 | 8760 | 1720.1251 | 21612.3603 | 0 | 0 | 896.379 | 6867.1244 | 5483.3781 | -1490.7075 | 7422.2313 | 2880.0924 | 8760 | 8938.7683 | 3997.2094 | 4941.5588 | 8940.7124 | 12216.2389 | 5676.3223 | 21907.3342 | 12821.2779 | 0 | 19454.438 | 8760 | 26049.9519 | 652.975 | 421.45 | 1854.725 | 2920776.1453 | 178372.614 | 2765.6
103 | C | SOK | NAP | CC | FP | WC | R10 | 4.1884 | 58 | 1.45 | 8760 | 211995.6048 | 0 | 129595.8661 | 65533.1035 | 121436.5822 | 63835.5 | 202145.75 | 143629.875 | 127671 | 148463.0507 | 8760 | 1720.1251 | 19716.9326 | 0 | 0 | 954.4809 | 7499.4639 | 6564.8072 | -1462.0749 | 6333.0678 | 2959.6208 | 8760 | 8939.4353 | 4682.6679 | 4256.7674 | 8940.7124 | 12216.2389 | 5673.725 | 21873.7433 | 12784.4578 | 0 | 17476.8905 | 8760 | 25952.5062 | 527.875 | 536.05 | 1854.725 | 2920779.5773 | 178372.614 | 2947.725
104 | C | SOK | NAP | CC | FP | WC | R10 | 4.1884 | 58 | 2.9 | 8760 | 223263.4303 | 0 | 121498.6559 | 65533.1035 | 121436.5822 | 64365 | 203822.5 | 144821.25 | 128730 | 148743.8693 | 8760 | 1720.1251 | 21917.9266 | 0 | 0 | 826.4118 | 6704.1772 | 5501.5719 | -1514.2439 | 7423.9803 | 2914.4182 | 8760 | 8939.7548 | 4007.9856 | 4931.7692 | 8940.7124 | 12216.2389 | 5707.6606 | 21932.6217 | 12848.5722 | 0 | 19715.444 | 8760 | 26050.5244 | 646.625 | 426.125 | 1854.725 | 2920831.1222 | 178372.614 | 2899.3
105 | C | SOK | NAP | CC | FP | WC | R10 | 4.1884 | 58 | 4.35 | 8760 | 230366.5532 | 0 | 116484.4902 | 65533.1035 | 121436.5822 | 64783.5 | 205147.75 | 145762.875 | 129567 | 148877.4838 | 8760 | 1720.1251 | 23420.7022 | 0 | 0 | 798.0829 | 6192.6983 | 4600.1138 | -1521.9038 | 8349.2289 | 2875.3679 | 8760 | 8937.7658 | 3378.7717 | 5558.994 | 8940.7124 | 12216.2389 | 5702.1626 | 21974.3739 | 12894.2431 | 0 | 21243.4646 | 8760 | 26127.7392 | 730.025 | 349.7 | 1854.725 | 2920702.2044 | 178372.614 | 2871.95
106 | C | SOK | NAP | CC | FP | WC | R600 | 4.9191 | 23 | 0.6 | 8760 | 181197.0457 | 0 | 140013.4215 | 65533.1035 | 70239.375 | 72874.5 | 230769.25 | 163967.625 | 145749 | 171111.2969 | 8760 | 1720.1251 | 13566.4147 | 0 | 0 | 1273.64 | 5239.1765 | 10515.9639 | -1316.3518 | 3853.254 | 2871.1593 | 8760 | 9991.3606 | 7309.8294 | 2681.5312 | 9995.5229 | 6223.2263 | 6153.6945 | 24267.2538 | 14111.0353 | 0 | 11471.8345 | 8760 | 28796.7324 | 315.525 | 899.05 | 2104.7 | 3240436.2932 | 155104.6653 | 2267.6
107 | C | SOK | NAP | CC | FP | WC | R600 | 4.9191 | 23 | 1.15 | 8760 | 184860.3906 | 0 | 137381.8469 | 65533.1035 | 70239.375 | 72829.5 | 230626.75 | 163866.375 | 145659 | 174194.3314 | 8760 | 1720.1251 | 14147.8114 | 0 | 0 | 1115.3427 | 4991.1222 | 10471.4048 | -1376.2795 | 3881.2382 | 2838.9934 | 8760 | 9992.6356 | 7320.5402 | 2672.0954 | 9995.5229 | 6223.2263 | 6245.8738 | 24270.0219 | 14113.6568 | 0 | 12080.6444 | 8760 | 28801.8677 | 327 | 886.825 | 2104.7 | 3240531.7595 | 155104.6653 | 2254.125
108 | C | SOK | NAP | CC | FP | WC | R600 | 4.9191 | 23 | 1.75 | 8760 | 185668.1617 | 0 | 135183.7435 | 65533.1035 | 70239.375 | 72886.5 | 230807.25 | 163994.625 | 145773 | 174187.3677 | 8760 | 1720.1251 | 14411.3832 | 0 | 0 | 1118.399 | 4793.0509 | 10434.1886 | -1394.111 | 3919.825 | 2806.311 | 8760 | 9992.7228 | 7316.9244 | 2675.7984 | 9995.5229 | 6223.2263 | 6262.5253 | 24277.2606 | 14119.7125 | 0 | 12369.7827 | 8760 | 28813.0578 | 337.575 | 877.2 | 2104.7 | 3240495.5031 | 155104.6653 | 2266.525
109 | C | SOK | NAP | CC | FP | WC | R600 | 4.9191 | 32 | 0.8 | 8760 | 184603.3306 | 0 | 133145.3794 | 65533.1035 | 70239.375 | 72612 | 229938 | 163377 | 145224 | 167628.871 | 8760 | 1720.1251 | 15503.3357 | 0 | 0 | 1075.5231 | 4730.8938 | 9453.561 | -1398.742 | 4941.1509 | 2936.6524 | 8760 | 9988.3321 | 6596.3005 | 3392.0316 | 9995.5229 | 6223.2263 | 6263.2319 | 24324.6948 | 14168.5301 | 0 | 13299.9732 | 8760 | 28819.7348 | 407.925 | 802.275 | 2104.7 | 3240486.5532 | 155104.6653 | 2503
110 | C | SOK | NAP | CC | FP | WC | R600 | 4.9191 | 32 | 1.6 | 8760 | 189804.1026 | 0 | 128557.9353 | 65533.1035 | 70239.375 | 72498 | 229577 | 163120.5 | 144996 | 172157.5293 | 8760 | 1720.1251 | 16527.512 | 0 | 0 | 937.2011 | 4389.4564 | 9095.7868 | -1462.4474 | 5267.4206 | 2893.6772 | 8760 | 9991.8674 | 6426.0701 | 3565.7973 | 9995.5229 | 6223.2263 | 6336.362 | 24333.5235 | 14177.0145 | 0 | 14357.1658 | 8760 | 28847.3249 | 453.6 | 754.7 | 2104.7 | 3240474.1454 | 155104.6653 | 2489
111 | C | SOK | NAP | CC | FP | WC | R600 | 4.9191 | 32 | 2.4 | 8760 | 192785.9227 | 0 | 125141.1631 | 65533.1035 | 70239.375 | 72615 | 229947.5 | 163383.75 | 145230 | 171709.9743 | 8760 | 1720.1251 | 17123.4946 | 0 | 0 | 915.4419 | 4131.5712 | 8827.3898 | -1476.0082 | 5541.3065 | 2862.4006 | 8760 | 9992.9892 | 6270.3191 | 3722.6701 | 9995.5229 | 6223.2263 | 6338.4702 | 24350.0966 | 14193.3613 | 0 | 14975.7553 | 8760 | 28875.3296 | 488 | 722.25 | 2104.7 | 3240587.5117 | 155104.6653 | 2478.2
112 | C | SOK | NAP | CC | FP | WC | R600 | 4.9191 | 40.5 | 1 | 8760 | 190213.2914 | 0 | 128078.7172 | 65533.1035 | 70239.375 | 72114 | 228361 | 162256.5 | 144228 | 165928.6369 | 8760 | 1720.1251 | 16810.0834 | 0 | 0 | 954.9104 | 4335.6122 | 8714.3015 | -1456.7055 | 5678.437 | 2953.0202 | 8760 | 9992.9149 | 6116.8397 | 3876.0752 | 9995.5229 | 6223.2263 | 6331.3735 | 24367.4854 | 14209.5192 | 0 | 14556.0478 | 8760 | 28843.5583 | 466.8 | 735.1 | 2104.7 | 3240600.4156 | 155104.6653 | 2688.25
113 | C | SOK | NAP | CC | FP | WC | R600 | 4.9191 | 40.5 | 2.05 | 8760 | 196764.5467 | 0 | 121636.6467 | 65533.1035 | 70239.375 | 72292.5 | 228926.25 | 162658.125 | 144585 | 168525.7058 | 8760 | 1720.1251 | 18212.0636 | 0 | 0 | 825.3826 | 3918.8454 | 8039.1359 | -1515.1911 | 6353.9133 | 2906.5698 | 8760 | 9992.6487 | 5730.54 | 4262.1087 | 9995.5229 | 6223.2263 | 6387.13 | 24398.1971 | 14244.6944 | 0 | 15990.4453 | 8760 | 28896.3498 | 550.3 | 654.575 | 2104.7 | 3240583.0445 | 155104.6653 | 2673.9
114 | C | SOK | NAP | CC | FP | WC | R600 | 4.9191 | 40.5 | 3.05 | 8760 | 202097.1467 | 0 | 117311.6851 | 65533.1035 | 70239.375 | 72417 | 229320.5 | 162938.25 | 144834 | 168753.7118 | 8760 | 1720.1251 | 19247.8481 | 0 | 0 | 797.9481 | 3566.6356 | 7533.2802 | -1527.4658 | 6873.4933 | 2872.6181 | 8760 | 9994.3777 | 5403.0422 | 4591.3355 | 9995.5229 | 6223.2263 | 6390.3514 | 24418.3503 | 14266.1245 | 0 | 17045.9401 | 8760 | 28943.3779 | 605.525 | 601.425 | 2104.7 | 3240608.7791 | 155104.6653 | 2646.2
115 | C | SOK | NAP | CC | FP | WC | R60 | 4.9191 | 49 | 1.25 | 8760 | 198598.3317 | 0 | 123465.7747 | 65533.1035 | 70239.375 | 72039 | 228123.5 | 162087.75 | 144078 | 162275.2945 | 8760 | 1720.1251 | 17953.3732 | 0 | 0 | 848.526 | 3997.6915 | 8136.2025 | -1501.2803 | 6277.2274 | 2944.423 | 8760 | 9995.207 | 5753.1158 | 4242.0912 | 9995.5229 | 6223.2263 | 6383.3514 | 24422.6758 | 14265.6803 | 0 | 15675.599 | 8760 | 28890.3524 | 521.375 | 679.275 | 2104.7 | 3240676.0444 | 155104.6653 | 2844.925
116 | C | SOK | NAP | CC | FP | WC | R60 | 4.9191 | 49 | 2.45 | 8760 | 207118.4346 | 0 | 116797.9693 | 65533.1035 | 70239.375 | 72295.5 | 228935.75 | 162664.875 | 144591 | 163701.8579 | 8760 | 1720.1251 | 19635.9635 | 0 | 0 | 739.4428 | 3519.7405 | 7278.577 | -1553.3851 | 7153.4778 | 2909.987 | 8760 | 9994.6883 | 5228.0322 | 4766.6561 | 9995.5229 | 6223.2263 | 6429.0311 | 24459.0603 | 14306.8669 | 0 | 17377.3842 | 8760 | 28954.057 | 623.025 | 581.9 | 2104.7 | 3240583.7937 | 155104.6653 | 2816.7
117 | C | SOK | NAP | CC | FP | WC | R60 | 4.9191 | 49 | 3.7 | 8760 | 213897.8139 | 0 | 111477.824 | 65533.1035 | 70239.375 | 72655.5 | 230075.75 | 163474.875 | 145311 | 162922.6909 | 8760 | 1720.1251 | 20954.0276 | 0 | 0 | 688.9801 | 3125.6363 | 6476.7077 | -1566.7027 | 7978.6022 | 2874.8577 | 8760 | 9994.5193 | 4688.5572 | 5305.9622 | 9995.5229 | 6223.2263 | 6433.5155 | 24499.8389 | 14351.3515 | 0 | 18717.1389 | 8760 | 29029.4963 | 703.425 | 507.5 | 2104.7 | 3240544.9063 | 155104.6653 | 2784.2
118 | C | SOK | NAP | CC | FP | WC | R60 | 4.9191 | 58 | 1.45 | 8760 | 211053.3755 | 0 | 119842.7663 | 65533.1035 | 70239.375 | 72040.5 | 228128.25 | 162091.125 | 144081 | 157762.2542 | 8760 | 1720.1251 | 18939.5078 | 0 | 0 | 776.3575 | 3702.4028 | 7672.3342 | -1535.324 | 6766.0317 | 2933.5802 | 8760 | 9994.0029 | 5453.3385 | 4540.6645 | 9995.5229 | 6223.2263 | 6420.1445 | 24456.2684 | 14306.8228 | 0 | 16641.9464 | 8760 | 28918.0136 | 567.3 | 633.375 | 2104.7 | 3240702.5036 | 155104.6653 | 2969.825
119 | C | SOK | NAP | CC | FP | WC | R60 | 4.9191 | 58 | 2.9 | 8760 | 221141.4971 | 0 | 112343.2663 | 65533.1035 | 70239.375 | 72517.5 | 229638.75 | 163164.375 | 145035 | 158388.413 | 8760 | 1720.1251 | 20998.5939 | 0 | 0 | 655.1946 | 3169.5168 | 6503.8426 | -1583.8761 | 7966.9545 | 2891.6855 | 8760 | 9995.1922 | 4713.2587 | 5281.9335 | 9995.5229 | 6223.2263 | 6458.7234 | 24519.0605 | 14375.3422 | 0 | 18732.1693 | 8760 | 29021.9249 | 697.775 | 510.85 | 2104.7 | 3240621.9777 | 155104.6653 | 2941.2
120 | C | SOK | NAP | CC | FP | WC | R60 | 4.9191 | 58 | 4.35 | 8760 | 228776.6268 | 0 | 106921.8777 | 65533.1035 | 70239.375 | 72966 | 231059 | 164173.5 | 145932 | 158194.0798 | 8760 | 1720.1251 | 22513.8284 | 0 | 0 | 602.6606 | 2767.6886 | 5494.872 | -1596.9503 | 9004.6308 | 2852.8741 | 8760 | 9995.625 | 4002.5322 | 5993.0928 | 9995.5229 | 6223.2263 | 6467.6027 | 24572.2681 | 14427.761 | 0 | 20269.6745 | 8760 | 29115.0848 | 788.7 | 427.4 | 2104.7 | 3240647.3878 | 155104.6653 | 2910.75
121 | C | SOK | NAP | FC | ET | HC | OFF0 | 0.22955 | 11.5 | 0.288 | 8760 | 168158.836 | 0 | 102884.1469 | 0 | 29538.1641 | 52104 | 121576 | 117234 | 104208 | 139402.3444 | 8760 | 1720.1251 | 9192.9891 | 0 | 0 | 0 | 303.4646 | 5176.9207 | -1519.7491 | 4162.6928 | 3548.7592 | 8760 | 5746.4556 | 3081.6674 | 2664.7882 | 5745.6847 | 641.83 | 0 | 14460.8738 | 9093.7716 | 0 | 6527.8433 | 8760 | 0 | 364.05 | 504.35 | 2468.675 | 2115839.4534 | 110654.3789 | 1900.75 | -249.6311
122 | C | SOK | NAP | FC | ET | HC | OFF0 | 0.22955 | 11.5 | 0.575 | 8760 | 171575.9858 | 0 | 100186.5768 | 0 | 29538.1641 | 52096.5 | 121558.5 | 117217.125 | 104193 | 134314.8823 | 8760 | 1720.1251 | 9434.8287 | 0 | 0 | 0 | 224.8042 | 5100.1737 | -1566.1657 | 4255.8512 | 3567.7636 | 8760 | 5746.3621 | 3021.1849 | 2725.1772 | 5745.6847 | 641.83 | 0 | 14466.22 | 9096.6439 | 0 | 6755.3576 | 8760 | 0 | 372.125 | 496.15 | 2468.675 | 2116314.4555 | 110654.3789 | 1854.125 | -241.5106
123 | C | SOK | NAP | FC | ET | HC | OFF0 | 0.22955 | 11.5 | 0.863 | 8760 | 173347.785 | 0 | 99301.6358 | 0 | 29538.1641 | 52138.5 | 121656.5 | 117311.625 | 104277 | 133787.5554 | 8760 | 1720.1251 | 9571.2541 | 0 | 0 | 0 | 197.8399 | 5036.8127 | -1589.685 | 4320.0287 | 3581.0961 | 8760 | 5746.4861 | 2977.802 | 2768.6841 | 5745.6847 | 641.83 | 0 | 14464.9956 | 9098.4379 | 0 | 6881.3497 | 8760 | 0 | 377.875 | 491.1 | 2468.675 | 2116173.9674 | 110654.3789 | 1831.25 | -241.6126
124 | C | SOK | NAP | FC | ET | HC | OFF0 | 0.22955 | 15.5 | 0.388 | 8760 | 162840.4868 | 0 | 95727.3741 | 0 | 29538.1641 | 50359.5 | 117505.5 | 113308.875 | 100719 | 103255.5123 | 8760 | 1720.1251 | 11019.4197 | 0 | 0 | 0 | 203.5234 | 3730.3962 | -1597.7589 | 5548.6916 | 3674.5471 | 8760 | 5745.7193 | 2203.6485 | 3542.0708 | 5745.6847 | 641.83 | 0 | 14474.87 | 9078.7895 | 0 | 8195.5881 | 8760 | 0 | 476.825 | 362.5 | 2468.675 | 2116053.1837 | 110654.3789 | 2111.975 | -190.4673
125 | C | SOK | NAP | FC | ET | HC | OFF0 | 0.22955 | 15.5 | 0.775 | 8760 | 167405.1419 | 0 | 92855.8156 | 0 | 29538.1641 | 50214 | 117166 | 112981.5 | 100428 | 100965.9905 | 8760 | 1720.1251 | 11416.2346 | 0 | 0 | 0 | 132.2838 | 3504.6901 | -1637.8918 | 5775.8249 | 3695.0751 | 8760 | 5745.717 | 2057.1335 | 3688.5835 | 5745.6847 | 641.83 | 0 | 14477.9244 | 9077.6644 | 0 | 8575.4181 | 8760 | 0 | 496.5 | 340.4 | 2468.675 | 2115879.2232 | 110654.3789 | 2055 | -177.2925
126 | C | SOK | NAP | FC | ET | HC | OFF0 | 0.22955 | 15.5 | 1.163 | 8760 | 169826.3871 | 0 | 92093.1164 | 0 | 29538.1641 | 50086.5 | 116868.5 | 112694.625 | 100173 | 100244.5684 | 8760 | 1720.1251 | 11634.0708 | 0 | 0 | 0 | 107.7647 | 3374.3523 | -1657.6056 | 5892.1602 | 3707.2798 | 8760 | 5745.7229 | 1987.4063 | 3758.3166 | 5745.6847 | 641.83 | 0 | 14471.5765 | 9075.5655 | 0 | 8780.6837 | 8760 | 0 | 508.075 | 326.7 | 2468.675 | 2116291.1137 | 110654.3789 | 2025.45 | -175.466
127 | C | SOK | NAP | FC | ET | HC | OFF0 | 0.22955 | 20 | 0.5 | 8760 | 156528.2796 | 0 | 90503.2224 | 0 | 29538.1641 | 48762 | 113778 | 109714.5 | 97524 | 68259.8746 | 8760 | 1720.1251 | 12456.1682 | 0 | 0 | 0 | 129.3191 | 2677.8434 | -1648.5994 | 6559.4879 | 3750.1845 | 8760 | 5745.8731 | 1564.0829 | 4181.7903 | 5745.6847 | 641.83 | 0 | 14506.3282 | 9062.8422 | 0 | 9513.5391 | 8760 | 0 | 555.25 | 257.45 | 2468.675 | 2115611.5543 | 110654.3789 | 2335.725 | -104.1185
128 | C | SOK | NAP | FC | ET | HC | OFF0 | 0.22955 | 20 | 1 | 8760 | 161701.6262 | 0 | 87726.1576 | 0 | 29538.1641 | 48436.5 | 113018.5 | 108982.125 | 96873 | 66423.4956 | 8760 | 1720.1251 | 12962.5154 | 0 | 0 | 0 | 70.6872 | 2363.9401 | -1692.912 | 6852.5964 | 3776.6458 | 8760 | 5745.8047 | 1378.1332 | 4367.6716 | 5745.6847 | 641.83 | 0 | 14497.3678 | 9058.6709 | 0 | 9994.0605 | 8760 | 0 | 580.25 | 227.025 | 2468.675 | 2115555.8602 | 110654.3789 | 2275.2 | -99.4439
129 | C | SOK | NAP | FC | ET | HC | OFF0 | 0.22955 | 20 | 1.5 | 8760 | 164351.4762 | 0 | 85956.2756 | 0 | 29538.1641 | 48210 | 112490 | 108472.5 | 96420 | 65778.0845 | 8760 | 1720.1251 | 13222.2461 | 0 | 0 | 0 | 31.823 | 2146.9366 | -1706.4899 | 7048.4086 | 3786.7165 | 8760 | 5745.9503 | 1258.8336 | 4487.1167 | 5745.6847 | 641.83 | 0 | 14492.4545 | 9054.5682 | 0 | 10244.9058 | 8760 | 0 | 598.825 | 204.675 | 2468.675 | 2115960.6006 | 110654.3789 | 2242.7 | -93.4246
130 | C | SOK | NAP | FC | ET | HC | OFF | 0.22955 | 24 | 0.6 | 8760 | 151430.5883 | 0 | 88245.8729 | 0 | 29538.1641 | 48402 | 112938 | 108904.5 | 96804 | 67725.6804 | 8760 | 1720.1251 | 13344.6874 | 0 | 0 | 0 | 89.0318 | 2441.1499 | -1683.1949 | 6901.631 | 3781.4684 | 8760 | 5746.5217 | 1345.7512 | 4400.7705 | 5745.6847 | 641.83 | 0 | 14467.5505 | 9052.0191 | 0 | 10335.9437 | 8760 | 0 | 584.85 | 221.85 | 2468.675 | 2115829.2953 | 110654.3789 | 2516.1 | -141.4011
131 | C | SOK | NAP | FC | ET | HC | OFF | 0.22955 | 24 | 1.2 | 8760 | 156869.2809 | 0 | 85259.572 | 0 | 29538.1641 | 47931 | 111839 | 107844.75 | 95862 | 64809.2561 | 8760 | 1720.1251 | 13900.6724 | 0 | 0 | 0 | 34.1723 | 2037.1579 | -1724.2032 | 7262.0408 | 3803.4857 | 8760 | 5745.6915 | 1118.1242 | 4627.5673 | 5745.6847 | 641.83 | 0 | 14464.1378 | 9043.2632 | 0 | 10872.158 | 8760 | 0 | 616.15 | 182.7 | 2468.675 | 2115878.7648 | 110654.3789 | 2452.9 | -122.0203
132 | C | SOK | NAP | FC | ET | HC | OFF | 0.22955 | 24 | 1.8 | 8760 | 158823.7488 | 0 | 83439.4434 | 0 | 29538.1641 | 47424 | 110656 | 106704 | 94848 | 64841.6416 | 8760 | 1720.1251 | 14101.4772 | 0 | 0 | 0 | 1.9819 | 1654.1139 | -1737.088 | 7559.6057 | 3813.6364 | 8760 | 5745.6731 | 926.8454 | 4818.8277 | 5745.6847 | 641.83 | 0 | 14444.4968 | 9033.2139 | 0 | 11064.2711 | 8760 | 0 | 640.075 | 150.325 | 2468.675 | 2115763.6899 | 110654.3789 | 2428.35 | -127.6628
133 | C | SOK | NAP | FC | ET | HC | OFF | 0.22955 | 28.5 | 0.713 | 8760 | 142052.8006 | 0 | 85476.3075 | 0 | 29538.1641 | 47247 | 110243 | 106305.75 | 94494 | 64570.8754 | 8760 | 1720.1251 | 13450.9281 | 0 | 0 | 0 | 53.9117 | 1869.2334 | -1712.6908 | 7386.584 | 3807.5104 | 8760 | 5746.8032 | 1027.9733 | 4718.8299 | 5745.6847 | 641.83 | 0 | 14426.3838 | 9023.1427 | 0 | 10390.9178 | 8760 | 0 | 618.125 | 169.325 | 2468.675 | 2115663.9856 | 110654.3789 | 2729.6 | -159.6483
134 | C | SOK | NAP | FC | ET | HC | OFF | 0.22955 | 28.5 | 1.425 | 8760 | 147213.4899 | 0 | 82795.9862 | 0 | 29538.1641 | 46446 | 108374 | 104503.5 | 92892 | 61034.0405 | 8760 | 1720.1251 | 14001.6711 | 0 | 0 | 0 | 11.8918 | 1312.0596 | -1754.6753 | 7856.6998 | 3834.1768 | 8760 | 5746.1183 | 734.8698 | 5011.2485 | 5745.6847 | 641.83 | 0 | 14424.2398 | 9009.361 | 0 | 10918.4014 | 8760 | 0 | 657.625 | 116.475 | 2468.675 | 2115528.0658 | 110654.3789 | 2671.675 | -125.4743
135 | C | SOK | NAP | FC | ET | HC | OFF | 0.22955 | 28.5 | 2.138 | 8760 | 150092.085 | 0 | 81674.0611 | 0 | 29538.1641 | 46119 | 107611 | 103767.75 | 92238 | 58564.8005 | 8760 | 1720.1251 | 14332.7718 | 0 | 0 | 0 | 1.9819 | 1039.9407 | -1767.5069 | 8085.3019 | 3840.6365 | 8760 | 5745.3736 | 589.0175 | 5156.3561 | 5745.6847 | 641.83 | 0 | 14413.9434 | 9003.2624 | 0 | 11242.7384 | 8760 | 0 | 677.175 | 91.475 | 2468.675 | 2115514.4292 | 110654.3789 | 2641.15 | -122.8556
136 | C | SOK | NAP | FC | ET | HC | R100 | 1.6444 | 11.5 | 0.288 | 8760 | 161159.0854 | 0 | 141250.839 | 65533.1035 | 84103.8032 | 37083 | 86527 | 83436.75 | 74166 | 53913.8209 | 8760 | 1720.1251 | 8813.725 | 0 | 0 | 670.1309 | 4023.0073 | 4950.5162 | -1249.8288 | 1913.3097 | 3294.1297 | 8760 | 4247.9216 | 3095.9302 | 1151.9914 | 4247.8969 | 4796.318 | 2580.7575 | 10583.7789 | 6611.841 | 0 | 6412.8678 | 8760 | 0 | 187.125 | 430.925 | 2227.75 | 1524669.4811 | 178372.614 | 1979.9 | -115.0466
137 | C | SOK | NAP | FC | ET | HC | R100 | 1.6444 | 11.5 | 0.575 | 8760 | 166640.4547 | 0 | 138476.024 | 65533.1035 | 84103.8032 | 37179 | 86751 | 83652.75 | 74358 | 48316.026 | 8760 | 1720.1251 | 9169.711 | 0 | 0 | 604.9649 | 3882.2426 | 4901.3476 | -1311.2677 | 1968.1219 | 3290.7607 | 8760 | 4248.6753 | 3055.7948 | 1192.8806 | 4247.8969 | 4796.318 | 2589.1694 | 10597.1995 | 6619.4091 | 0 | 6760.1916 | 8760 | 0 | 190.575 | 429.075 | 2227.75 | 1524825.3662 | 178372.614 | 1904.5 | -111.4041
138 | C | SOK | NAP | FC | ET | HC | R100 | 1.6444 | 11.5 | 0.863 | 8760 | 169161.2627 | 0 | 137216.108 | 65533.1035 | 84103.8032 | 37225.5 | 86859.5 | 83757.375 | 74451 | 45786.3198 | 8760 | 1720.1251 | 9338.5567 | 0 | 0 | 601.2239 | 3821.2508 | 4825.9438 | -1332.4043 | 2039.5472 | 3295.3703 | 8760 | 4248.9539 | 3003.0779 | 1245.8761 | 4247.8969 | 4796.318 | 2590.121 | 10606.3174 | 6623.0735 | 0 | 6926.9087 | 8760 | 0 | 195.25 | 425.175 | 2227.75 | 1524876.1694 | 178372.614 | 1872.425 | -107.0852
139 | C | SOK | NAP | FC | ET | HC | R100 | 1.6444 | 15.5 | 0.388 | 8760 | 154506.9947 | 0 | 132309.1852 | 65533.1035 | 84103.8032 | 35659.5 | 83205.5 | 80233.875 | 71319 | 35473.4869 | 8760 | 1720.1251 | 10495.2871 | 0 | 0 | 563.7295 | 3607.107 | 4104.0693 | -1337.4742 | 2697.8492 | 3443.7191 | 8760 | 4248.0888 | 2608.5101 | 1639.5787 | 4247.8969 | 4796.318 | 2593.6057 | 10584.9611 | 6585.419 | 0 | 7861.3749 | 8760 | 0 | 251.65 | 342.675 | 2227.75 | 1524622.3431 | 178372.614 | 2198.4 | -75.56
140 | C | SOK | NAP | FC | ET | HC | R100 | 1.6444 | 15.5 | 0.775 | 8760 | 161284.1629 | 0 | 128674.1775 | 65533.1035 | 84103.8032 | 35707.5 | 83317.5 | 80341.875 | 71415 | 33339.7878 | 8760 | 1720.1251 | 11059.5193 | 0 | 0 | 506.3428 | 3407.1799 | 3926.6125 | -1391.9609 | 2860.09 | 3443.7611 | 8760 | 4248.6755 | 2494.037 | 1754.6385 | 4247.8969 | 4796.318 | 2597.8123 | 10589.9746 | 6590.353 | 0 | 8414.6758 | 8760 | 0 | 263.825 | 331.3 | 2227.75 | 1524620.9955 | 178372.614 | 2110.075 | -67.7753
141 | C | SOK | NAP | FC | ET | HC | R100 | 1.6444 | 15.5 | 1.163 | 8760 | 164751.5625 | 0 | 127106.782 | 65533.1035 | 84103.8032 | 35781 | 83489 | 80507.25 | 71562 | 32359.0146 | 8760 | 1720.1251 | 11329.1975 | 0 | 0 | 514.2811 | 3320.4088 | 3773.2174 | -1408.9486 | 3003.9468 | 3446.2266 | 8760 | 4248.1224 | 2386.5988 | 1861.5236 | 4247.8969 | 4796.318 | 2597.2663 | 10588.4199 | 6594.7141 | 0 | 8687.6136 | 8760 | 0 | 273.4 | 322.95 | 2227.75 | 1524524.9833 | 178372.614 | 2065.875 | -70.0854
142 | C | SOK | NAP | FC | ET | HC | R100 | 1.6444 | 20 | 0.5 | 8760 | 149092.5644 | 0 | 124858.4319 | 65533.1035 | 84103.8032 | 34788 | 81172 | 78273 | 69576 | 19117.5961 | 8760 | 1720.1251 | 11973.8121 | 0 | 0 | 484.7187 | 3198.3533 | 3574.4076 | -1404.2261 | 3190.0615 | 3537.2638 | 8760 | 4248.6114 | 2297.2524 | 1951.3589 | 4247.8969 | 4796.318 | 2601.253 | 10589.7471 | 6571.8803 | 0 | 9159.9853 | 8760 | 0 | 289.975 | 289.825 | 2227.75 | 1524361.4886 | 178372.614 | 2405.05 | -36.6042
143 | C | SOK | NAP | FC | ET | HC | R100 | 1.6444 | 20 | 1 | 8760 | 157132.7987 | 0 | 120365.4815 | 65533.1035 | 84103.8032 | 34696.5 | 80958.5 | 78067.125 | 69393 | 18433.4934 | 8760 | 1720.1251 | 12757.7857 | 0 | 0 | 436.5106 | 2937.9805 | 3226.6352 | -1455.7834 | 3504.5991 | 3538.1598 | 8760 | 4248.0029 | 2074.37 | 2173.6329 | 4247.8969 | 4796.318 | 2604.2742 | 10582.1677 | 6572.4169 | 0 | 9928.9916 | 8760 | 0 | 312.675 | 265.6 | 2227.75 | 1524308.1719 | 178372.614 | 2303.15 | -34.3246
144 | C | SOK | NAP | FC | ET | HC | R100 | 1.6444 | 20 | 1.5 | 8760 | 161610.6646 | 0 | 117569.6679 | 65533.1035 | 84103.8032 | 34689 | 80941 | 78050.25 | 69378 | 18604.7985 | 8760 | 1720.1251 | 13177.6124 | 0 | 0 | 442.4105 | 2783.1475 | 2949.1097 | -1464.6342 | 3769.9795 | 3530.7399 | 8760 | 4248.8014 | 1886.365 | 2362.4364 | 4247.8969 | 4796.318 | 2602.123 | 10587.6041 | 6578.2187 | 0 | 10362.2272 | 8760 | 0 | 331.325 | 246.825 | 2227.75 | 1524330.2263 | 178372.614 | 2249.375 | -32.4132
145 | C | SOK | NAP | FC | ET | HC | R10 | 1.6444 | 24 | 0.6 | 8760 | 146669.6266 | 0 | 120173.4943 | 65533.1035 | 84103.8032 | 34801.5 | 81203.5 | 78303.375 | 69603 | 25386.6538 | 8760 | 1720.1251 | 13123.4361 | 0 | 0 | 431.5374 | 2885.0749 | 3429.7705 | -1447.08 | 3385.0428 | 3576.514 | 8760 | 4247.9537 | 2161.5253 | 2086.4284 | 4247.8969 | 4796.318 | 2605.533 | 10556.0558 | 6567.5569 | 0 | 10216.4918 | 8760 | 0 | 306.875 | 273.15 | 2227.75 | 1524405.6977 | 178372.614 | 2547.3 | -79.0303
146 | C | SOK | NAP | FC | ET | HC | R10 | 1.6444 | 24 | 1.2 | 8760 | 155257.8931 | 0 | 114841.3498 | 65533.1035 | 84103.8032 | 34561.5 | 80643.5 | 77763.375 | 69123 | 22647.653 | 8760 | 1720.1251 | 14052.006 | 0 | 0 | 377.3832 | 2593.7226 | 2930.369 | -1499.9816 | 3821.7758 | 3582.0315 | 8760 | 4248.3008 | 1857.989 | 2390.3118 | 4247.8969 | 4796.318 | 2609.9856 | 10558.2096 | 6568.6635 | 0 | 11118.1091 | 8760 | 0 | 338.15 | 237.875 | 2227.75 | 1524206.944 | 178372.614 | 2445.475 | -69.7202
147 | C | SOK | NAP | FC | ET | HC | R10 | 1.6444 | 24 | 1.8 | 8760 | 160211.6835 | 0 | 112032.0371 | 65533.1035 | 84103.8032 | 34476 | 80444 | 77571 | 68952 | 22848.4372 | 8760 | 1720.1251 | 14593.2718 | 0 | 0 | 374.4405 | 2399.0703 | 2589.9663 | -1512.0353 | 4143.5665 | 3578.4087 | 8760 | 4248.2702 | 1626.8057 | 2621.4645 | 4247.8969 | 4796.318 | 2608.954 | 10550.6207 | 6571.2625 | 0 | 11665.9005 | 8760 | 0 | 359.875 | 214.725 | 2227.75 | 1524366.1472 | 178372.614 | 2389.75 | -78.4817
148 | C | SOK | NAP | FC | ET | HC | R10 | 1.6444 | 28.5 | 0.713 | 8760 | 138849.1364 | 0 | 115517.0547 | 65533.1035 | 84103.8032 | 34122 | 79618 | 76774.5 | 68244 | 29474.1198 | 8760 | 1720.1251 | 13389.6951 | 0 | 0 | 373.6313 | 2600.8595 | 3147.9431 | -1485.7598 | 3627.9028 | 3607.4666 | 8760 | 4248.058 | 1990.7729 | 2257.2851 | 4247.8969 | 4796.318 | 2609.6746 | 10533.3227 | 6547.8454 | 0 | 10430.3513 | 8760 | 0 | 319.85 | 248.85 | 2227.75 | 1524297.5711 | 178372.614 | 2735.8 | -93.3241
149 | C | SOK | NAP | FC | ET | HC | R10 | 1.6444 | 28.5 | 1.425 | 8760 | 148475.2164 | 0 | 109552.7024 | 65533.1035 | 84103.8032 | 33724.5 | 78690.5 | 75880.125 | 67449 | 28798.2351 | 8760 | 1720.1251 | 14513.3167 | 0 | 0 | 341.6145 | 2249.0385 | 2519.8149 | -1538.2332 | 4202.7807 | 3615.4667 | 8760 | 4248.0612 | 1587.8134 | 2660.2478 | 4247.8969 | 4796.318 | 2614.6595 | 10498.1206 | 6542.9058 | 0 | 11517.8946 | 8760 | 0 | 360.275 | 201.8 | 2227.75 | 1524284.6464 | 178372.614 | 2629.75 | -125.7284
150 | C | SOK | NAP | FC | ET | HC | R10 | 1.6444 | 28.5 | 2.138 | 8760 | 154185.0955 | 0 | 105309.4852 | 65533.1035 | 84103.8032 | 33561 | 78309 | 75512.25 | 67122 | 26453.1573 | 8760 | 1720.1251 | 15200.4024 | 0 | 0 | 328.236 | 1980.5112 | 2107.9042 | -1553.0069 | 4584.8932 | 3613.1145 | 8760 | 4248.0583 | 1320.0988 | 2927.9595 | 4247.8969 | 4796.318 | 2614.8051 | 10512.481 | 6546.3411 | 0 | 12210.3715 | 8760 | 0 | 386.85 | 172.5 | 2227.75 | 1524357.1321 | 178372.614 | 2568.9 | -105.8683
151 | C | SOK | NAP | FC | ET | HC | R600 | 1.8872 | 11.5 | 0.288 | 8760 | 161935.9223 | 0 | 126248.8392 | 65533.1035 | 51088.7482 | 39730.5 | 92704.5 | 89393.625 | 79461 | 55702.0804 | 8760 | 1720.1251 | 8844.8824 | 0 | 0 | 603.6845 | 2019.8688 | 5455.3148 | -1306.0865 | 1959.4379 | 3249.0739 | 8760 | 4612.6796 | 3429.4763 | 1183.2033 | 4611.5962 | 2387.5621 | 2926.4091 | 11479.8609 | 7145.7167 | 0 | 6389.3868 | 8760 | 0 | 190.55 | 471.625 | 2346.175 | 1648467.7479 | 155104.6653 | 1975.075 | -117.0612
152 | C | SOK | NAP | FC | ET | HC | R600 | 1.8872 | 11.5 | 0.575 | 8760 | 167748.7327 | 0 | 123221.2911 | 65533.1035 | 51088.7482 | 39822 | 92918 | 89599.5 | 79644 | 48922.4529 | 8760 | 1720.1251 | 9229.7495 | 0 | 0 | 536.9239 | 1905.8127 | 5394.3675 | -1374.0179 | 2023.5785 | 3259.7123 | 8760 | 4611.7136 | 3378.2719 | 1233.4416 | 4611.5962 | 2387.5621 | 2943.7821 | 11490.5028 | 7150.8049 | 0 | 6748.0655 | 8760 | 0 | 194 | 469.7 | 2346.175 | 1648504.998 | 155104.6653 | 1894.1 | -112.9489
153 | C | SOK | NAP | FC | ET | HC | R600 | 1.8872 | 11.5 | 0.863 | 8760 | 170512.9362 | 0 | 121764.1382 | 65533.1035 | 51088.7482 | 39894 | 93086 | 89761.5 | 79788 | 46495.3265 | 8760 | 1720.1251 | 9407.0434 | 0 | 0 | 530.8306 | 1851.2743 | 5311.3604 | -1391.4967 | 2103.9315 | 3262.3014 | 8760 | 4611.6559 | 3320.4105 | 1291.2453 | 4611.5962 | 2387.5621 | 2945.321 | 11496.1064 | 7155.7174 | 0 | 6924.8908 | 8760 | 0 | 199.75 | 465.15 | 2346.175 | 1648290.7752 | 155104.6653 | 1857.7 | -109.1918
154 | C | SOK | NAP | FC | ET | HC | R600 | 1.8872 | 15.5 | 0.388 | 8760 | 154481.0515 | 0 | 118427.6107 | 65533.1035 | 51088.7482 | 38256 | 89264 | 86076 | 76512 | 35282.7485 | 8760 | 1720.1251 | 10448.9834 | 0 | 0 | 485.2076 | 1768.8952 | 4571.9256 | -1407.4383 | 2778.4018 | 3410.8295 | 8760 | 4611.755 | 2918.8226 | 1692.9325 | 4611.5962 | 2387.5621 | 2950.6063 | 11476.0746 | 7116.8383 | 0 | 7744.9571 | 8760 | 0 | 257.825 | 379.775 | 2346.175 | 1648026.7336 | 155104.6653 | 2205.55 | -78.935
155 | C | SOK | NAP | FC | ET | HC | R600 | 1.8872 | 15.5 | 0.775 | 8760 | 161937.05 | 0 | 114577.3674 | 65533.1035 | 51088.7482 | 38286 | 89334 | 86143.5 | 76572 | 33758.2192 | 8760 | 1720.1251 | 11051.5655 | 0 | 0 | 418.6937 | 1626.3247 | 4374.6766 | -1471.4101 | 2960.249 | 3428.8204 | 8760 | 4611.612 | 2787.1291 | 1824.4829 | 4611.5962 | 2387.5621 | 2962.9538 | 11478.9784 | 7120.517 | 0 | 8315.1958 | 8760 | 0 | 270.55 | 367.55 | 2346.175 | 1648224.2587 | 155104.6653 | 2106.525 | -69.0772
156 | C | SOK | NAP | FC | ET | HC | R600 | 1.8872 | 15.5 | 1.163 | 8760 | 165883.4651 | 0 | 112479.0072 | 65533.1035 | 51088.7482 | 38374.5 | 89540.5 | 86342.625 | 76749 | 33071.3644 | 8760 | 1720.1251 | 11372.0378 | 0 | 0 | 413.5137 | 1520.9836 | 4196.7777 | -1484.3916 | 3132.6328 | 3431.6524 | 8760 | 4612.1466 | 2664.609 | 1947.5375 | 4611.5962 | 2387.5621 | 2962.0908 | 11479.8613 | 7127.1385 | 0 | 8641.0029 | 8760 | 0 | 283.25 | 356.325 | 2346.175 | 1648015.4788 | 155104.6653 | 2055.8 | -71.3295
157 | C | SOK | NAP | FC | ET | HC | R600 | 1.8872 | 20 | 0.5 | 8760 | 148148.4097 | 0 | 112171.5278 | 65533.1035 | 51088.7482 | 37321.5 | 87083.5 | 83973.375 | 74643 | 20811.2175 | 8760 | 1720.1251 | 11815.3993 | 0 | 0 | 393.6674 | 1543.6731 | 4014.252 | -1480.5553 | 3293.4402 | 3507.7689 | 8760 | 4611.7607 | 2589.3022 | 2022.4585 | 4611.5962 | 2387.5621 | 2965.2539 | 11477.8708 | 7100.8277 | 0 | 8929.4745 | 8760 | 0 | 296.975 | 325.05 | 2346.175 | 1648022.9541 | 155104.6653 | 2423.75 | -38.5271
158 | C | SOK | NAP | FC | ET | HC | R600 | 1.8872 | 20 | 1 | 8760 | 156653.9256 | 0 | 107443.093 | 65533.1035 | 51088.7482 | 37243.5 | 86901.5 | 83797.875 | 74487 | 18651.855 | 8760 | 1720.1251 | 12622.8669 | 0 | 0 | 353.2551 | 1344.0296 | 3619.7162 | -1535.7022 | 3657.5203 | 3521.8609 | 8760 | 4612.1389 | 2334.2096 | 2277.9293 | 4611.5962 | 2387.5621 | 2974.1784 | 11476.6225 | 7104.0325 | 0 | 9703.1974 | 8760 | 0 | 323.65 | 297.075 | 2346.175 | 1647717.2802 | 155104.6653 | 2319.025 | -35.7395
159 | C | SOK | NAP | FC | ET | HC | R600 | 1.8872 | 20 | 1.5 | 8760 | 161431.5121 | 0 | 104441.7931 | 65533.1035 | 51088.7482 | 37201.5 | 86803.5 | 83703.375 | 74403 | 19612.3738 | 8760 | 1720.1251 | 13079.0285 | 0 | 0 | 332.5704 | 1223.8534 | 3326.0537 | -1554.6904 | 3935.6953 | 3530.5126 | 8760 | 4611.621 | 2136.4457 | 2475.1753 | 4611.5962 | 2387.5621 | 2975.5604 | 11471.2283 | 7106.014 | 0 | 10154.1014 | 8760 | 0 | 343.525 | 276.5 | 2346.175 | 1647781.8232 | 155104.6653 | 2260.45 | -36.3833
160 | C | SOK | NAP | FC | ET | HC | R60 | 1.8872 | 24 | 0.6 | 8760 | 145146.2219 | 0 | 107968.808 | 65533.1035 | 51088.7482 | 37297.5 | 87027.5 | 83919.375 | 74595 | 24635.5211 | 8760 | 1720.1251 | 12874.7815 | 0 | 0 | 337.6129 | 1356.0721 | 3777.1582 | -1524.8341 | 3556.293 | 3543.503 | 8760 | 4611.8015 | 2411.9488 | 2199.8527 | 4611.5962 | 2387.5621 | 2973.627 | 11453.6489 | 7098.4059 | 0 | 9901.8689 | 8760 | 0 | 319.825 | 301.8 | 2346.175 | 1647973.6724 | 155104.6653 | 2573.875 | -69.0482
161 | C | SOK | NAP | FC | ET | HC | R60 | 1.8872 | 24 | 1.2 | 8760 | 153850.2652 | 0 | 102999.6392 | 65533.1035 | 51088.7482 | 37101 | 86569 | 83477.25 | 74202 | 24814.4634 | 8760 | 1720.1251 | 13805.9068 | 0 | 0 | 301.1253 | 1134.2382 | 3312.4412 | -1575.1103 | 3997.957 | 3559.0781 | 8760 | 4611.6729 | 2099.111 | 2512.5619 | 4611.5962 | 2387.5621 | 2980.207 | 11434.3817 | 7097.3145 | 0 | 10791.5471 | 8760 | 0 | 350.85 | 267.5 | 2346.175 | 1647649.1276 | 155104.6653 | 2474.875 | -89.9797
162 | C | SOK | NAP | FC | ET | HC | R60 | 1.8872 | 24 | 1.8 | 8760 | 159296.9139 | 0 | 100442.3098 | 65533.1035 | 51088.7482 | 37005 | 86345 | 83261.25 | 74010 | 22958.9343 | 8760 | 1720.1251 | 14381.2894 | 0 | 0 | 264.5318 | 1025.492 | 2925.9536 | -1596.7822 | 4367.722 | 3576.2877 | 8760 | 4611.6398 | 1838.072 | 2773.5678 | 4611.5962 | 2387.5621 | 2982.6117 | 11428.1253 | 7100.2424 | 0 | 11350.0274 | 8760 | 0 | 377.125 | 239.625 | 2346.175 | 1647921.1014 | 155104.6653 | 2412.75 | -94.7148
163 | C | SOK | NAP | FC | ET | HC | R60 | 1.8872 | 28.5 | 0.713 | 8760 | 136896.4867 | 0 | 104303.0523 | 65533.1035 | 51088.7482 | 36661.5 | 85543.5 | 82488.375 | 73323 | 29605.8298 | 8760 | 1720.1251 | 13064.0916 | 0 | 0 | 293.4047 | 1166.6549 | 3536.4233 | -1564.1026 | 3794.1547 | 3574.7746 | 8760 | 4612.0101 | 2240.493 | 2371.5171 | 4611.5962 | 2387.5621 | 2981.9479 | 11404.964 | 7077.6935 | 0 | 10041.4527 | 8760 | 0 | 332.05 | 278.975 | 2346.175 | 1647876.0466 | 155104.6653 | 2767.8 | -123.2807
164 | C | SOK | NAP | FC | ET | HC | R60 | 1.8872 | 28.5 | 1.425 | 8760 | 146098.1945 | 0 | 98675.4276 | 65533.1035 | 51088.7482 | 36289.5 | 84675.5 | 81651.375 | 72579 | 29276.5775 | 8760 | 1720.1251 | 14131.0637 | 0 | 0 | 237.8705 | 926.2516 | 2878.603 | -1612.08 | 4394.2418 | 3594.2837 | 8760 | 4611.3449 | 1826.0471 | 2785.2978 | 4611.5962 | 2387.5621 | 2986.6768 | 11413.4286 | 7076.157 | 0 | 11054.3651 | 8760 | 0 | 375.5 | 229.325 | 2346.175 | 1647625.034 | 155104.6653 | 2669.275 | -91.2028
165 | C | SOK | NAP | FC | ET | HC | R60 | 1.8872 | 28.5 | 2.138 | 8760 | 151702.4668 | 0 | 95352.3991 | 65533.1035 | 51088.7482 | 36021 | 84049 | 81047.25 | 72042 | 26376.4755 | 8760 | 1720.1251 | 14791.2387 | 0 | 0 | 209.2716 | 798.0144 | 2381.7409 | -1635.648 | 4855.8036 | 3609.1236 | 8760 | 4612.3196 | 1502.0604 | 3110.2592 | 4611.5962 | 2387.5621 | 2992.813 | 11410.1002 | 7077.2306 | 0 | 11700.4048 | 8760 | 0 | 407.175 | 193.175 | 2346.175 | 1647770.6122 | 155104.6653 | 2611.3 | -93.7243
166 | C | SOK | NAP | FC | ET | WC | OFF0 | 0.36343 | 18 | 0.45 | 8760 | 182644.4915 | 0 | 113935.4101 | 0 | 31184.5118 | 96363 | 305149.5 | 216816.75 | 192726 | 174006.1702 | 8760 | 1720.1251 | 12342.2086 | 0 | 0 | 0 | 404.0301 | 8549.0306 | -1564.1511 | 6991.0477 | 3611.5385 | 8760 | 9072.7547 | 4918.8704 | 4153.8842 | 9096.653 | 1016.1548 | 0 | 24454.2285 | 15260.199 | 0 | 9614.0111 | 8760 | 30136.275 | 694.375 | 911.675 | 2468.675 | 3408466.4941 | 110654.3789 | 1985.25
167 | C | SOK | NAP | FC | ET | WC | OFF0 | 0.36343 | 18 | 0.9 | 8760 | 186273.7719 | 0 | 111319.5845 | 0 | 31184.5118 | 96417 | 305320.5 | 216938.25 | 192834 | 172937.0766 | 8760 | 1720.1251 | 12652.1142 | 0 | 0 | 0 | 291.2035 | 8446.7841 | -1595.4745 | 7099.7848 | 3620.6736 | 8760 | 9071.5796 | 4865.6213 | 4205.9583 | 9096.653 | 1016.1548 | 0 | 24449.5158 | 15260.1335 | 0 | 9912.8273 | 8760 | 30136.741 | 710.5 | 896.45 | 2468.675 | 3408517.2047 | 110654.3789 | 1939.925
168 | C | SOK | NAP | FC | ET | WC | OFF0 | 0.36343 | 18 | 1.35 | 8760 | 188028.5762 | 0 | 110579.3839 | 0 | 31184.5118 | 96469.5 | 305486.75 | 217056.375 | 192939 | 171993.7608 | 8760 | 1720.1251 | 12796.9219 | 0 | 0 | 0 | 258.4111 | 8399.7284 | -1610.4531 | 7149.7586 | 3628.4961 | 8760 | 9071.1768 | 4843.5905 | 4227.5863 | 9096.653 | 1016.1548 | 0 | 24450.803 | 15263.3988 | 0 | 10051.3948 | 8760 | 30138.253 | 718.2 | 889.625 | 2468.675 | 3408584.0102 | 110654.3789 | 1917.8
169 | C | SOK | NAP | FC | ET | WC | OFF0 | 0.36343 | 24.5 | 0.6 | 8760 | 186535.8836 | 0 | 105820.2012 | 0 | 31184.5118 | 96154.5 | 304489.25 | 216347.625 | 192309 | 162235.0552 | 8760 | 1720.1251 | 15000.8327 | 0 | 0 | 0 | 280.212 | 6627.4902 | -1621.6199 | 9088.3495 | 3676.7913 | 8760 | 9080.3611 | 3683.1534 | 5397.2077 | 9096.653 | 1016.1548 | 0 | 24579.8815 | 15384.4912 | 0 | 12170.9784 | 8760 | 30215.7123 | 889.175 | 713.4 | 2468.675 | 3408764.4911 | 110654.3789 | 2156.725
170 | C | SOK | NAP | FC | ET | WC | OFF0 | 0.36343 | 24.5 | 1.25 | 8760 | 190689.6816 | 0 | 102686.1601 | 0 | 31184.5118 | 96145.5 | 304460.75 | 216327.375 | 192291 | 161138.22 | 8760 | 1720.1251 | 15413.4736 | 0 | 0 | 0 | 174.5089 | 6379.1023 | -1653.2829 | 9316.9304 | 3699.7397 | 8760 | 9080.268 | 3564.4973 | 5515.7707 | 9096.653 | 1016.1548 | 0 | 24584.2915 | 15393.9815 | 0 | 12559.0386 | 8760 | 30218.9164 | 916.775 | 685.65 | 2468.675 | 3408840.9733 | 110654.3789 | 2107.325
171 | C | SOK | NAP | FC | ET | WC | OFF0 | 0.36343 | 24.5 | 1.85 | 8760 | 192957.5585 | 0 | 101616.7314 | 0 | 31184.5118 | 96135 | 304427.5 | 216303.75 | 192270 | 161266.8154 | 8760 | 1720.1251 | 15648.9457 | 0 | 0 | 0 | 135.6383 | 6241.8543 | -1663.6825 | 9446.2797 | 3700.0019 | 8760 | 9080.6147 | 3496.7297 | 5583.8849 | 9096.653 | 1016.1548 | 0 | 24587.0088 | 15397.5772 | 0 | 12797.5065 | 8760 | 30221.5243 | 932.525 | 669.725 | 2468.675 | 3408704.958 | 110654.3789 | 2081.75
172 | C | SOK | NAP | FC | ET | WC | OFF0 | 0.36343 | 31 | 0.8 | 8760 | 181178.1763 | 0 | 99643.613 | 0 | 31184.5118 | 94527 | 299335.5 | 212685.75 | 189054 | 165337.2409 | 8760 | 1720.1251 | 15896.9021 | 0 | 0 | 0 | 177.3081 | 5214.0436 | -1663.5001 | 10472.299 | 3716.3924 | 8760 | 9085.9706 | 2837.5164 | 6248.4542 | 9096.653 | 1016.1548 | 0 | 24609.7644 | 15409.9312 | 0 | 12992.1082 | 8760 | 30189.031 | 1000.85 | 574.6 | 2468.675 | 3408208.2074 | 110654.3789 | 2394.075
173 | C | SOK | NAP | FC | ET | WC | OFF0 | 0.36343 | 31 | 1.55 | 8760 | 187158.6446 | 0 | 96626.5641 | 0 | 31184.5118 | 94494 | 299231 | 212611.5 | 188988 | 165317.1851 | 8760 | 1720.1251 | 16554.4426 | 0 | 0 | 0 | 97.7535 | 4795.0969 | -1691.2895 | 10887.3979 | 3746.1095 | 8760 | 9085.9467 | 2616.1519 | 6469.7948 | 9096.653 | 1016.1548 | 0 | 24617.3923 | 15424.7083 | 0 | 13620.7213 | 8760 | 30195.4332 | 1049.275 | 525.625 | 2468.675 | 3408988.6197 | 110654.3789 | 2333.775
174 | C | SOK | NAP | FC | ET | WC | OFF0 | 0.36343 | 31 | 2.35 | 8760 | 190052.0874 | 0 | 94564.9516 | 0 | 31184.5118 | 94456.5 | 299112.25 | 212527.125 | 188913 | 164821.6353 | 8760 | 1720.1251 | 16921.0036 | 0 | 0 | 0 | 31.4306 | 4554.9805 | -1697.4417 | 11115.3317 | 3732.0588 | 8760 | 9084.9538 | 2493.974 | 6590.9798 | 9096.653 | 1016.1548 | 0 | 24614.006 | 15425.1777 | 0 | 14007.9411 | 8760 | 30190.9417 | 1077.475 | 496.8 | 2468.675 | 3408282.8904 | 110654.3789 | 2305.7
175 | C | SOK | NAP | FC | ET | WC | OFF | 0.36343 | 38 | 0.95 | 8760 | 179362.3921 | 0 | 95512.1384 | 0 | 31184.5118 | 93024 | 294576 | 209304 | 186048 | 166504.7587 | 8760 | 1720.1251 | 16649.7033 | 0 | 0 | 0 | 115.2715 | 4247.4543 | -1695.6995 | 11405.9998 | 3746.2719 | 8760 | 9087.1462 | 2275.8166 | 6811.3295 | 9096.653 | 1016.1548 | 0 | 24615.616 | 15419.7103 | 0 | 13690.3262 | 8760 | 30136.4069 | 1074.15 | 476.25 | 2468.675 | 3408424.7722 | 110654.3789 | 2601.325
176 | C | SOK | NAP | FC | ET | WC | OFF | 0.36343 | 38 | 1.9 | 8760 | 187236.6909 | 0 | 91342.4164 | 0 | 31184.5118 | 93261 | 295326.5 | 209837.25 | 186522 | 164722.6931 | 8760 | 1720.1251 | 17587.4727 | 0 | 0 | 0 | 29.262 | 3513.6497 | -1719.0726 | 12148.4892 | 3766.2142 | 8760 | 9091.1185 | 1879.2155 | 7211.903 | 9096.653 | 1016.1548 | 0 | 24657.5043 | 15465.3868 | 0 | 14603.6672 | 8760 | 30175.0337 | 1160.25 | 394.1 | 2468.675 | 3408629.0756 | 110654.3789 | 2530.05
177 | C | SOK | NAP | FC | ET | WC | OFF | 0.36343 | 38 | 2.85 | 8760 | 191516.0464 | 0 | 89369.298 | 0 | 31184.5118 | 93363 | 295649.5 | 210066.75 | 186726 | 164026.4859 | 8760 | 1720.1251 | 18125.6458 | 0 | 0 | 0 | 2.7334 | 3169.53 | -1728.4019 | 12488.2508 | 3758.1122 | 8760 | 9089.5267 | 1719.1488 | 7370.3779 | 9096.653 | 1016.1548 | 0 | 24662.5174 | 15477.3513 | 0 | 15153.325 | 8760 | 30178.555 | 1208.05 | 348 | 2468.675 | 3408733.4288 | 110654.3789 | 2492.1
178 | C | SOK | NAP | FC | ET | WC | OFF | 0.36343 | 44.5 | 1.1 | 8760 | 180305.4115 | 0 | 92404.3456 | 0 | 31184.5118 | 91734 | 290491 | 206401.5 | 183468 | 165557.3176 | 8760 | 1720.1251 | 17186.5709 | 0 | 0 | 0 | 76.9575 | 3558.2063 | -1718.4136 | 12052.6212 | 3750.4502 | 8760 | 9090.2737 | 1892.99 | 7197.2837 | 9096.653 | 1016.1548 | 0 | 24614.5811 | 15419.0222 | 0 | 14206.3993 | 8760 | 30088.3958 | 1124.75 | 404.15 | 2468.675 | 3408467.4432 | 110654.3789 | 2756.35
179 | C | SOK | NAP | FC | ET | WC | OFF | 0.36343 | 44.5 | 2.25 | 8760 | 189464.4527 | 0 | 88066.6348 | 0 | 31184.5118 | 92254.5 | 292139.25 | 207572.625 | 184509 | 162012.05 | 8760 | 1720.1251 | 18319.0587 | 0 | 0 | 0 | 5.9001 | 2681.5786 | -1744.3484 | 12949.9814 | 3767.2865 | 8760 | 9091.8828 | 1427.937 | 7663.9458 | 9096.653 | 1016.1548 | 0 | 24672.5957 | 15480.157 | 0 | 15307.3141 | 8760 | 30139.8881 | 1235.15 | 302.425 | 2468.675 | 3408320.3858 | 110654.3789 | 2681.575
180 | C | SOK | NAP | FC | ET | WC | OFF | 0.36343 | 44.5 | 3.35 | 8760 | 193510.6604 | 0 | 86107.0155 | 0 | 31184.5118 | 92235 | 292077.5 | 207528.75 | 184470 | 161295.0499 | 8760 | 1720.1251 | 18864.081 | 0 | 0 | 0 | 2.7334 | 2201.7676 | -1752.2948 | 13424.6763 | 3752.6049 | 8760 | 9089.5007 | 1195.8042 | 7893.6966 | 9096.653 | 1016.1548 | 0 | 24673.2136 | 15491.8236 | 0 | 15870.1012 | 8760 | 30134.7404 | 1298 | 239.25 | 2468.675 | 3408893.2022 | 110654.3789 | 2651.7
181 | C | SOK | NAP | FC | ET | WC | R100 | 2.6035 | 18 | 0.45 | 8760 | 173269.5126 | 0 | 157292.2695 | 65533.1035 | 98086.1127 | 82432.5 | 261036.25 | 185473.125 | 164865 | 82363.4165 | 8760 | 1720.1251 | 12036.111 | 0 | 0 | 927.634 | 6134.0285 | 8752.3633 | -1295.5756 | 3413.0903 | 3364.2665 | 8760 | 6720.2959 | 4793.7361 | 1926.5598 | 6725.3331 | 7593.6017 | 3843.2417 | 18737.7813 | 11914.4623 | 0 | 9624.0169 | 8760 | 22328.9716 | 362.725 | 1011.15 | 2227.75 | 2452035.6665 | 178372.614 | 2061.075
182 | C | SOK | NAP | FC | ET | WC | R100 | 2.6035 | 18 | 0.9 | 8760 | 179170.7957 | 0 | 153790.7529 | 65533.1035 | 98086.1127 | 82404 | 260946 | 185409 | 164808 | 81496.7536 | 8760 | 1720.1251 | 12547.972 | 0 | 0 | 845.7883 | 5888.0856 | 8647.6839 | -1345.3279 | 3510.9434 | 3352.2817 | 8760 | 6720.5438 | 4746.4546 | 1974.0892 | 6725.3331 | 7593.6017 | 3872.9297 | 18733.7718 | 11912.4608 | 0 | 10151.1395 | 8760 | 22329.8404 | 376.775 | 996.625 | 2227.75 | 2451944.0686 | 178372.614 | 1990.25
183 | C | SOK | NAP | FC | ET | WC | R100 | 2.6035 | 18 | 1.35 | 8760 | 181565.7765 | 0 | 152364.348 | 65533.1035 | 98086.1127 | 82554 | 261421 | 185746.5 | 165108 | 79505.887 | 8760 | 1720.1251 | 12739.1605 | 0 | 0 | 841.6738 | 5783.8028 | 8609.3348 | -1362.3729 | 3557.5686 | 3348.0445 | 8760 | 6720.4691 | 4734.1051 | 1986.364 | 6725.3331 | 7593.6017 | 3877.5185 | 18744.4708 | 11923.547 | 0 | 10345.3466 | 8760 | 22341.7678 | 385.65 | 990.25 | 2227.75 | 2452189.0825 | 178372.614 | 1962.025
184 | C | SOK | NAP | FC | ET | WC | R100 | 2.6035 | 24.5 | 0.6 | 8760 | 173621.3791 | 0 | 148116.6312 | 65533.1035 | 98086.1127 | 82129.5 | 260076.75 | 184791.375 | 164259 | 80545.8939 | 8760 | 1720.1251 | 14408.6473 | 0 | 0 | 793.631 | 5514.7205 | 7878.6238 | -1369.4519 | 4425.2961 | 3470.0193 | 8760 | 6723.16 | 4231.3294 | 2491.8306 | 6725.3331 | 7593.6017 | 3883.671 | 18787.584 | 11965.6401 | 0 | 11841.2029 | 8760 | 22360.4847 | 465.125 | 903.7 | 2227.75 | 2452150.2015 | 178372.614 | 2262.8
185 | C | SOK | NAP | FC | ET | WC | R100 | 2.6035 | 24.5 | 1.25 | 8760 | 180591.6159 | 0 | 143260.705 | 65533.1035 | 98086.1127 | 82060.5 | 259858.25 | 184636.125 | 164121 | 80331.413 | 8760 | 1720.1251 | 15131.7086 | 0 | 0 | 715.803 | 5147.1276 | 7689.5878 | -1414.9905 | 4577.2417 | 3458.9229 | 8760 | 6723.3612 | 4184.9306 | 2538.4306 | 6725.3331 | 7593.6017 | 3903.7931 | 18787.6722 | 11968.1761 | 0 | 12576.818 | 8760 | 22365.2604 | 492.775 | 874.9 | 2227.75 | 2452216.7173 | 178372.614 | 2180.75
186 | C | SOK | NAP | FC | ET | WC | R100 | 2.6035 | 24.5 | 1.85 | 8760 | 183369.7644 | 0 | 141313.0849 | 65533.1035 | 98086.1127 | 81993 | 259644.5 | 184484.25 | 163986 | 80328.6021 | 8760 | 1720.1251 | 15399.6028 | 0 | 0 | 733.208 | 4996.6174 | 7521.7002 | -1425.551 | 4722.2521 | 3456.2207 | 8760 | 6723.9825 | 4133.9196 | 2590.0629 | 6725.3331 | 7593.6017 | 3902.5026 | 18791.5259 | 11973.6973 | 0 | 12846.6609 | 8760 | 22374.5728 | 516.175 | 850.375 | 2227.75 | 2452090.4801 | 178372.614 | 2149.6
187 | C | SOK | NAP | FC | ET | WC | R100 | 2.6035 | 31 | 0.8 | 8760 | 169362.5167 | 0 | 139836.4333 | 65533.1035 | 98086.1127 | 80571 | 255141.5 | 181284.75 | 161142 | 86830.85 | 8760 | 1720.1251 | 15504.9237 | 0 | 0 | 686.7233 | 4908.0081 | 7102.9792 | -1427.5489 | 5106.6645 | 3536.8718 | 8760 | 6722.1943 | 3836.5107 | 2885.6836 | 6725.3331 | 7593.6017 | 3912.7441 | 18755.8461 | 11941.6054 | 0 | 12833.9835 | 8760 | 22295.8523 | 524.05 | 818.8 | 2227.75 | 2451914.4365 | 178372.614 | 2480.1
188 | C | SOK | NAP | FC | ET | WC | R100 | 2.6035 | 31 | 1.55 | 8760 | 177122.1946 | 0 | 134825.2674 | 65533.1035 | 98086.1127 | 80439 | 254723.5 | 180987.75 | 160878 | 85513.5087 | 8760 | 1720.1251 | 16402.3564 | 0 | 0 | 630.4093 | 4517.5308 | 6710.7014 | -1467.5877 | 5468.4441 | 3533.6144 | 8760 | 6723.3872 | 3683.0554 | 3040.3318 | 6725.3331 | 7593.6017 | 3926.6955 | 18760.6013 | 11949.216 | 0 | 13737.0175 | 8760 | 22305.3082 | 577.075 | 763.575 | 2227.75 | 2452157.8464 | 178372.614 | 2397.775
189 | C | SOK | NAP | FC | ET | WC | R100 | 2.6035 | 31 | 2.35 | 8760 | 181626.5094 | 0 | 130912.0283 | 65533.1035 | 98086.1127 | 80092.5 | 253626.25 | 180208.125 | 160185 | 85387.4537 | 8760 | 1720.1251 | 16919.8899 | 0 | 0 | 627.574 | 4277.6439 | 6355.7751 | -1473.7845 | 5773.2778 | 3518.8669 | 8760 | 6723.7079 | 3543.1132 | 3180.5947 | 6725.3331 | 7593.6017 | 3919.7628 | 18748.8373 | 11938.974 | 0 | 14264.8114 | 8760 | 22294.9024 | 619.775 | 715.1 | 2227.75 | 2452214.602 | 178372.614 | 2352
190 | C | SOK | NAP | FC | ET | WC | R10 | 2.6035 | 38 | 0.95 | 8760 | 168756.3304 | 0 | 133698.8425 | 65533.1035 | 98086.1127 | 79764 | 252586 | 179469 | 159528 | 87715.1954 | 8760 | 1720.1251 | 16479.5182 | 0 | 0 | 613.2302 | 4424.1983 | 6520.4781 | -1469.3011 | 5650.2803 | 3580.1247 | 8760 | 6724.7444 | 3547.8079 | 3176.9365 | 6725.3331 | 7593.6017 | 3931.1998 | 18774.4368 | 11960.2308 | 0 | 13736.0327 | 8760 | 22294.2976 | 575.475 | 753.925 | 2227.75 | 2451943.3427 | 178372.614 | 2664.975
191 | C | SOK | NAP | FC | ET | WC | R10 | 2.6035 | 38 | 1.9 | 8760 | 179128.2645 | 0 | 127076.0341 | 65533.1035 | 98086.1127 | 79489.5 | 251716.75 | 178851.375 | 158979 | 85397.7168 | 8760 | 1720.1251 | 17761.2433 | 0 | 0 | 538.2067 | 3964.3714 | 5902.5573 | -1514.5128 | 6220.7821 | 3572.1897 | 8760 | 6725.2466 | 3293.7254 | 3431.5212 | 6725.3331 | 7593.6017 | 3947.0036 | 18774.8182 | 11964.6365 | 0 | 15023.8966 | 8760 | 22300.1452 | 656.8 | 668.025 | 2227.75 | 2452122.7142 | 178372.614 | 2567.275
192 | C | SOK | NAP | FC | ET | WC | R10 | 2.6035 | 38 | 2.85 | 8760 | 185867.063 | 0 | 122643.8296 | 65533.1035 | 98086.1127 | 79080 | 250420 | 177930 | 158160 | 84029.0252 | 8760 | 1720.1251 | 18618.4973 | 0 | 0 | 524.343 | 3655.0216 | 5400.8725 | -1524.8454 | 6686.9967 | 3562.5442 | 8760 | 6723.9582 | 3067.2052 | 3656.7531 | 6725.3331 | 7593.6017 | 3943.3602 | 18757.7312 | 11952.8324 | 0 | 15886.7767 | 8760 | 22288.6665 | 719.125 | 598.875 | 2227.75 | 2452123.3492 | 178372.614 | 2506.35
193 | C | SOK | NAP | FC | ET | WC | R10 | 2.6035 | 44.5 | 1.1 | 8760 | 171891.7104 | 0 | 129003.4056 | 65533.1035 | 98086.1127 | 79311 | 251151.5 | 178449.75 | 158622 | 86332.9641 | 8760 | 1720.1251 | 17364.0057 | 0 | 0 | 540.8936 | 4048.4448 | 6102.1472 | -1501.757 | 6048.2848 | 3592.0095 | 8760 | 6723.7937 | 3341.6993 | 3382.0944 | 6725.3331 | 7593.6017 | 3946.6654 | 18787.4794 | 11973.0571 | 0 | 14587.9607 | 8760 | 22293.6904 | 617.075 | 704.775 | 2227.75 | 2452201.1465 | 178372.614 | 2792.775
194 | C | SOK | NAP | FC | ET | WC | R10 | 2.6035 | 44.5 | 2.25 | 8760 | 184495.8366 | 0 | 120925.6941 | 65533.1035 | 98086.1127 | 78790.5 | 249503.25 | 177278.625 | 157581 | 83552.094 | 8760 | 1720.1251 | 18967.254 | 0 | 0 | 493.9226 | 3470.8027 | 5266.0869 | -1547.5658 | 6832.3472 | 3585.8489 | 8760 | 6724.9544 | 2974.6671 | 3750.2873 | 6725.3331 | 7593.6017 | 3962.9091 | 18781.1856 | 11969.3427 | 0 | 16192.9595 | 8760 | 22293.3185 | 723.975 | 589.2 | 2227.75 | 2452033.5695 | 178372.614 | 2685
195 | C | SOK | NAP | FC | ET | WC | R10 | 2.6035 | 44.5 | 3.35 | 8760 | 192206.757 | 0 | 114882.597 | 65533.1035 | 98086.1127 | 78694.5 | 249199.25 | 177062.625 | 157389 | 82542.5502 | 8760 | 1720.1251 | 20017.9645 | 0 | 0 | 463.7878 | 3096.1849 | 4658.5164 | -1559.378 | 7426.464 | 3575.1388 | 8760 | 6725.2264 | 2689.9768 | 4035.2496 | 6725.3331 | 7593.6017 | 3961.1195 | 18788.7583 | 11982.1301 | 0 | 17246.7895 | 8760 | 22315.7022 | 803.825 | 507.75 | 2227.75 | 2452330.0457 | 178372.614 | 2621.95
196 | C | SOK | NAP | FC | ET | WC | R600 | 2.9879 | 18 | 0.45 | 8760 | 174400.35 | 0 | 144160.645 | 65533.1035 | 57958.323 | 89700 | 284050 | 201825 | 179400 | 84988.1696 | 8760 | 1720.1251 | 12047.212 | 0 | 0 | 799.3932 | 3021.7578 | 9677.9315 | -1359.9197 | 3524.3171 | 3331.4449 | 8760 | 7296.2008 | 5318.252 | 1977.9488 | 7301.1473 | 3780.0236 | 4316.9571 | 20368.9665 | 12943.4547 | 0 | 9569.6938 | 8760 | 24212.7929 | 376.625 | 1118.375 | 2346.175 | 2649976.1784 | 155104.6653 | 2053.3
197 | C | SOK | NAP | FC | ET | WC | R600 | 2.9879 | 18 | 0.9 | 8760 | 180200.5792 | 0 | 140437.8932 | 65533.1035 | 57958.323 | 89668.5 | 283950.25 | 201754.125 | 179337 | 84302.8628 | 8760 | 1720.1251 | 12537.3722 | 0 | 0 | 713.0906 | 2844.5077 | 9567.1252 | -1414.0992 | 3632.1917 | 3330.8153 | 8760 | 7297.212 | 5272.1572 | 2025.0548 | 7301.1473 | 3780.0236 | 4361.8688 | 20367.9406 | 12941.559 | 0 | 10061.4642 | 8760 | 24216.2989 | 393.625 | 1100.85 | 2346.175 | 2650087.2833 | 155104.6653 | 1981.875
198 | C | SOK | NAP | FC | ET | WC | R600 | 2.9879 | 18 | 1.35 | 8760 | 183151.6143 | 0 | 139152.4789 | 65533.1035 | 57958.323 | 89776.5 | 284292.25 | 201997.125 | 179553 | 82822.9004 | 8760 | 1720.1251 | 12772.4739 | 0 | 0 | 708.6576 | 2733.723 | 9496.9783 | -1429.8206 | 3707.1253 | 3331.5547 | 8760 | 7296.5933 | 5243.7319 | 2052.8614 | 7301.1473 | 3780.0236 | 4365.7264 | 20376.6309 | 12951.5727 | 0 | 10297.516 | 8760 | 24230.6317 | 405.525 | 1090.75 | 2346.175 | 2649837.32 | 155104.6653 | 1946.275
199 | C | SOK | NAP | FC | ET | WC | R600 | 2.9879 | 24.5 | 0.6 | 8760 | 173886.0614 | 0 | 135981.6903 | 65533.1035 | 57958.323 | 89452.5 | 283266.25 | 201268.125 | 178905 | 85192.9275 | 8760 | 1720.1251 | 14300.0502 | 0 | 0 | 657.7135 | 2653.6756 | 8881.1152 | -1444.3566 | 4499.6271 | 3441.267 | 8760 | 7295.6655 | 4783.5101 | 2512.1554 | 7301.1473 | 3780.0236 | 4377.2458 | 20411.7552 | 12988.8585 | 0 | 11660.4968 | 8760 | 24245.4464 | 478.85 | 1012.025 | 2346.175 | 2650017.2399 | 155104.6653 | 2268.35
200 | C | SOK | NAP | FC | ET | WC | R600 | 2.9879 | 24.5 | 1.25 | 8760 | 181082.0439 | 0 | 131275.0041 | 65533.1035 | 57958.323 | 89355 | 282957.5 | 201048.75 | 178710 | 83020.1773 | 8760 | 1720.1251 | 14990.9319 | 0 | 0 | 567.9545 | 2407.256 | 8537.7665 | -1500.2767 | 4774.8268 | 3456.1941 | 8760 | 7298.5332 | 4663.9232 | 2634.6101 | 7301.1473 | 3780.0236 | 4413.1161 | 20422.5954 | 13002.4734 | 0 | 12339.9665 | 8760 | 24250.6444 | 516.8 | 972.45 | 2346.175 | 2650005.1187 | 155104.6653 | 2182.7
201 | C | SOK | NAP | FC | ET | WC | R600 | 2.9879 | 24.5 | 1.85 | 8760 | 184528.8899 | 0 | 128371.1977 | 65533.1035 | 57958.323 | 89224.5 | 282544.25 | 200755.125 | 178449 | 83565.0592 | 8760 | 1720.1251 | 15330.2861 | 0 | 0 | 554.7477 | 2245.5502 | 8361.3491 | -1508.9764 | 4928.961 | 3453.2738 | 8760 | 7300.2825 | 4609.2605 | 2691.022 | 7301.1473 | 3780.0236 | 4411.0433 | 20424.5547 | 13002.6034 | 0 | 12681.2492 | 8760 | 24260.4416 | 542.175 | 944.9 | 2346.175 | 2650136.6988 | 155104.6653 | 2142.6
202 | C | SOK | NAP | FC | ET | WC | R600 | 2.9879 | 31 | 0.8 | 8760 | 168217.699 | 0 | 128719.1745 | 65533.1035 | 57958.323 | 87642 | 277533 | 197194.5 | 175284 | 91773.654 | 8760 | 1720.1251 | 15168.3451 | 0 | 0 | 547.7049 | 2326.1093 | 7912.3917 | -1507.5908 | 5329.8276 | 3517.5724 | 8760 | 7298.5889 | 4305.3869 | 2993.202 | 7301.1473 | 3780.0236 | 4417.6394 | 20385.4117 | 12966.7859 | 0 | 12417.3292 | 8760 | 24183.494 | 551.1 | 909.6 | 2346.175 | 2649767.6712 | 155104.6653 | 2500.825
203 | C | SOK | NAP | FC | ET | WC | R600 | 2.9879 | 31 | 1.55 | 8760 | 176101.0651 | 0 | 123439.5265 | 65533.1035 | 57958.323 | 87385.5 | 276720.75 | 196617.375 | 174771 | 90152.1736 | 8760 | 1720.1251 | 16035.8983 | 0 | 0 | 487.5294 | 2030.3635 | 7487.1442 | -1550.9767 | 5723.0696 | 3525.0089 | 8760 | 7298.6143 | 4125.5857 | 3173.0286 | 7301.1473 | 3780.0236 | 4441.0091 | 20379.9687 | 12967.1537 | 0 | 13276.7698 | 8760 | 24179.9275 | 605.475 | 850.95 | 2346.175 | 2649742.2285 | 155104.6653 | 2418.125
204 | C | SOK | NAP | FC | ET | WC | R600 | 2.9879 | 31 | 2.35 | 8760 | 181627.888 | 0 | 119493.2896 | 65533.1035 | 57958.323 | 87462 | 276963 | 196789.5 | 174924 | 87701.4116 | 8760 | 1720.1251 | 16652.4624 | 0 | 0 | 453.4177 | 1840.4569 | 7129.6425 | -1565.5507 | 6064.1117 | 3527.4041 | 8760 | 7299.6445 | 3980.3949 | 3319.2496 | 7301.1473 | 3780.0236 | 4444.2734 | 20396.781 | 12984.6732 | 0 | 13888.4109 | 8760 | 24203.0514 | 655.9 | 801.8 | 2346.175 | 2650096.9778 | 155104.6653 | 2361.425
205 | C | SOK | NAP | FC | ET | WC | R60 | 2.9879 | 38 | 0.95 | 8760 | 166795.9308 | 0 | 123366.7814 | 65533.1035 | 57958.323 | 86775 | 274787.5 | 195243.75 | 173550 | 92677.5412 | 8760 | 1720.1251 | 15995.9087 | 0 | 0 | 467.2496 | 2048.7008 | 7276.7856 | -1551.2183 | 5923.8697 | 3558.4406 | 8760 | 7300.92 | 3982.4516 | 3318.4684 | 7301.1473 | 3780.0236 | 4444.2577 | 20402.2974 | 12983.588 | 0 | 13173.2314 | 8760 | 24177.4129 | 606.55 | 839.7 | 2346.175 | 2649879.9005 | 155104.6653 | 2693.9
206 | C | SOK | NAP | FC | ET | WC | R60 | 2.9879 | 38 | 1.9 | 8760 | 177607.6699 | 0 | 116770.9711 | 65533.1035 | 57958.323 | 86383.5 | 273547.75 | 194362.875 | 172767 | 89331.8171 | 8760 | 1720.1251 | 17267.2175 | 0 | 0 | 403.2664 | 1689.6811 | 6573.979 | -1591.0859 | 6581.4379 | 3564.5222 | 8760 | 7299.6989 | 3678.7288 | 3620.9702 | 7301.1473 | 3780.0236 | 4458.0924 | 20399.227 | 12986.6948 | 0 | 14438.0606 | 8760 | 24177.9331 | 696.525 | 743.2 | 2346.175 | 2649670.7599 | 155104.6653 | 2592.9
207 | C | SOK | NAP | FC | ET | WC | R60 | 2.9879 | 38 | 2.85 | 8760 | 184435.43 | 0 | 112800.7358 | 65533.1035 | 57958.323 | 86230.5 | 273063.25 | 194018.625 | 172461 | 88104.7478 | 8760 | 1720.1251 | 18092.5612 | 0 | 0 | 351.8342 | 1520.4681 | 6055.4179 | -1610.3813 | 7082.2436 | 3566.3173 | 8760 | 7300.17 | 3442.3353 | 3857.8347 | 7301.1473 | 3780.0236 | 4468.0866 | 20402.7754 | 12991.6719 | 0 | 15255.3917 | 8760 | 24189.2483 | 765.175 | 672 | 2346.175 | 2649844.9309 | 155104.6653 | 2532.125
208 | C | SOK | NAP | FC | ET | WC | R60 | 2.9879 | 44.5 | 1.1 | 8760 | 169152.1022 | 0 | 119321.551 | 65533.1035 | 57958.323 | 86073 | 272564.5 | 193664.25 | 172146 | 92406.5115 | 8760 | 1720.1251 | 16768.5906 | 0 | 0 | 414.7048 | 1797.5096 | 6806.5755 | -1582.6789 | 6359.8534 | 3564.6341 | 8760 | 7300.0863 | 3750.1402 | 3549.946 | 7301.1473 | 3780.0236 | 4463.4375 | 20403.1801 | 12984.902 | 0 | 13918.7043 | 8760 | 24166.2534 | 650.375 | 784.175 | 2346.175 | 2649904.9751 | 155104.6653 | 2829.025
209 | C | SOK | NAP | FC | ET | WC | R60 | 2.9879 | 44.5 | 2.25 | 8760 | 181765.8567 | 0 | 111370.5811 | 65533.1035 | 57958.323 | 85773 | 271614.5 | 192989.25 | 171546 | 88537.6821 | 8760 | 1720.1251 | 18302.8455 | 0 | 0 | 330.5409 | 1400.0804 | 5933.1189 | -1623.4062 | 7198.3717 | 3574.3045 | 8760 | 7301.3969 | 3361.9726 | 3939.4243 | 7301.1473 | 3780.0236 | 4476.8412 | 20412.6995 | 12997.1985 | 0 | 15438.2279 | 8760 | 24183.367 | 765.675 | 663.875 | 2346.175 | 2649820.8439 | 155104.6653 | 2720.775
210 | C | SOK | NAP | FC | ET | WC | R60 | 2.9879 | 44.5 | 3.35 | 8760 | 189625.1527 | 0 | 106702.1424 | 65533.1035 | 57958.323 | 85546.5 | 270897.25 | 192479.625 | 171093 | 87287.424 | 8760 | 1720.1251 | 19278.432 | 0 | 0 | 288.0549 | 1222.1089 | 5261.6913 | -1645.4937 | 7852.1626 | 3581.671 | 8760 | 7300.8067 | 3036.3954 | 4264.4113 | 7301.1473 | 3780.0236 | 4493.2011 | 20414.4318 | 13003.7277 | 0 | 16400.5047 | 8760 | 24195.9097 | 850.075 | 575.7 | 2346.175 | 2649691.1079 | 155104.6653 | 2657.15
211 | C | SOK | NAP | FC | FP | HC | OFF0 | 0.22955 | 11.5 | 0.288 | 8760 | 150620.0431 | 0 | 109827.934 | 0 | 29538.1641 | 53074.5 | 123840.5 | 119417.625 | 106149 | 147061.6699 | 8760 | 1720.1251 | 6960.4635 | 0 | 0 | 0 | 383.7776 | 6573.9044 | -1432.4525 | 2870.9559 | 2839.8409 | 8760 | 5746.6975 | 3931.1174 | 1815.5801 | 5745.6847 | 641.83 | 0 | 14465.1389 | 9100.2105 | 0 | 4955.0234 | 8760 | 0 | 258.8 | 625.775 | 2468.675 | 2115999.0482 | 110654.3789 | 2401.3 | -262.6325
212 | C | SOK | NAP | FC | FP | HC | OFF0 | 0.22955 | 11.5 | 0.575 | 8760 | 150943.9156 | 0 | 106813.135 | 0 | 29538.1641 | 53133 | 123977 | 119549.25 | 106266 | 146268.9587 | 8760 | 1720.1251 | 7096.5253 | 0 | 0 | 0 | 297.728 | 6565.1124 | -1491.1711 | 2881.4473 | 2797.822 | 8760 | 5746.5327 | 3920.0645 | 1826.4683 | 5745.6847 | 641.83 | 0 | 14464.8933 | 9101.8615 | 0 | 5128.4993 | 8760 | 0 | 259.225 | 626.325 | 2468.675 | 2116535.3712 | 110654.3789 | 2421.875 | -263.8668
213 | C | SOK | NAP | FC | FP | HC | OFF0 | 0.22955 | 11.5 | 0.863 | 8760 | 151124.8747 | 0 | 105565.9682 | 0 | 29538.1641 | 53164.5 | 124050.5 | 119620.125 | 106329 | 146307.295 | 8760 | 1720.1251 | 7154.0676 | 0 | 0 | 0 | 257.8281 | 6565.3665 | -1514.4267 | 2878.7722 | 2780.6843 | 8760 | 5746.6228 | 3920.9732 | 1825.6497 | 5745.6847 | 641.83 | 0 | 14460.8253 | 9102.4482 | 0 | 5199.4897 | 8760 | 0 | 259.275 | 626.8 | 2468.675 | 2116673.9737 | 110654.3789 | 2428.375 | -267.8426
214 | C | SOK | NAP | FC | FP | HC | OFF0 | 0.22955 | 15.5 | 0.388 | 8760 | 149607.0157 | 0 | 102832.4004 | 0 | 29538.1641 | 51951 | 121219 | 116889.75 | 103902 | 120793.722 | 8760 | 1720.1251 | 8367.64 | 0 | 0 | 0 | 286.6801 | 5446.2357 | -1504.5726 | 3948.105 | 2891.0694 | 8760 | 5745.7273 | 3250.2501 | 2495.4773 | 5745.6847 | 641.83 | 0 | 14479.7776 | 9090.8087 | 0 | 6282.9284 | 8760 | 0 | 350.2 | 515.65 | 2468.675 | 2116197.1339 | 110654.3789 | 2548.575 | -218.745
215 | C | SOK | NAP | FC | FP | HC | OFF0 | 0.22955 | 15.5 | 0.775 | 8760 | 151573.7715 | 0 | 100387.5634 | 0 | 29538.1641 | 51799.5 | 120865.5 | 116548.875 | 103599 | 120059.2837 | 8760 | 1720.1251 | 8637.2248 | 0 | 0 | 0 | 210.1342 | 5305.2301 | -1564.8057 | 4077.8384 | 2856.167 | 8760 | 5746.6137 | 3168.262 | 2578.3517 | 5745.6847 | 641.83 | 0 | 14475.919 | 9089.272 | 0 | 6579.9029 | 8760 | 0 | 361.175 | 502.15 | 2468.675 | 2116605.7973 | 110654.3789 | 2547.35 | -217.1363
216 | C | SOK | NAP | FC | FP | HC | OFF0 | 0.22955 | 15.5 | 1.163 | 8760 | 152981.8718 | 0 | 99047.4028 | 0 | 29538.1641 | 51781.5 | 120823.5 | 116508.375 | 103563 | 118309.5317 | 8760 | 1720.1251 | 8804.3003 | 0 | 0 | 0 | 177.6898 | 5196.032 | -1588.5427 | 4176.6695 | 2836.2935 | 8760 | 5746.711 | 3106.4945 | 2640.2165 | 5745.6847 | 641.83 | 0 | 14474.9603 | 9089.7936 | 0 | 6764.3957 | 8760 | 0 | 371.125 | 491.9 | 2468.675 | 2116575.7037 | 110654.3789 | 2539.375 | -214.5027
217 | C | SOK | NAP | FC | FP | HC | OFF0 | 0.22955 | 20 | 0.5 | 8760 | 147898.9493 | 0 | 98015.4716 | 0 | 29538.1641 | 50755.5 | 118429.5 | 114199.875 | 101511 | 93017.8864 | 8760 | 1720.1251 | 9544.465 | 0 | 0 | 0 | 213.1279 | 4550.4575 | -1564.1868 | 4808.4019 | 2914.4079 | 8760 | 5746.0085 | 2709.2584 | 3036.7501 | 5745.6847 | 641.83 | 0 | 14501.6602 | 9079.0266 | 0 | 7398.1802 | 8760 | 0 | 420.075 | 425.85 | 2468.675 | 2116157.1055 | 110654.3789 | 2707.95 | -158.1155
218 | C | SOK | NAP | FC | FP | HC | OFF0 | 0.22955 | 20 | 1 | 8760 | 151896.4429 | 0 | 94794.4363 | 0 | 29538.1641 | 50548.5 | 117946.5 | 113734.125 | 101097 | 89578.3567 | 8760 | 1720.1251 | 10015.4161 | 0 | 0 | 0 | 138.1779 | 4226.7957 | -1619.8076 | 5108.2875 | 2885.1964 | 8760 | 5745.7991 | 2521.3533 | 3224.4458 | 5745.6847 | 641.83 | 0 | 14498.5564 | 9077.8541 | 0 | 7893.5333 | 8760 | 0 | 447.65 | 394.825 | 2468.675 | 2115981.0518 | 110654.3789 | 2680.275 | -152.569
219 | C | SOK | NAP | FC | FP | HC | OFF0 | 0.22955 | 20 | 1.5 | 8760 | 153803.9151 | 0 | 94183.2271 | 0 | 29538.1641 | 50478 | 117782 | 113575.5 | 100956 | 86191.2555 | 8760 | 1720.1251 | 10244.94 | 0 | 0 | 0 | 121.2044 | 4044.0529 | -1645.2131 | 5275.1297 | 2872.6803 | 8760 | 5746.0087 | 2415.7118 | 3330.2969 | 5745.6847 | 641.83 | 0 | 14499.4657 | 9078.8569 | 0 | 8134.1435 | 8760 | 0 | 463.05 | 378.25 | 2468.675 | 2116361.452 | 110654.3789 | 2666.675 | -149.5245
220 | C | SOK | NAP | FC | FP | HC | OFF | 0.22955 | 24 | 0.6 | 8760 | 146389.2279 | 0 | 95479.8906 | 0 | 29538.1641 | 50622 | 118118 | 113899.5 | 101244 | 92653.6309 | 8760 | 1720.1251 | 10355.7383 | 0 | 0 | 0 | 166.9192 | 4246.2505 | -1601.7187 | 5178.3302 | 2917.2203 | 8760 | 5746.1945 | 2475.4915 | 3270.703 | 5745.6847 | 641.83 | 0 | 14481.1926 | 9074.0845 | 0 | 8175.0615 | 8760 | 0 | 455.125 | 388.575 | 2468.675 | 2116062.7092 | 110654.3789 | 2834.225 | -180.9644
221 | C | SOK | NAP | FC | FP | HC | OFF | 0.22955 | 24 | 1.2 | 8760 | 151223.4022 | 0 | 91868.8814 | 0 | 29538.1641 | 50128.5 | 116966.5 | 112789.125 | 100257 | 86786.3483 | 8760 | 1720.1251 | 10931.9579 | 0 | 0 | 0 | 92.4438 | 3733.6952 | -1655.4233 | 5626.5981 | 2889.3537 | 8760 | 5745.7427 | 2194.7259 | 3551.0168 | 5745.6847 | 641.83 | 0 | 14481.6521 | 9068.537 | 0 | 8777.4591 | 8760 | 0 | 494.625 | 340.85 | 2468.675 | 2116052.2983 | 110654.3789 | 2797.475 | -159.1671
222 | C | SOK | NAP | FC | FP | HC | OFF | 0.22955 | 24 | 1.8 | 8760 | 154137.1482 | 0 | 90319.4847 | 0 | 29538.1641 | 49936.5 | 116518.5 | 112357.125 | 99873 | 83476.3545 | 8760 | 1720.1251 | 11227.3798 | 0 | 0 | 0 | 63.6296 | 3392.1454 | -1674.6489 | 5914.5157 | 2887.5461 | 8760 | 5746.6818 | 2013.8997 | 3732.7821 | 5745.6847 | 641.83 | 0 | 14485.7835 | 9070.8776 | 0 | 9075.3757 | 8760 | 0 | 520.5 | 311.775 | 2468.675 | 2115789.596 | 110654.3789 | 2770.1 | -149.9972
223 | C | SOK | NAP | FC | FP | HC | OFF | 0.22955 | 28.5 | 0.713 | 8760 | 141979.7989 | 0 | 92437.3435 | 0 | 29538.1641 | 49729.5 | 116035.5 | 111891.375 | 99459 | 82851.1362 | 8760 | 1720.1251 | 10541.8295 | 0 | 0 | 0 | 126.253 | 3605.9147 | -1633.6724 | 5748.7919 | 2922.9645 | 8760 | 5746.4025 | 2111.1599 | 3635.2426 | 5745.6847 | 641.83 | 0 | 14470.1639 | 9058.3598 | 0 | 8337.5895 | 8760 | 0 | 500.125 | 328.7 | 2468.675 | 2115600.1785 | 110654.3789 | 2982.5 | -171.9541
224 | C | SOK | NAP | FC | FP | HC | OFF | 0.22955 | 28.5 | 1.425 | 8760 | 147746.476 | 0 | 88562.3518 | 0 | 29538.1641 | 49197 | 114793 | 110693.25 | 98394 | 75289.9524 | 8760 | 1720.1251 | 11237.4819 | 0 | 0 | 0 | 51.5771 | 3028.8727 | -1685.9006 | 6253.5891 | 2903.3091 | 8760 | 5745.8143 | 1798.4105 | 3947.4039 | 5745.6847 | 641.83 | 0 | 14481.3566 | 9053.5201 | 0 | 9052.1685 | 8760 | 0 | 545.625 | 274.325 | 2468.675 | 2115737.2552 | 110654.3789 | 2937.45 | -136.4046
225 | C | SOK | NAP | FC | FP | HC | OFF | 0.22955 | 28.5 | 2.138 | 8760 | 151172.2879 | 0 | 86363.4984 | 0 | 29538.1641 | 48964.5 | 114250.5 | 110170.125 | 97929 | 75123.8156 | 8760 | 1720.1251 | 11708.516 | 0 | 0 | 0 | 8.1615 | 2698.0653 | -1705.486 | 6544.0998 | 2892.4579 | 8760 | 5745.464 | 1613.1225 | 4132.3414 | 5745.6847 | 641.83 | 0 | 14477.2078 | 9050.0338 | 0 | 9529.1131 | 8760 | 0 | 571.725 | 244.35 | 2468.675 | 2115783.2882 | 110654.3789 | 2911.875 | -132.8927
226 | C | SOK | NAP | FC | FP | HC | R100 | 1.6444 | 11.5 | 0.288 | 8760 | 159131.7701 | 0 | 144979.5904 | 65533.1035 | 84103.8032 | 37641 | 87829 | 84692.25 | 75282 | 62941.3992 | 8760 | 1720.1251 | 7543.3597 | 0 | 0 | 719.5829 | 4149.9108 | 5468.2292 | -1190.9143 | 1456.1647 | 2849.2322 | 8760 | 4248.8991 | 3379.7713 | 869.1278 | 4247.8969 | 4796.318 | 2575.3042 | 10643.5312 | 6624.8948 | 0 | 5639.4851 | 8760 | 0 | 145.125 | 482.225 | 2227.75 | 1524867.1383 | 178372.614 | 2139.6 | -117.4514
227 | C | SOK | NAP | FC | FP | HC | R100 | 1.6444 | 11.5 | 0.575 | 8760 | 161969.3843 | 0 | 141442.8262 | 65533.1035 | 84103.8032 | 37789.5 | 88175.5 | 85026.375 | 75579 | 57964.143 | 8760 | 1720.1251 | 7861.0852 | 0 | 0 | 635.5839 | 3962.2215 | 5469.0542 | -1257.9903 | 1456.9224 | 2805.0236 | 8760 | 4248.9137 | 3371.7157 | 877.198 | 4247.8969 | 4796.318 | 2582.7469 | 10650.2827 | 6631.6834 | 0 | 6002.2305 | 8760 | 0 | 143.725 | 486.1 | 2227.75 | 1524881.9648 | 178372.614 | 2129.35 | -118.2527
228 | C | SOK | NAP | FC | FP | HC | R100 | 1.6444 | 11.5 | 0.863 | 8760 | 163042.0286 | 0 | 139714.9414 | 65533.1035 | 84103.8032 | 37857 | 88333 | 85178.25 | 75714 | 57703.8612 | 8760 | 1720.1251 | 8008.6417 | 0 | 0 | 621.212 | 3873.0165 | 5430.6855 | -1278.2976 | 1492.315 | 2779.4716 | 8760 | 4248.8017 | 3340.2904 | 908.5113 | 4247.8969 | 4796.318 | 2583.9347 | 10651.9168 | 6634.827 | 0 | 6177.0712 | 8760 | 0 | 145 | 485.95 | 2227.75 | 1524842.141 | 178372.614 | 2132.825 | -116.1877
229 | C | SOK | NAP | FC | FP | HC | R100 | 1.6444 | 15.5 | 0.388 | 8760 | 156518.3438 | 0 | 137270.1044 | 65533.1035 | 84103.8032 | 36627 | 85463 | 82410.75 | 73254 | 48202.3389 | 8760 | 1720.1251 | 8908.8468 | 0 | 0 | 608.3038 | 3796.2085 | 4809.4473 | -1281.3643 | 2063.0555 | 2939.3976 | 8760 | 4248.94 | 3010.1479 | 1238.7921 | 4247.8969 | 4796.318 | 2587.5186 | 10637.4394 | 6604.7416 | 0 | 6879.0188 | 8760 | 0 | 198.625 | 411.825 | 2227.75 | 1524885.3706 | 178372.614 | 2312.95 | -89.4383
230 | C | SOK | NAP | FC | FP | HC | R100 | 1.6444 | 15.5 | 0.775 | 8760 | 159662.1367 | 0 | 133060.6351 | 65533.1035 | 84103.8032 | 36682.5 | 85592.5 | 82535.625 | 73365 | 47035.8352 | 8760 | 1720.1251 | 9362.6512 | 0 | 0 | 531.747 | 3575.357 | 4699.7199 | -1345.5369 | 2161.3757 | 2897.6788 | 8760 | 4248.0253 | 2932.5583 | 1315.467 | 4247.8969 | 4796.318 | 2592.4285 | 10638.8269 | 6609.1181 | 0 | 7373.0578 | 8760 | 0 | 203.75 | 407.625 | 2227.75 | 1524742.3751 | 178372.614 | 2308.525 | -85.4447
231 | C | SOK | NAP | FC | FP | HC | R100 | 1.6444 | 15.5 | 1.163 | 8760 | 161532.5282 | 0 | 130937.5266 | 65533.1035 | 84103.8032 | 36760.5 | 85774.5 | 82711.125 | 73521 | 46038.32 | 8760 | 1720.1251 | 9590.6484 | 0 | 0 | 527.1796 | 3453.3932 | 4589.207 | -1363.2894 | 2262.8745 | 2869.7465 | 8760 | 4248.107 | 2857.9793 | 1390.1277 | 4247.8969 | 4796.318 | 2593.3461 | 10640.2759 | 6613.8645 | 0 | 7627.4197 | 8760 | 0 | 210.85 | 401.825 | 2227.75 | 1524773.9063 | 178372.614 | 2302.1 | -88.5196
232 | C | SOK | NAP | FC | FP | HC | R100 | 1.6444 | 20 | 0.5 | 8760 | 154144.3481 | 0 | 130550.5524 | 65533.1035 | 84103.8032 | 35893.5 | 83751.5 | 80760.375 | 71787 | 34053.691 | 8760 | 1720.1251 | 10060.6545 | 0 | 0 | 525.4993 | 3444.2253 | 4329.1355 | -1350.0197 | 2509.2166 | 2993.6742 | 8760 | 4248.9614 | 2732.9832 | 1515.9782 | 4247.8969 | 4796.318 | 2595.0824 | 10644.1194 | 6593.825 | 0 | 7931.7505 | 8760 | 0 | 235.375 | 362.85 | 2227.75 | 1524447.1407 | 178372.614 | 2484.925 | -52.914
233 | C | SOK | NAP | FC | FP | HC | R100 | 1.6444 | 20 | 1 | 8760 | 158306.7077 | 0 | 125558.8852 | 65533.1035 | 84103.8032 | 35820 | 83580 | 80595 | 71640 | 32848.5955 | 8760 | 1720.1251 | 10704.6381 | 0 | 0 | 457.618 | 3176.3718 | 4068.3412 | -1409.5425 | 2742.4904 | 2951.8324 | 8760 | 4248.8034 | 2566.9262 | 1681.8772 | 4247.8969 | 4796.318 | 2599.9578 | 10642.4232 | 6595.6087 | 0 | 8618.9073 | 8760 | 0 | 251.675 | 345.325 | 2227.75 | 1524328.8632 | 178372.614 | 2470.95 | -50.1221
234 | C | SOK | NAP | FC | FP | HC | R100 | 1.6444 | 20 | 1.5 | 8760 | 160828.954 | 0 | 122607.082 | 65533.1035 | 84103.8032 | 35800.5 | 83534.5 | 80551.125 | 71601 | 32690.7303 | 8760 | 1720.1251 | 11058.5294 | 0 | 0 | 460.4578 | 3010.6013 | 3853.3225 | -1424.7611 | 2943.6997 | 2925.4992 | 8760 | 4248.8315 | 2421.0316 | 1827.7999 | 4247.8969 | 4796.318 | 2599.3496 | 10646.4828 | 6598.4107 | 0 | 8998.6233 | 8760 | 0 | 265.05 | 331.625 | 2227.75 | 1524485.4967 | 178372.614 | 2458.375 | -45.0692
235 | C | SOK | NAP | FC | FP | HC | R10 | 1.6444 | 24 | 0.6 | 8760 | 152831.3729 | 0 | 126240.5898 | 65533.1035 | 84103.8032 | 35731.5 | 83373.5 | 80395.875 | 71463 | 35627.3184 | 8760 | 1720.1251 | 10902.3132 | 0 | 0 | 471.6691 | 3188.4591 | 4135.7019 | -1394.3056 | 2718.3929 | 3013.6145 | 8760 | 4248.2058 | 2596.75 | 1651.4559 | 4247.8969 | 4796.318 | 2600.348 | 10617.9487 | 6586.3389 | 0 | 8722.6316 | 8760 | 0 | 254.4 | 341.125 | 2227.75 | 1524359.7428 | 178372.614 | 2618.55 | -76.9199
236 | C | SOK | NAP | FC | FP | HC | R10 | 1.6444 | 24 | 1.2 | 8760 | 158475.5479 | 0 | 120318.2346 | 65533.1035 | 84103.8032 | 35478 | 82782 | 79825.5 | 70956 | 35745.047 | 8760 | 1720.1251 | 11710.2438 | 0 | 0 | 411.1267 | 2866.8269 | 3686.1603 | -1451.8363 | 3095.301 | 2977.799 | 8760 | 4247.9682 | 2331.4516 | 1916.5166 | 4247.8969 | 4796.318 | 2604.5591 | 10615.7615 | 6584.7278 | 0 | 9569.2555 | 8760 | 0 | 280.525 | 310.775 | 2227.75 | 1524549.5949 | 178372.614 | 2584.6 | -68.4288
237 | C | SOK | NAP | FC | FP | HC | R10 | 1.6444 | 24 | 1.8 | 8760 | 160395.2354 | 0 | 117232.9403 | 65533.1035 | 84103.8032 | 35395.5 | 82589.5 | 79639.875 | 70791 | 34880.0446 | 8760 | 1720.1251 | 12110.5128 | 0 | 0 | 399.7517 | 2683.7775 | 3413.2797 | -1464.1229 | 3360.5045 | 2942.5452 | 8760 | 4248.7702 | 2141.6251 | 2107.1451 | 4247.8969 | 4796.318 | 2602.9393 | 10620.8356 | 6589.1858 | 0 | 10002.8837 | 8760 | 0 | 297.675 | 292.25 | 2227.75 | 1524435.4859 | 178372.614 | 2585.925 | -65.2508
238 | C | SOK | NAP | FC | FP | HC | R10 | 1.6444 | 28.5 | 0.713 | 8760 | 149599.2571 | 0 | 121680.1438 | 65533.1035 | 84103.8032 | 35206.5 | 82148.5 | 79214.625 | 70413 | 35640.9384 | 8760 | 1720.1251 | 11255.0916 | 0 | 0 | 424.5724 | 2927.6086 | 3841.9167 | -1434.3811 | 2970.853 | 3029.6992 | 8760 | 4248.8921 | 2427.314 | 1821.5781 | 4247.8969 | 4796.318 | 2605.0155 | 10591.0745 | 6572.7473 | 0 | 9036.3865 | 8760 | 0 | 271.525 | 315.25 | 2227.75 | 1524483.8946 | 178372.614 | 2768.4 | -95.6159
239 | C | SOK | NAP | FC | FP | HC | R10 | 1.6444 | 28.5 | 1.425 | 8760 | 156590.6712 | 0 | 115094.0829 | 65533.1035 | 84103.8032 | 34846.5 | 81308.5 | 78404.625 | 69693 | 34450.2093 | 8760 | 1720.1251 | 12279.0399 | 0 | 0 | 369.8449 | 2566.6675 | 3291.0574 | -1492.5189 | 3469.3495 | 2996.3005 | 8760 | 4248.1406 | 2078.2724 | 2169.8682 | 4247.8969 | 4796.318 | 2608.6686 | 10584.8527 | 6568.9369 | 0 | 10098.062 | 8760 | 0 | 306.45 | 274.325 | 2227.75 | 1524113.1249 | 178372.614 | 2723.85 | -87.5177
240 | C | SOK | NAP | FC | FP | HC | R10 | 1.6444 | 28.5 | 2.138 | 8760 | 159703.3353 | 0 | 111411.8284 | 65533.1035 | 84103.8032 | 34728 | 81032 | 78138 | 69456 | 33505.1951 | 8760 | 1720.1251 | 12897.6333 | 0 | 0 | 357.5274 | 2324.0877 | 2921.7974 | -1504.7533 | 3814.8345 | 2953.4564 | 8760 | 4247.9355 | 1832.7765 | 2415.1591 | 4247.8969 | 4796.318 | 2608.5564 | 10594.1694 | 6571.8055 | 0 | 10755.2675 | 8760 | 0 | 330 | 248.8 | 2227.75 | 1524442.7147 | 178372.614 | 2714.25 | -75.9173
241 | C | SOK | NAP | FC | FP | HC | R600 | 1.8872 | 11.5 | 0.288 | 8760 | 160151.9905 | 0 | 129786.3534 | 65533.1035 | 51088.7482 | 40296 | 94024 | 90666 | 80592 | 64904.851 | 8760 | 1720.1251 | 7546.4825 | 0 | 0 | 671.7481 | 2116.2383 | 5977.8378 | -1235.1639 | 1492.6569 | 2782.8933 | 8760 | 4611.7455 | 3718.7105 | 893.035 | 4611.5962 | 2387.5621 | 2912.026 | 11538.4009 | 7156.6807 | 0 | 5609.9718 | 8760 | 0 | 148.2 | 523.4 | 2346.175 | 1648451.1025 | 155104.6653 | 2134.05 | -119.1953
242 | C | SOK | NAP | FC | FP | HC | R600 | 1.8872 | 11.5 | 0.575 | 8760 | 163229.261 | 0 | 126865.2981 | 65533.1035 | 51088.7482 | 40440 | 94360 | 90990 | 80880 | 58776.6087 | 8760 | 1720.1251 | 7848.0839 | 0 | 0 | 566.7001 | 1990.7212 | 5970.188 | -1304.8387 | 1499.029 | 2750.3167 | 8760 | 4611.6369 | 3705.18 | 906.4569 | 4611.5962 | 2387.5621 | 2930.186 | 11541.6918 | 7163.8946 | 0 | 5946.515 | 8760 | 0 | 146.65 | 527.35 | 2346.175 | 1648313.1518 | 155104.6653 | 2118.275 | -120.4964
243 | C | SOK | NAP | FC | FP | HC | R600 | 1.8872 | 11.5 | 0.863 | 8760 | 164254.331 | 0 | 124599.6992 | 65533.1035 | 51088.7482 | 40513.5 | 94531.5 | 91155.375 | 81027 | 57508.5327 | 8760 | 1720.1251 | 7994.7307 | 0 | 0 | 557.2317 | 1908.0986 | 5936.4405 | -1326.235 | 1533.0072 | 2723.6047 | 8760 | 4611.4917 | 3672.0324 | 939.4594 | 4611.5962 | 2387.5621 | 2934.2851 | 11542.5567 | 7166.8143 | 0 | 6119.842 | 8760 | 0 | 147.025 | 528.2 | 2346.175 | 1648304.2192 | 155104.6653 | 2125.5 | -120.9997
244 | C | SOK | NAP | FC | FP | HC | R600 | 1.8872 | 15.5 | 0.388 | 8760 | 157234.2266 | 0 | 123528.7706 | 65533.1035 | 51088.7482 | 39261 | 91609 | 88337.25 | 78522 | 48490.2469 | 8760 | 1720.1251 | 8847.3547 | 0 | 0 | 538.815 | 1910.5646 | 5288.0092 | -1336.4402 | 2128.6176 | 2883.6325 | 8760 | 4611.6328 | 3326.3184 | 1285.3144 | 4611.5962 | 2387.5621 | 2938.5071 | 11529.5075 | 7137.0124 | 0 | 6774.5611 | 8760 | 0 | 202.85 | 451.5 | 2346.175 | 1648168.6818 | 155104.6653 | 2313.475 | -92.8851
245 | C | SOK | NAP | FC | FP | HC | R600 | 1.8872 | 15.5 | 0.775 | 8760 | 160614.6143 | 0 | 119490.2898 | 65533.1035 | 51088.7482 | 39283.5 | 91661.5 | 88387.875 | 78567 | 46506.1418 | 8760 | 1720.1251 | 9271.9917 | 0 | 0 | 454.9942 | 1761.8529 | 5168.4062 | -1406.5206 | 2235.4346 | 2849.0855 | 8760 | 4611.6605 | 3244.4808 | 1367.1797 | 4611.5962 | 2387.5621 | 2951.7138 | 11530.1935 | 7140.656 | 0 | 7230.8518 | 8760 | 0 | 208.7 | 446.025 | 2346.175 | 1648096.0677 | 155104.6653 | 2304.275 | -90.3758
246 | C | SOK | NAP | FC | FP | HC | R600 | 1.8872 | 15.5 | 1.163 | 8760 | 162483.4901 | 0 | 117211.9417 | 65533.1035 | 51088.7482 | 39328.5 | 91766.5 | 88489.125 | 78657 | 47005.0516 | 8760 | 1720.1251 | 9518.5673 | 0 | 0 | 445.4094 | 1654.7271 | 5039.7239 | -1423.4527 | 2355.3823 | 2821.3649 | 8760 | 4612.2905 | 3155.4415 | 1456.849 | 4611.5962 | 2387.5621 | 2952.0623 | 11534.102 | 7144.1471 | 0 | 7504.7713 | 8760 | 0 | 216.55 | 438.925 | 2346.175 | 1648449.1002 | 155104.6653 | 2300.5 | -88.3571
247 | C | SOK | NAP | FC | FP | HC | R600 | 1.8872 | 20 | 0.5 | 8760 | 154316.4979 | 0 | 117821.6511 | 65533.1035 | 51088.7482 | 38452.5 | 89722.5 | 86518.125 | 76905 | 34185.254 | 8760 | 1720.1251 | 9893.8828 | 0 | 0 | 449.3181 | 1716.5195 | 4783.7962 | -1412.4049 | 2593.3502 | 2942.1454 | 8760 | 4611.7908 | 3038.0611 | 1573.7296 | 4611.5962 | 2387.5621 | 2954.6141 | 11532.7573 | 7122.9945 | 0 | 7718.1765 | 8760 | 0 | 241.225 | 399.65 | 2346.175 | 1647950.0769 | 155104.6653 | 2491.8 | -58.0888
248 | C | SOK | NAP | FC | FP | HC | R600 | 1.8872 | 20 | 1 | 8760 | 158608.5486 | 0 | 112776.7374 | 65533.1035 | 51088.7482 | 38395.5 | 89589.5 | 86389.875 | 76791 | 33020.4371 | 8760 | 1720.1251 | 10515.9279 | 0 | 0 | 384.8115 | 1524.5597 | 4497.9597 | -1477.1482 | 2852.4508 | 2903.0808 | 8760 | 4611.6732 | 2852.8049 | 1758.8683 | 4611.5962 | 2387.5621 | 2965.381 | 11531.4477 | 7126.0566 | 0 | 8377.8284 | 8760 | 0 | 259 | 380.925 | 2346.175 | 1647943.6022 | 155104.6653 | 2480.275 | -54.4981
249 | C | SOK | NAP | FC | FP | HC | R600 | 1.8872 | 20 | 1.5 | 8760 | 160657.805 | 0 | 109583.4503 | 65533.1035 | 51088.7482 | 38410.5 | 89624.5 | 86423.625 | 76821 | 32886.3838 | 8760 | 1720.1251 | 10852.6016 | 0 | 0 | 379.1767 | 1378.8966 | 4278.9802 | -1489.6707 | 3064.6444 | 2868.2937 | 8760 | 4612.2096 | 2701.5692 | 1910.6404 | 4611.5962 | 2387.5621 | 2964.7574 | 11537.8767 | 7130.3144 | 0 | 8746.4573 | 8760 | 0 | 273.925 | 366.25 | 2346.175 | 1648046.1468 | 155104.6653 | 2477.45 | -50.1028
250 | C | SOK | NAP | FC | FP | HC | R60 | 1.8872 | 24 | 0.6 | 8760 | 152553.0639 | 0 | 114248.8893 | 65533.1035 | 51088.7482 | 38254.5 | 89260.5 | 86072.625 | 76509 | 35618.3617 | 8760 | 1720.1251 | 10601.8135 | 0 | 0 | 395.7479 | 1583.7622 | 4565.117 | -1461.4909 | 2824.6251 | 2962.7112 | 8760 | 4611.9744 | 2888.0878 | 1723.8866 | 4611.5962 | 2387.5621 | 2964.1675 | 11511.4006 | 7115.97 | 0 | 8373.2686 | 8760 | 0 | 261.525 | 376.05 | 2346.175 | 1647932.5069 | 155104.6653 | 2629.375 | -76.7536
251 | C | SOK | NAP | FC | FP | HC | R60 | 1.8872 | 24 | 1.2 | 8760 | 157442.689 | 0 | 108604.0156 | 65533.1035 | 51088.7482 | 38056.5 | 88798.5 | 85627.125 | 76113 | 34606.2624 | 8760 | 1720.1251 | 11381.8311 | 0 | 0 | 346.1782 | 1344.9025 | 4121.2746 | -1520.5241 | 3220.0153 | 2920.9571 | 8760 | 4611.5556 | 2612.1279 | 1999.4277 | 4611.5962 | 2387.5621 | 2973.2168 | 11509.0388 | 7116.3631 | 0 | 9195.1605 | 8760 | 0 | 289.975 | 344.3 | 2346.175 | 1647678.6179 | 155104.6653 | 2616.875 | -69.9234
252 | C | SOK | NAP | FC | FP | HC | R60 | 1.8872 | 24 | 1.8 | 8760 | 160182.6402 | 0 | 105025.2542 | 65533.1035 | 51088.7482 | 37966.5 | 88588.5 | 85424.625 | 75933 | 35230.0337 | 8760 | 1720.1251 | 11803.6055 | 0 | 0 | 319.4826 | 1193.6599 | 3819.5867 | -1538.2356 | 3505.8941 | 2892.3842 | 8760 | 4611.6518 | 2406.1709 | 2205.4809 | 4611.5962 | 2387.5621 | 2973.5579 | 11509.7139 | 7118.7335 | 0 | 9641.2434 | 8760 | 0 | 308.75 | 324.025 | 2346.175 | 1648003.5866 | 155104.6653 | 2605.25 | -71.0275
253 | C | SOK | NAP | FC | FP | HC | R60 | 1.8872 | 28.5 | 0.713 | 8760 | 148494.8691 | 0 | 110428.644 | 65533.1035 | 51088.7482 | 37722 | 88018 | 84874.5 | 75444 | 36810.9981 | 8760 | 1720.1251 | 10871.0844 | 0 | 0 | 351.8946 | 1435.4369 | 4264.2178 | -1502.3589 | 3091.1617 | 2977.6793 | 8760 | 4612.593 | 2710.1267 | 1902.4663 | 4611.5962 | 2387.5621 | 2971.9735 | 11479.4153 | 7101.3325 | 0 | 8603.7053 | 8760 | 0 | 280.325 | 348.375 | 2346.175 | 1647948.2657 | 155104.6653 | 2791.9 | -101.9201
254 | C | SOK | NAP | FC | FP | HC | R60 | 1.8872 | 28.5 | 1.425 | 8760 | 154347.2738 | 0 | 104888.0133 | 65533.1035 | 51088.7482 | 37398 | 87262 | 84145.5 | 74796 | 32986.4712 | 8760 | 1720.1251 | 11805.3452 | 0 | 0 | 302.4252 | 1184.7275 | 3699.2903 | -1559.9591 | 3604.572 | 2933.9604 | 8760 | 4611.6102 | 2352.0878 | 2259.5224 | 4611.5962 | 2387.5621 | 2978.942 | 11490.3187 | 7100.6689 | 0 | 9581.0746 | 8760 | 0 | 316.475 | 306.825 | 2346.175 | 1647883.9497 | 155104.6653 | 2772.375 | -73.7871
255 | C | SOK | NAP | FC | FP | HC | R60 | 1.8872 | 28.5 | 2.138 | 8760 | 158652.2725 | 0 | 101385.7468 | 65533.1035 | 51088.7482 | 37339.5 | 87125.5 | 84013.875 | 74679 | 33360.4179 | 8760 | 1720.1251 | 12462.7791 | 0 | 0 | 267.2382 | 1030.7046 | 3316.8229 | -1578.3623 | 3973.6712 | 2910.2468 | 8760 | 4611.5919 | 2089.7517 | 2521.8402 | 4611.5962 | 2387.5621 | 2981.3788 | 11490.9536 | 7104.9539 | 0 | 10259.2554 | 8760 | 0 | 342.25 | 280.075 | 2346.175 | 1647941.6913 | 155104.6653 | 2746.45 | -75.3946
256 | C | SOK | NAP | FC | FP | WC | OFF0 | 0.36343 | 18 | 0.45 | 8760 | 157067.659 | 0 | 120957.9419 | 0 | 31184.5118 | 96460.5 | 305458.25 | 217036.125 | 192921 | 176498.3524 | 8760 | 1720.1251 | 9950.1685 | 0 | 0 | 0 | 487.2897 | 10094.4412 | -1506.0316 | 5451.5698 | 2902.1147 | 8760 | 9071.3744 | 5799.8044 | 3271.57 | 9096.653 | 1016.1548 | 0 | 24393.9058 | 15198.2359 | 0 | 7868.6966 | 8760 | 30070.3067 | 533.55 | 1074.125 | 2468.675 | 3408727.8296 | 110654.3789 | 2564.175
257 | C | SOK | NAP | FC | FP | WC | OFF0 | 0.36343 | 18 | 0.9 | 8760 | 158482.3566 | 0 | 118063.8849 | 0 | 31184.5118 | 96478.5 | 305515.25 | 217076.625 | 192957 | 175522.6213 | 8760 | 1720.1251 | 10153.4915 | 0 | 0 | 0 | 362.1693 | 10070.8975 | -1550.575 | 5470.0738 | 2872.7106 | 8760 | 9069.7812 | 5801.6489 | 3268.1323 | 9096.653 | 1016.1548 | 0 | 24388.2335 | 15195.0494 | 0 | 8092.6181 | 8760 | 30067.911 | 540.4 | 1067.575 | 2468.675 | 3408694.027 | 110654.3789 | 2556.875
258 | C | SOK | NAP | FC | FP | WC | OFF0 | 0.36343 | 18 | 1.35 | 8760 | 159459.7162 | 0 | 117352.1823 | 0 | 31184.5118 | 96531 | 305681.5 | 217194.75 | 193062 | 175514.0889 | 8760 | 1720.1251 | 10258.9731 | 0 | 0 | 0 | 323.6061 | 10036.8687 | -1566.1109 | 5502.3034 | 2859.9298 | 8760 | 9070.4731 | 5784.6264 | 3285.8467 | 9096.653 | 1016.1548 | 0 | 24389.1192 | 15198.0306 | 0 | 8213.2485 | 8760 | 30071.0932 | 544.675 | 1064.175 | 2468.675 | 3408169.4325 | 110654.3789 | 2549.85
259 | C | SOK | NAP | FC | FP | WC | OFF0 | 0.36343 | 24.5 | 0.6 | 8760 | 160956.118 | 0 | 113712.675 | 0 | 31184.5118 | 96381 | 305206.5 | 216857.25 | 192762 | 168127.2752 | 8760 | 1720.1251 | 12042.3089 | 0 | 0 | 0 | 359.397 | 8650.4142 | -1565.2229 | 7022.1276 | 2915.5617 | 8760 | 9075.6953 | 4867.124 | 4208.5714 | 9096.653 | 1016.1548 | 0 | 24479.4368 | 15285.2376 | 0 | 9909.4345 | 8760 | 30116.9166 | 680.05 | 926.3 | 2468.675 | 3408731.5084 | 110654.3789 | 2712.375
260 | C | SOK | NAP | FC | FP | WC | OFF0 | 0.36343 | 24.5 | 1.25 | 8760 | 163809.9857 | 0 | 111118.5979 | 0 | 31184.5118 | 96270 | 304855 | 216607.5 | 192540 | 167396.0833 | 8760 | 1720.1251 | 12365.2249 | 0 | 0 | 0 | 245.3929 | 8509.3871 | -1606.6747 | 7156.7658 | 2906.3198 | 8760 | 9073.7379 | 4800.8692 | 4272.8688 | 9096.653 | 1016.1548 | 0 | 24474.883 | 15284.2935 | 0 | 10235.2632 | 8760 | 30108.6123 | 697.35 | 907.15 | 2468.675 | 3408601.5239 | 110654.3789 | 2686.5
261 | C | SOK | NAP | FC | FP | WC | OFF0 | 0.36343 | 24.5 | 1.85 | 8760 | 165314.6052 | 0 | 110473.6409 | 0 | 31184.5118 | 96378 | 305197 | 216850.5 | 192756 | 166613.0823 | 8760 | 1720.1251 | 12545.3083 | 0 | 0 | 0 | 219.9713 | 8417.6344 | -1622.5052 | 7243.8635 | 2893.9393 | 8760 | 9074.8901 | 4757.055 | 4317.8351 | 9096.653 | 1016.1548 | 0 | 24484.7259 | 15293.8874 | 0 | 10430.3847 | 8760 | 30118.3447 | 708.5 | 897.8 | 2468.675 | 3408377.2788 | 110654.3789 | 2675.025
262 | C | SOK | NAP | FC | FP | WC | OFF0 | 0.36343 | 31 | 0.8 | 8760 | 157459.4153 | 0 | 108707.5087 | 0 | 31184.5118 | 95026.5 | 300917.25 | 213809.625 | 190053 | 172229.7025 | 8760 | 1720.1251 | 12664.5226 | 0 | 0 | 0 | 268.045 | 7535.4384 | -1618.3991 | 8096.1894 | 2930.263 | 8760 | 9081.3424 | 4200.0106 | 4881.3318 | 9096.653 | 1016.1548 | 0 | 24487.7868 | 15286.1776 | 0 | 10486.0523 | 8760 | 30087.3808 | 767.2 | 816.575 | 2468.675 | 3408896.1895 | 110654.3789 | 2909.4
263 | C | SOK | NAP | FC | FP | WC | OFF0 | 0.36343 | 31 | 1.55 | 8760 | 161468.756 | 0 | 105662.7117 | 0 | 31184.5118 | 95149.5 | 301306.75 | 214086.375 | 190299 | 171301.1714 | 8760 | 1720.1251 | 13220.7277 | 0 | 0 | 0 | 169.8949 | 7233.4104 | -1655.5497 | 8390.5353 | 2914.5602 | 8760 | 9084.2244 | 4057.5933 | 5026.6311 | 9096.653 | 1016.1548 | 0 | 24512.4821 | 15310.797 | 0 | 11056.241 | 8760 | 30115.5469 | 804.55 | 781.275 | 2468.675 | 3408660.6235 | 110654.3789 | 2880.225
264 | C | SOK | NAP | FC | FP | WC | OFF0 | 0.36343 | 31 | 2.35 | 8760 | 163250.5986 | 0 | 105119.7479 | 0 | 31184.5118 | 95076 | 301074 | 213921 | 190152 | 171366.3181 | 8760 | 1720.1251 | 13480.3221 | 0 | 0 | 0 | 145.5558 | 7069.6023 | -1671.6024 | 8538.6003 | 2900.1999 | 8760 | 9083.3101 | 3982.6202 | 5100.6899 | 9096.653 | 1016.1548 | 0 | 24503.1212 | 15305.6543 | 0 | 11330.7036 | 8760 | 30105.8425 | 824.75 | 759.85 | 2468.675 | 3408755.8874 | 110654.3789 | 2867.175
265 | C | SOK | NAP | FC | FP | WC | OFF | 0.36343 | 38 | 0.95 | 8760 | 157844.0384 | 0 | 105000.5058 | 0 | 31184.5118 | 94473 | 299164.5 | 212564.25 | 188946 | 169781.6352 | 8760 | 1720.1251 | 13413.5163 | 0 | 0 | 0 | 204.8312 | 6694.3491 | -1651.7079 | 8902.7245 | 2925.9467 | 8760 | 9084.815 | 3731.6326 | 5353.1825 | 9096.653 | 1016.1548 | 0 | 24534.5564 | 15329.0246 | 0 | 11219.8075 | 8760 | 30094.6061 | 837.925 | 736.625 | 2468.675 | 3408605.6648 | 110654.3789 | 3071.775
266 | C | SOK | NAP | FC | FP | WC | OFF | 0.36343 | 38 | 1.9 | 8760 | 164303.262 | 0 | 100734.7902 | 0 | 31184.5118 | 94581 | 299506.5 | 212807.25 | 189162 | 168804.4079 | 8760 | 1720.1251 | 14290.3109 | 0 | 0 | 0 | 94.3935 | 6123.9494 | -1683.2096 | 9462.7406 | 2915.2313 | 8760 | 9082.7912 | 3438.0429 | 5644.7483 | 9096.653 | 1016.1548 | 0 | 24546.7456 | 15350.0741 | 0 | 12097.1806 | 8760 | 30099.063 | 907.1 | 669.25 | 2468.675 | 3408784.5705 | 110654.3789 | 3023.2
267 | C | SOK | NAP | FC | FP | WC | OFF | 0.36343 | 38 | 2.85 | 8760 | 167162.9238 | 0 | 98782.6704 | 0 | 31184.5118 | 94864.5 | 300404.25 | 213445.125 | 189729 | 166097.8913 | 8760 | 1720.1251 | 14811.9686 | 0 | 0 | 0 | 45.9515 | 5732.8565 | -1694.9506 | 9863.9038 | 2887.1484 | 8760 | 9084.5832 | 3237.0078 | 5847.5754 | 9096.653 | 1016.1548 | 0 | 24574.3702 | 15380.0306 | 0 | 12639.096 | 8760 | 30124.9438 | 958.675 | 622.4 | 2468.675 | 3408964.2037 | 110654.3789 | 3006.2
268 | C | SOK | NAP | FC | FP | WC | OFF | 0.36343 | 44.5 | 1.1 | 8760 | 162083.5694 | 0 | 102357.682 | 0 | 31184.5118 | 93723 | 296789.5 | 210876.75 | 187446 | 166659.9572 | 8760 | 1720.1251 | 14149.4022 | 0 | 0 | 0 | 168.3605 | 6046.8057 | -1672.4904 | 9514.5393 | 2916.8022 | 8760 | 9087.765 | 3370.0676 | 5717.6974 | 9096.653 | 1016.1548 | 0 | 24549.0765 | 15344.4208 | 0 | 11946.7844 | 8760 | 30065.6918 | 889.7 | 672.35 | 2468.675 | 3408913.9582 | 110654.3789 | 3176.8
269 | C | SOK | NAP | FC | FP | WC | OFF | 0.36343 | 44.5 | 2.25 | 8760 | 169822.7022 | 0 | 97466.5081 | 0 | 31184.5118 | 94155 | 298157.5 | 211848.75 | 188310 | 163471.9284 | 8760 | 1720.1251 | 15301.0541 | 0 | 0 | 0 | 54.2603 | 5209.3766 | -1699.6785 | 10359.7018 | 2894.2596 | 8760 | 9087.1769 | 2922.4763 | 6164.7006 | 9096.653 | 1016.1548 | 0 | 24590.0471 | 15391.7394 | 0 | 13100.8392 | 8760 | 30100.0122 | 992.85 | 576.4 | 2468.675 | 3408891.2772 | 110654.3789 | 3126.425
270 | C | SOK | NAP | FC | FP | WC | OFF | 0.36343 | 44.5 | 3.35 | 8760 | 174313.4279 | 0 | 93976.9908 | 0 | 31184.5118 | 94360.5 | 298808.25 | 212311.125 | 188721 | 162043.2318 | 8760 | 1720.1251 | 16021.0881 | 0 | 0 | 0 | 2.7334 | 4626.1857 | -1711.716 | 10949.8855 | 2873.7519 | 8760 | 9088.3182 | 2634.2371 | 6454.0811 | 9096.653 | 1016.1548 | 0 | 24614.5294 | 15420.7959 | 0 | 13835.6107 | 8760 | 30126.4449 | 1071.075 | 501.6 | 2468.675 | 3408628.7747 | 110654.3789 | 3094.875
271 | C | SOK | NAP | FC | FP | WC | R100 | 2.6035 | 18 | 0.45 | 8760 | 167683.3004 | 0 | 160752.5388 | 65533.1035 | 98086.1127 | 82642.5 | 261701.25 | 185945.625 | 165285 | 82839.6124 | 8760 | 1720.1251 | 10788.218 | 0 | 0 | 977.7799 | 6261.7383 | 9359.4341 | -1251.1118 | 2823.915 | 2956.0559 | 8760 | 6720.8412 | 5108.3496 | 1612.4916 | 6725.3331 | 7593.6017 | 3825.4406 | 18726.2799 | 11899.5276 | 0 | 8766.7578 | 8760 | 22319.4589 | 295.175 | 1082.2 | 2227.75 | 2451854.7262 | 178372.614 | 2256.275
272 | C | SOK | NAP | FC | FP | WC | R100 | 2.6035 | 18 | 0.9 | 8760 | 171287.502 | 0 | 156918.0444 | 65533.1035 | 98086.1127 | 82641 | 261696.5 | 185942.25 | 165282 | 81243.1948 | 8760 | 1720.1251 | 11298.0344 | 0 | 0 | 855.0337 | 5965.1681 | 9330.8132 | -1312.6547 | 2842.583 | 2916.184 | 8760 | 6721.4038 | 5103.7935 | 1617.6103 | 6725.3331 | 7593.6017 | 3856.7501 | 18725.3339 | 11898.2289 | 0 | 9312.5623 | 8760 | 22319.9767 | 299.55 | 1077.8 | 2227.75 | 2452091.5184 | 178372.614 | 2238.65
273 | C | SOK | NAP | FC | FP | WC | R100 | 2.6035 | 18 | 1.35 | 8760 | 172272.5031 | 0 | 154954.6753 | 65533.1035 | 98086.1127 | 82695 | 261867.5 | 186063.75 | 165390 | 80283.5755 | 8760 | 1720.1251 | 11497.2169 | 0 | 0 | 843.5789 | 5829.1953 | 9290.9315 | -1328.8251 | 2885.8902 | 2889.0238 | 8760 | 6721.3481 | 5089.1709 | 1632.1772 | 6725.3331 | 7593.6017 | 3862.1258 | 18729.7864 | 11903.8477 | 0 | 9537.0082 | 8760 | 22326.9392 | 306.85 | 1071.4 | 2227.75 | 2451899.3083 | 178372.614 | 2244.6
274 | C | SOK | NAP | FC | FP | WC | R100 | 2.6035 | 24.5 | 0.6 | 8760 | 170240.3943 | 0 | 153202.7921 | 65533.1035 | 98086.1127 | 82450.5 | 261093.25 | 185513.625 | 164901 | 82240.1679 | 8760 | 1720.1251 | 12793.4988 | 0 | 0 | 836.1497 | 5720.7418 | 8760.5568 | -1326.1971 | 3551.2819 | 3017.4454 | 8760 | 6720.8753 | 4702.7486 | 2018.1267 | 6725.3331 | 7593.6017 | 3863.7361 | 18755.1164 | 11930.1994 | 0 | 10659.77 | 8760 | 22333.5901 | 370.375 | 1003.8 | 2227.75 | 2451908.6387 | 178372.614 | 2433.95
275 | C | SOK | NAP | FC | FP | WC | R100 | 2.6035 | 24.5 | 1.25 | 8760 | 173773.6055 | 0 | 147734.1567 | 65533.1035 | 98086.1127 | 82285.5 | 260570.75 | 185142.375 | 164571 | 82899.9384 | 8760 | 1720.1251 | 13501.1448 | 0 | 0 | 726.068 | 5316.8784 | 8626.6006 | -1384.2093 | 3649.0565 | 2965.6213 | 8760 | 6720.8396 | 4679.9001 | 2040.9395 | 6725.3331 | 7593.6017 | 3889.3211 | 18745.2863 | 11923.0476 | 0 | 11414.5923 | 8760 | 22330.7707 | 390.575 | 980.85 | 2227.75 | 2452079.1816 | 178372.614 | 2429.6
276 | C | SOK | NAP | FC | FP | WC | R100 | 2.6035 | 24.5 | 1.85 | 8760 | 174819.3115 | 0 | 145497.8058 | 65533.1035 | 98086.1127 | 82294.5 | 260599.25 | 185162.625 | 164589 | 82590.0415 | 8760 | 1720.1251 | 13770.3517 | 0 | 0 | 721.4367 | 5111.962 | 8529.0341 | -1397.1071 | 3737.3051 | 2940.3699 | 8760 | 6720.4004 | 4651.8331 | 2068.5673 | 6725.3331 | 7593.6017 | 3891.7503 | 18748.5052 | 11926.3697 | 0 | 11706.6844 | 8760 | 22336.4702 | 406.6 | 964.975 | 2227.75 | 2452107.1734 | 178372.614 | 2430.375
277 | C | SOK | NAP | FC | FP | WC | R100 | 2.6035 | 31 | 0.8 | 8760 | 168810.6119 | 0 | 145584.8 | 65533.1035 | 98086.1127 | 81163.5 | 257017.75 | 182617.875 | 162327 | 85667.5872 | 8760 | 1720.1251 | 13747.5626 | 0 | 0 | 727.8035 | 5182.4584 | 8006.0664 | -1387.2032 | 4185.8048 | 3042.9591 | 8760 | 6723.451 | 4326.3351 | 2397.1159 | 6725.3331 | 7593.6017 | 3895.3351 | 18732.4603 | 11909.7738 | 0 | 11554.4907 | 8760 | 22279.275 | 425.275 | 927.45 | 2227.75 | 2452063.2686 | 178372.614 | 2634.15
278 | C | SOK | NAP | FC | FP | WC | R100 | 2.6035 | 31 | 1.55 | 8760 | 173347.8802 | 0 | 139950.4257 | 65533.1035 | 98086.1127 | 81082.5 | 256761.25 | 182435.625 | 162165 | 83467.9254 | 8760 | 1720.1251 | 14602.3393 | 0 | 0 | 640.8547 | 4751.2941 | 7654.9128 | -1437.3957 | 4506.9559 | 3005.6052 | 8760 | 6724.0988 | 4194.3776 | 2529.7212 | 6725.3331 | 7593.6017 | 3914.2664 | 18743.2011 | 11923.3255 | 0 | 12444.4674 | 8760 | 22296.0603 | 472.425 | 878.95 | 2227.75 | 2451947.3829 | 178372.614 | 2612.75
279 | C | SOK | NAP | FC | FP | WC | R100 | 2.6035 | 31 | 2.35 | 8760 | 175664.9341 | 0 | 135832.4503 | 65533.1035 | 98086.1127 | 80895 | 256167.5 | 182013.75 | 161790 | 82737.6833 | 8760 | 1720.1251 | 15109.1233 | 0 | 0 | 635.6616 | 4472.2934 | 7411.9627 | -1447.0241 | 4718.602 | 2972.6833 | 8760 | 6723.5931 | 4107.6268 | 2615.9663 | 6725.3331 | 7593.6017 | 3910.3431 | 18732.5904 | 11915.0516 | 0 | 12977.6501 | 8760 | 22288.4962 | 506.175 | 842.075 | 2227.75 | 2452112.3688 | 178372.614 | 2603.9
280 | C | SOK | NAP | FC | FP | WC | R10 | 2.6035 | 38 | 0.95 | 8760 | 172181.9224 | 0 | 140023.9208 | 65533.1035 | 98086.1127 | 81163.5 | 257017.75 | 182617.875 | 162327 | 82309.9914 | 8760 | 1720.1251 | 14720.1202 | 0 | 0 | 657.4415 | 4761.5498 | 7452.548 | -1427.4097 | 4739.794 | 3057.1248 | 8760 | 6725.8799 | 4054.3111 | 2671.5688 | 6725.3331 | 7593.6017 | 3914.4652 | 18792.2758 | 11968.5421 | 0 | 12487.032 | 8760 | 22323.7089 | 486.525 | 866.2 | 2227.75 | 2452169.5219 | 178372.614 | 2784.475
281 | C | SOK | NAP | FC | FP | WC | R10 | 2.6035 | 38 | 1.9 | 8760 | 178951.3034 | 0 | 132787.6533 | 65533.1035 | 98086.1127 | 80899.5 | 256181.75 | 182023.875 | 161799 | 82101.2975 | 8760 | 1720.1251 | 15994.4064 | 0 | 0 | 567.2769 | 4252.0147 | 6897.525 | -1480.945 | 5258.2621 | 3014.5066 | 8760 | 6725.0359 | 3830.8042 | 2894.2317 | 6725.3331 | 7593.6017 | 3932.2501 | 18789.8652 | 11970.8022 | 0 | 13795.6784 | 8760 | 22329.9418 | 562.75 | 785.575 | 2227.75 | 2452155.8743 | 178372.614 | 2749.275
282 | C | SOK | NAP | FC | FP | WC | R10 | 2.6035 | 38 | 2.85 | 8760 | 182677.2939 | 0 | 128259.4552 | 65533.1035 | 98086.1127 | 80673 | 255464.5 | 181514.25 | 161346 | 81476.955 | 8760 | 1720.1251 | 16809.2421 | 0 | 0 | 542.091 | 3944.1116 | 6457.7731 | -1489.9497 | 5667.9999 | 2975.5457 | 8760 | 6723.9747 | 3641.0772 | 3082.8975 | 6725.3331 | 7593.6017 | 3927.5959 | 18780.7655 | 11965.2198 | 0 | 14638.737 | 8760 | 22328.1936 | 621.05 | 723.5 | 2227.75 | 2452298.5957 | 178372.614 | 2735.6
283 | C | SOK | NAP | FC | FP | WC | R10 | 2.6035 | 44.5 | 1.1 | 8760 | 177647.4328 | 0 | 135407.2286 | 65533.1035 | 98086.1127 | 81018 | 256557 | 182290.5 | 162036 | 81295.4786 | 8760 | 1720.1251 | 15586.1319 | 0 | 0 | 598.3551 | 4419.9827 | 7076.518 | -1457.4191 | 5120.9682 | 3048.8115 | 8760 | 6724.1304 | 3872.122 | 2852.0085 | 6725.3331 | 7593.6017 | 3929.9284 | 18814.1122 | 11991.3066 | 0 | 13340.7401 | 8760 | 22335.4652 | 532.375 | 817.925 | 2227.75 | 2452158.9505 | 178372.614 | 2895.9
284 | C | SOK | NAP | FC | FP | WC | R10 | 2.6035 | 44.5 | 2.25 | 8760 | 185848.2336 | 0 | 126958.2919 | 65533.1035 | 98086.1127 | 80731.5 | 255649.75 | 181645.875 | 161463 | 80279.0743 | 8760 | 1720.1251 | 17131.2187 | 0 | 0 | 512.0911 | 3839.5719 | 6338.2235 | -1513.3174 | 5817.6864 | 3012.891 | 8760 | 6724.5381 | 3563.4339 | 3161.1043 | 6725.3331 | 7593.6017 | 3946.0556 | 18817.8976 | 11999.385 | 0 | 14910.7132 | 8760 | 22349.4321 | 632.1 | 713.425 | 2227.75 | 2452169.5252 | 178372.614 | 2855.75
285 | C | SOK | NAP | FC | FP | WC | R10 | 2.6035 | 44.5 | 3.35 | 8760 | 190885.741 | 0 | 121077.934 | 65533.1035 | 98086.1127 | 80373 | 254514.5 | 180839.25 | 160746 | 80279.9439 | 8760 | 1720.1251 | 18241.479 | 0 | 0 | 496.7164 | 3432.3133 | 5661.9679 | -1522.871 | 6461.2352 | 2964.8431 | 8760 | 6725.6522 | 3250.1238 | 3475.5284 | 6725.3331 | 7593.6017 | 3944.011 | 18812.8426 | 11997.572 | 0 | 16056.7151 | 8760 | 22356.939 | 717.325 | 622.225 | 2227.75 | 2452283.0037 | 178372.614 | 2836.2
286 | C | SOK | NAP | FC | FP | WC | R600 | 2.9879 | 18 | 0.45 | 8760 | 169013.266 | 0 | 147635.9133 | 65533.1035 | 57958.323 | 89931 | 284781.5 | 202344.75 | 179862 | 85117.0692 | 8760 | 1720.1251 | 10752.4683 | 0 | 0 | 855.4793 | 3131.2233 | 10290.3711 | -1304.2941 | 2928.8428 | 2904.8457 | 8760 | 7297.1848 | 5639.3836 | 1657.8012 | 7301.1473 | 3780.0236 | 4283.162 | 20359.4128 | 12928.1836 | 0 | 8683.6196 | 8760 | 24204.5351 | 309.6 | 1189.25 | 2346.175 | 2649955.4521 | 155104.6653 | 2249.65
287 | C | SOK | NAP | FC | FP | WC | R600 | 2.9879 | 18 | 0.9 | 8760 | 171875.2196 | 0 | 144120.1477 | 65533.1035 | 57958.323 | 89874 | 284601 | 202216.5 | 179748 | 84098.7744 | 8760 | 1720.1251 | 11182.79 | 0 | 0 | 730.5289 | 2931.8447 | 10287.8829 | -1372.6038 | 2922.0311 | 2868.8374 | 8760 | 7297.4599 | 5650.5335 | 1646.9264 | 7301.1473 | 3780.0236 | 4336.9008 | 20353.9786 | 12923.5917 | 0 | 9144.7689 | 8760 | 24202.6724 | 311.275 | 1186.625 | 2346.175 | 2650094.0035 | 155104.6653 | 2244.1
288 | C | SOK | NAP | FC | FP | WC | R600 | 2.9879 | 18 | 1.35 | 8760 | 172922.6464 | 0 | 142492.0062 | 65533.1035 | 57958.323 | 89806.5 | 284387.25 | 202064.625 | 179613 | 83840.5297 | 8760 | 1720.1251 | 11382.1996 | 0 | 0 | 713.0562 | 2812.8753 | 10249.8069 | -1389.4507 | 2957.8007 | 2841.4485 | 8760 | 7297.3241 | 5640.9013 | 1656.4228 | 7301.1473 | 3780.0236 | 4344.6596 | 20350.5821 | 12921.5443 | 0 | 9367.9908 | 8760 | 24201.052 | 318 | 1178.775 | 2346.175 | 2649936.0577 | 155104.6653 | 2250.125
289 | C | SOK | NAP | FC | FP | WC | R600 | 2.9879 | 24.5 | 0.6 | 8760 | 171024.3949 | 0 | 141064.1014 | 65533.1035 | 57958.323 | 89632.5 | 283836.25 | 201673.125 | 179265 | 85690.3982 | 8760 | 1720.1251 | 12615.2147 | 0 | 0 | 709.7287 | 2818.0369 | 9670.7414 | -1389.0522 | 3682.1168 | 2971.7967 | 8760 | 7297.7459 | 5223.0165 | 2074.7294 | 7301.1473 | 3780.0236 | 4345.779 | 20385.6347 | 12957.0794 | 0 | 10428.5467 | 8760 | 24217.7051 | 387.625 | 1106.25 | 2346.175 | 2649889.685 | 155104.6653 | 2435.725
290 | C | SOK | NAP | FC | FP | WC | R600 | 2.9879 | 24.5 | 1.25 | 8760 | 174293.3572 | 0 | 136268.9212 | 65533.1035 | 57958.323 | 89502 | 283423 | 201379.5 | 179004 | 85464.4422 | 8760 | 1720.1251 | 13226.8789 | 0 | 0 | 593.6851 | 2560.9173 | 9507.3107 | -1454.2063 | 3807.7231 | 2927.8092 | 8760 | 7296.4959 | 5180.1431 | 2116.3528 | 7301.1473 | 3780.0236 | 4386.3851 | 20379.2985 | 12952.1492 | 0 | 11078.0415 | 8760 | 24216.2358 | 409.975 | 1081.725 | 2346.175 | 2649798.4375 | 155104.6653 | 2433.075
291 | C | SOK | NAP | FC | FP | WC | R600 | 2.9879 | 24.5 | 1.85 | 8760 | 175262.126 | 0 | 133462.6082 | 65533.1035 | 57958.323 | 89455.5 | 283275.75 | 201274.875 | 178911 | 85223.3881 | 8760 | 1720.1251 | 13548.2837 | 0 | 0 | 579.7213 | 2362.2443 | 9411.0717 | -1465.5712 | 3893.8192 | 2892.842 | 8760 | 7298.3514 | 5153.6239 | 2144.7274 | 7301.1473 | 3780.0236 | 4386.223 | 20378.077 | 12951.62 | 0 | 11429.6082 | 8760 | 24222.3001 | 425.9 | 1065.025 | 2346.175 | 2650104.4573 | 155104.6653 | 2440.225
292 | C | SOK | NAP | FC | FP | WC | R600 | 2.9879 | 31 | 0.8 | 8760 | 168693.076 | 0 | 134878.5138 | 65533.1035 | 57958.323 | 88458 | 280117 | 199030.5 | 176916 | 89227.2375 | 8760 | 1720.1251 | 13350.9155 | 0 | 0 | 595.7871 | 2546.6429 | 8867.6948 | -1460.223 | 4369.5416 | 3003.0043 | 8760 | 7299.5551 | 4820.4404 | 2479.1148 | 7301.1473 | 3780.0236 | 4393.0171 | 20376.7182 | 12949.5979 | 0 | 11098.0948 | 8760 | 24180.479 | 448.125 | 1026.175 | 2346.175 | 2649780.473 | 155104.6653 | 2645.025
293 | C | SOK | NAP | FC | FP | WC | R600 | 2.9879 | 31 | 1.55 | 8760 | 172130.4185 | 0 | 129233.6402 | 65533.1035 | 57958.323 | 88128 | 279072 | 198288 | 176256 | 87692.0924 | 8760 | 1720.1251 | 14131.3976 | 0 | 0 | 522.1568 | 2243.0783 | 8507.5173 | -1510.8569 | 4689.8816 | 2959.6255 | 8760 | 7299.5433 | 4678.6837 | 2620.8595 | 7301.1473 | 3780.0236 | 4419.2534 | 20360.2062 | 12939.2543 | 0 | 11916.5207 | 8760 | 24168.542 | 494.725 | 974.075 | 2346.175 | 2649854.14 | 155104.6653 | 2646.75
294 | C | SOK | NAP | FC | FP | WC | R600 | 2.9879 | 31 | 2.35 | 8760 | 174643.0397 | 0 | 125248.4059 | 65533.1035 | 57958.323 | 87834 | 278141 | 197626.5 | 175668 | 87428.5266 | 8760 | 1720.1251 | 14641.0205 | 0 | 0 | 495.7727 | 2002.4826 | 8250.5473 | -1522.3637 | 4910.9031 | 2927.2617 | 8760 | 7299.4458 | 4583.0602 | 2716.3856 | 7301.1473 | 3780.0236 | 4417.8784 | 20345.9517 | 12926.6693 | 0 | 12452.1519 | 8760 | 24158.2871 | 528 | 935.9 | 2346.175 | 2649944.1919 | 155104.6653 | 2636.35
295 | C | SOK | NAP | FC | FP | WC | R60 | 2.9879 | 38 | 0.95 | 8760 | 170834.3841 | 0 | 129784.8535 | 65533.1035 | 57958.323 | 88072.5 | 278896.25 | 198163.125 | 176145 | 86813.5381 | 8760 | 1720.1251 | 14176.0888 | 0 | 0 | 532.3641 | 2311.7906 | 8264.0036 | -1499.2903 | 4947.216 | 3010.3797 | 8760 | 7301.0804 | 4521.272 | 2779.8084 | 7301.1473 | 3780.0236 | 4418.1379 | 20407.3806 | 12980.3799 | 0 | 11887.6834 | 8760 | 24192.3825 | 509.75 | 958.125 | 2346.175 | 2649847.6413 | 155104.6653 | 2811.025
296 | C | SOK | NAP | FC | FP | WC | R60 | 2.9879 | 38 | 1.9 | 8760 | 176468.0835 | 0 | 123464.2749 | 65533.1035 | 57958.323 | 87802.5 | 278041.25 | 197555.625 | 175605 | 86195.8507 | 8760 | 1720.1251 | 15329.6252 | 0 | 0 | 453.7691 | 1967.9624 | 7692.6502 | -1553.098 | 5484.3116 | 2962.4795 | 8760 | 7300.3557 | 4282.2999 | 3018.0559 | 7301.1473 | 3780.0236 | 4440.1424 | 20404.1241 | 12980.5384 | 0 | 13078.664 | 8760 | 24197.1352 | 587.3 | 876.075 | 2346.175 | 2649973.0206 | 155104.6653 | 2798.675
297 | C | SOK | NAP | FC | FP | WC | R60 | 2.9879 | 38 | 2.85 | 8760 | 181187.6805 | 0 | 118370.6144 | 65533.1035 | 57958.323 | 87537 | 277200.5 | 196958.25 | 175074 | 85705.2833 | 8760 | 1720.1251 | 16165.3001 | 0 | 0 | 413.0057 | 1720.4875 | 7194.4408 | -1567.7381 | 5953.6134 | 2933.3254 | 8760 | 7300.459 | 4061.3699 | 3239.089 | 7301.1473 | 3780.0236 | 4445.1441 | 20394.4407 | 12975.7303 | 0 | 13934.1417 | 8760 | 24195.4829 | 652.425 | 806.525 | 2346.175 | 2649983.6347 | 155104.6653 | 2773.15
298 | C | SOK | NAP | FC | FP | WC | R60 | 2.9879 | 44.5 | 1.1 | 8760 | 175599.3644 | 0 | 126141.5964 | 65533.1035 | 57958.323 | 87810 | 278065 | 197572.5 | 175620 | 86342.8577 | 8760 | 1720.1251 | 14920.8221 | 0 | 0 | 474.9093 | 2127.0767 | 7874.9073 | -1531.439 | 5330.9058 | 2998.2183 | 8760 | 7299.5964 | 4332.2978 | 2967.2986 | 7301.1473 | 3780.0236 | 4436.8692 | 20423.0505 | 12994.9092 | 0 | 12622.688 | 8760 | 24198.9663 | 554.7 | 908.8 | 2346.175 | 2649747.6198 | 155104.6653 | 2930.575
299 | C | SOK | NAP | FC | FP | WC | R60 | 2.9879 | 44.5 | 2.25 | 8760 | 182831.8965 | 0 | 118445.6095 | 65533.1035 | 57958.323 | 87351 | 276611.5 | 196539.75 | 174702 | 84803.2034 | 8760 | 1720.1251 | 16362.6595 | 0 | 0 | 392.9689 | 1715.4866 | 7049.3859 | -1582.6874 | 6108.4855 | 2958.4996 | 8760 | 7301.6257 | 3968.8132 | 3332.8125 | 7301.1473 | 3780.0236 | 4455.3226 | 20421.9907 | 12995.5462 | 0 | 14092.0694 | 8760 | 24207.1843 | 660.675 | 795.175 | 2346.175 | 2649777.3314 | 155104.6653 | 2908.3
300 | C | SOK | NAP | FC | FP | WC | R60 | 2.9879 | 44.5 | 3.35 | 8760 | 187448.266 | 0 | 113161.4618 | 65533.1035 | 57958.323 | 87316.5 | 276502.25 | 196462.125 | 174633 | 84128.1823 | 8760 | 1720.1251 | 17335.0529 | 0 | 0 | 341.5988 | 1478.2456 | 6433.4559 | -1600.9643 | 6721.5777 | 2915.5185 | 8760 | 7301.6393 | 3677.8055 | 3623.8338 | 7301.1473 | 3780.0236 | 4464.6761 | 20435.8615 | 13012.6573 | 0 | 15092.5264 | 8760 | 24236.0346 | 743.775 | 711.5 | 2346.175 | 2649785.0802 | 155104.6653 | 2891.7
301 | C | SOK | STR | FC | ET | HC | OFF0 | 0.28797 | 11.5 | 0.288 | 8760 | 122418.1164 | 0 | 170642.8794 | 0 | 117547.8381 | 23056.5 | 53798.5 | 51877.125 | 46113 | 21536.9165 | 8760 | 1150.2925 | 5765.0079 | 0 | 0 | 0 | 5722.0511 | 3009.737 | -1157.948 | 1698.0965 | 2857.5051 | 8760 | 3052.2127 | 1904.7886 | 1147.4241 | 3051.699 | 6046.5519 | 0 | 7437.6083 | 4533.8424 | 0 | 3837.6003 | 8760 | 0 | 132.875 | 251.4 | 1446.5 | 1056612.2674 | 186766.0544 | 2418.425 | -13.6324
302 | C | SOK | STR | FC | ET | HC | OFF0 | 0.28797 | 11.5 | 0.575 | 8760 | 125219.557 | 0 | 169694.1926 | 0 | 117547.8381 | 23028 | 53732 | 51813 | 46056 | 19470.055 | 8760 | 1150.2925 | 5933.3673 | 0 | 0 | 0 | 5669.1449 | 2939.2137 | -1201.5443 | 1763.4584 | 2859.098 | 8760 | 3052.8296 | 1858.8798 | 1193.9499 | 3051.699 | 6046.5519 | 0 | 7438.9558 | 4534.9039 | 0 | 4006.7711 | 8760 | 0 | 137.55 | 246.25 | 1446.5 | 1056914.9529 | 186766.0544 | 2381.125 | -11.872
303 | C | SOK | STR | FC | ET | HC | OFF0 | 0.28797 | 11.5 | 0.863 | 8760 | 126359.0132 | 0 | 169091.9828 | 0 | 117547.8381 | 23046 | 53774 | 51853.5 | 46092 | 18533.732 | 8760 | 1150.2925 | 6002.7061 | 0 | 0 | 0 | 5631.7842 | 2923.7705 | -1216.7836 | 1777.5075 | 2857.9826 | 8760 | 3052.7792 | 1852.0589 | 1200.7203 | 3051.699 | 6046.5519 | 0 | 7435.2543 | 4535.3112 | 0 | 4078.2296 | 8760 | 0 | 139.85 | 244.25 | 1446.5 | 1056621.9974 | 186766.0544 | 2366.725 | -12.9545
304 | C | SOK | STR | FC | ET | HC | OFF0 | 0.28797 | 15.5 | 0.388 | 8760 | 120005.4496 | 0 | 162800.6522 | 0 | 117547.8381 | 22455 | 52395 | 50523.75 | 44910 | 17169.9721 | 8760 | 1150.2925 | 6994.9155 | 0 | 0 | 0 | 5391.6432 | 2321.6941 | -1221.608 | 2355.0789 | 2961.0077 | 8760 | 3052.6255 | 1461.1293 | 1591.4962 | 3051.699 | 6046.5519 | 0 | 7431.3159 | 4529.9511 | 0 | 4936.952 | 8760 | 0 | 181.25 | 193 | 1446.5 | 1056627.7576 | 186766.0544 | 2553.375 | -11.8512
305 | C | SOK | STR | FC | ET | HC | OFF0 | 0.28797 | 15.5 | 0.775 | 8760 | 123548.6274 | 0 | 160702.2921 | 0 | 117547.8381 | 22350 | 52150 | 50287.5 | 44700 | 15405.5884 | 8760 | 1150.2925 | 7257.7017 | 0 | 0 | 0 | 5300.0902 | 2171.1005 | -1258.2607 | 2490.7343 | 2955.8552 | 8760 | 3052.1075 | 1369.2712 | 1682.8363 | 3051.699 | 6046.5519 | 0 | 7426.0705 | 4528.8676 | 0 | 5207.218 | 8760 | 0 | 191.775 | 180.725 | 1446.5 | 1056802.8845 | 186766.0544 | 2509.075 | -11.8439
306 | C | SOK | STR | FC | ET | HC | OFF0 | 0.28797 | 15.5 | 1.163 | 8760 | 125609.1648 | 0 | 159366.6312 | 0 | 117547.8381 | 22305 | 52045 | 50186.25 | 44610 | 15856.9779 | 8760 | 1150.2925 | 7412.0607 | 0 | 0 | 0 | 5251.0657 | 2068.747 | -1266.7773 | 2581.6873 | 2945.3499 | 8760 | 3052.1696 | 1304.8837 | 1747.2859 | 3051.699 | 6046.5519 | 0 | 7423.6223 | 4529.1013 | 0 | 5374.1139 | 8760 | 0 | 198.35 | 173.4 | 1446.5 | 1056539.0878 | 186766.0544 | 2484.125 | -10.0615
307 | C | SOK | STR | FC | ET | HC | OFF0 | 0.28797 | 20 | 0.5 | 8760 | 118088.2497 | 0 | 154488.2064 | 0 | 117547.8381 | 21928.5 | 51166.5 | 49339.125 | 43857 | 13710.2082 | 8760 | 1150.2925 | 8116.88 | 0 | 0 | 0 | 5035.033 | 1715.4181 | -1268.7793 | 2925.1589 | 3024.3645 | 8760 | 3052.6836 | 1077.982 | 1974.7016 | 3051.699 | 6046.5519 | 0 | 7425.2225 | 4525.648 | 0 | 5966.9845 | 8760 | 0 | 223.9 | 141.575 | 1446.5 | 1056375.5341 | 186766.0544 | 2690.15 | -8.2594
308 | C | SOK | STR | FC | ET | HC | OFF0 | 0.28797 | 20 | 1 | 8760 | 122447.677 | 0 | 151465.9079 | 0 | 117547.8381 | 21720 | 50680 | 48870 | 43440 | 12013.8004 | 8760 | 1150.2925 | 8495.3581 | 0 | 0 | 0 | 4900.2378 | 1494.8742 | -1303.0924 | 3130.888 | 3012.7679 | 8760 | 3052.5125 | 939.4337 | 2113.0788 | 3051.699 | 6046.5519 | 0 | 7418.9871 | 4524.3853 | 0 | 6361.492 | 8760 | 0 | 239.15 | 122.85 | 1446.5 | 1056213.7114 | 186766.0544 | 2634.975 | -7.7318
309 | C | SOK | STR | FC | ET | HC | OFF0 | 0.28797 | 20 | 1.5 | 8760 | 124514.9555 | 0 | 150596.7159 | 0 | 117547.8381 | 21598.5 | 50396.5 | 48596.625 | 43197 | 11489.3107 | 8760 | 1150.2925 | 8677.2677 | 0 | 0 | 0 | 4846.0703 | 1369.8607 | -1311.0209 | 3241.1982 | 3004.5229 | 8760 | 3052.5732 | 864.6419 | 2187.9313 | 3051.699 | 6046.5519 | 0 | 7413.7793 | 4522.7445 | 0 | 6552.6714 | 8760 | 0 | 247.35 | 112.625 | 1446.5 | 1056315.9347 | 186766.0544 | 2611.55 | -7.5959
310 | C | SOK | STR | FC | ET | HC | OFF | 0.28797 | 24 | 0.6 | 8760 | 116879.9993 | 0 | 148736.8399 | 0 | 117547.8381 | 21519 | 50211 | 48417.75 | 43038 | 10902.7139 | 8760 | 1150.2925 | 8913.8529 | 0 | 0 | 0 | 4771.7258 | 1333.433 | -1303.5152 | 3306.873 | 3061.0227 | 8760 | 3052.09 | 819.0535 | 2233.0365 | 3051.699 | 6046.5519 | 0 | 7417.0727 | 4520.334 | 0 | 6706.3502 | 8760 | 0 | 251.1 | 107.55 | 1446.5 | 1056189.1591 | 186766.0544 | 2799.65 | -6.8065
311 | C | SOK | STR | FC | ET | HC | OFF | 0.28797 | 24 | 1.2 | 8760 | 121097.6657 | 0 | 145799.2858 | 0 | 117547.8381 | 21291 | 49679 | 47904.75 | 42582 | 11374.8208 | 8760 | 1150.2925 | 9324.9795 | 0 | 0 | 0 | 4609.3092 | 1100.8573 | -1338.6159 | 3510.7048 | 3046.5232 | 8760 | 3052.6634 | 684.3477 | 2368.3157 | 3051.699 | 6046.5519 | 0 | 7410.433 | 4518.8462 | 0 | 7133.9989 | 8760 | 0 | 266.95 | 87.9 | 1446.5 | 1056401.433 | 186766.0544 | 2748.375 | -6.331
312 | C | SOK | STR | FC | ET | HC | OFF | 0.28797 | 24 | 1.8 | 8760 | 123341.2125 | 0 | 143565.1847 | 0 | 117547.8381 | 21124.5 | 49290.5 | 47530.125 | 42249 | 9771.475 | 8760 | 1150.2925 | 9548.8577 | 0 | 0 | 0 | 4519.0088 | 950.4175 | -1344.7336 | 3642.442 | 3039.5891 | 8760 | 3052.253 | 601.7749 | 2450.4781 | 3051.699 | 6046.5519 | 0 | 7406.3874 | 4516.0566 | 0 | 7365.6545 | 8760 | 0 | 278.55 | 73.525 | 1446.5 | 1056449.3367 | 186766.0544 | 2722.725 | -5.0831
313 | C | SOK | STR | FC | ET | HC | OFF | 0.28797 | 28.5 | 0.713 | 8760 | 115593.0317 | 0 | 142495.756 | 0 | 117547.8381 | 21109.5 | 49255.5 | 47496.375 | 42219 | 11732.0433 | 8760 | 1150.2925 | 9588.0511 | 0 | 0 | 0 | 4487.5216 | 997.993 | -1333.2024 | 3630.3854 | 3082.1586 | 8760 | 3052.9468 | 599.7356 | 2453.2112 | 3051.699 | 6046.5519 | 0 | 7409.4979 | 4515.0672 | 0 | 7341.367 | 8760 | 0 | 273.15 | 78.675 | 1446.5 | 1056370.557 | 186766.0544 | 2913.55 | -9.9842
314 | C | SOK | STR | FC | ET | HC | OFF | 0.28797 | 28.5 | 1.425 | 8760 | 119612.7059 | 0 | 139606.9486 | 0 | 117547.8381 | 20802 | 48538 | 46804.5 | 41604 | 12105.4873 | 8760 | 1150.2925 | 10017.5586 | 0 | 0 | 0 | 4298.9189 | 741.5416 | -1364.8591 | 3845.444 | 3068.8811 | 8760 | 3052.0499 | 460.6595 | 2591.3904 | 3051.699 | 6046.5519 | 0 | 7399.7253 | 4510.0038 | 0 | 7783.6728 | 8760 | 0 | 290.65 | 56.05 | 1446.5 | 1056073.6884 | 186766.0544 | 2867.2 | -5.0638
315 | C | SOK | STR | FC | ET | HC | OFF | 0.28797 | 28.5 | 2.138 | 8760 | 121728.4633 | 0 | 137351.099 | 0 | 117547.8381 | 20635.5 | 48149.5 | 46429.875 | 41271 | 9972.2412 | 8760 | 1150.2925 | 10249.6332 | 0 | 0 | 0 | 4225.1473 | 580.9222 | -1378.1098 | 3982.8128 | 3069.9915 | 8760 | 3052.0371 | 371.8715 | 2680.1655 | 3051.699 | 6046.5519 | 0 | 7394.0832 | 4507.8301 | 0 | 8014.8471 | 8760 | 0 | 302.225 | 41.7 | 1446.5 | 1056269.7987 | 186766.0544 | 2843.55 | -3.1379
316 | C | SOK | STR | FC | ET | WC | OFF0 | 0.45591 | 18 | 0.45 | 8760 | 130952.812 | 0 | 179515.5378 | 0 | 135001.1402 | 52576.5 | 166492.25 | 118297.125 | 105153 | 54182.4068 | 8760 | 1150.2925 | 7442.1098 | 0 | 0 | 0 | 8769.7945 | 5534.0146 | -1199.3386 | 2826.6456 | 2899.2731 | 8760 | 4831.3768 | 3165.1654 | 1666.2114 | 4831.495 | 9572.9904 | 0 | 12956.6585 | 8156.2274 | 0 | 5461.5175 | 8760 | 15577.6322 | 286.775 | 589.5 | 1446.5 | 1700086.8008 | 186766.0544 | 2508.7
317 | C | SOK | STR | FC | ET | WC | OFF0 | 0.45591 | 18 | 0.9 | 8760 | 133051.8856 | 0 | 178518.8543 | 0 | 135001.1402 | 52687.5 | 166843.75 | 118546.875 | 105375 | 53905.4631 | 8760 | 1150.2925 | 7613.6782 | 0 | 0 | 0 | 8680.7185 | 5504.4254 | -1232.1181 | 2860.7269 | 2890.6915 | 8760 | 4831.5467 | 3154.0565 | 1677.4903 | 4831.495 | 9572.9904 | 0 | 12966.1676 | 8165.3268 | 0 | 5640.2707 | 8760 | 15592.0333 | 292.525 | 585.6 | 1446.5 | 1699903.1149 | 186766.0544 | 2487.25
318 | C | SOK | STR | FC | ET | WC | OFF0 | 0.45591 | 18 | 1.35 | 8760 | 134574.8277 | 0 | 178284.8699 | 0 | 135001.1402 | 52731 | 166981.5 | 118644.75 | 105462 | 53513.872 | 8760 | 1150.2925 | 7739.3688 | 0 | 0 | 0 | 8616.1073 | 5457.8982 | -1240.8954 | 2904.3691 | 2882.8567 | 8760 | 4831.5624 | 3127.9764 | 1703.586 | 4831.495 | 9572.9904 | 0 | 12966.9468 | 8166.9544 | 0 | 5776.734 | 8760 | 15592.1177 | 297.6 | 581.25 | 1446.5 | 1700074.4042 | 186766.0544 | 2469.825
319 | C | SOK | STR | FC | ET | WC | OFF0 | 0.45591 | 24.5 | 0.6 | 8760 | 135875.7778 | 0 | 171147.5957 | 0 | 135001.1402 | 52672.5 | 166796.25 | 118513.125 | 105345 | 52447.7422 | 8760 | 1150.2925 | 9199.642 | 0 | 0 | 0 | 8279.9396 | 4579.4203 | -1247.4669 | 3839.9883 | 2954.0465 | 8760 | 4832.444 | 2574.6333 | 2257.8107 | 4831.495 | 9572.9904 | 0 | 13019.2786 | 8218.5333 | 0 | 7135.2736 | 8760 | 15637.8345 | 385.725 | 492.15 | 1446.5 | 1700233.6814 | 186766.0544 | 2610.275
320 | C | SOK | STR | FC | ET | WC | OFF0 | 0.45591 | 24.5 | 1.25 | 8760 | 138881.8435 | 0 | 168757.5051 | 0 | 135001.1402 | 52797 | 167190.5 | 118793.25 | 105594 | 51997.2007 | 8760 | 1150.2925 | 9492.288 | 0 | 0 | 0 | 8119.5917 | 4444.1175 | -1273.7709 | 3981.1398 | 2939.8956 | 8760 | 4831.6212 | 2501.1477 | 2330.4735 | 4831.495 | 9572.9904 | 0 | 13032.0414 | 8233.6913 | 0 | 7444.1612 | 8760 | 15653.0401 | 402.2 | 477.75 | 1446.5 | 1700277.5961 | 186766.0544 | 2577.95
321 | C | SOK | STR | FC | ET | WC | OFF0 | 0.45591 | 24.5 | 1.85 | 8760 | 140629.1475 | 0 | 167024.3706 | 0 | 135001.1402 | 52821 | 167266.5 | 118847.25 | 105642 | 52224.2077 | 8760 | 1150.2925 | 9661.3337 | 0 | 0 | 0 | 8044.4903 | 4352.3992 | -1277.143 | 4062.1922 | 2927.8267 | 8760 | 4831.5158 | 2462.9269 | 2368.5889 | 4831.495 | 9572.9904 | 0 | 13035.2758 | 8237.5565 | 0 | 7629.8946 | 8760 | 15658.5262 | 413.475 | 466.875 | 1446.5 | 1700243.8415 | 186766.0544 | 2559.1
322 | C | SOK | STR | FC | ET | WC | OFF0 | 0.45591 | 31 | 0.8 | 8760 | 138667.6661 | 0 | 162889.1463 | 0 | 135001.1402 | 51967.5 | 164563.75 | 116926.875 | 103935 | 54235.5529 | 8760 | 1150.2925 | 10386.7207 | 0 | 0 | 0 | 7814.5966 | 3777.5103 | -1284.0326 | 4629.2738 | 2981.7937 | 8760 | 4831.746 | 2085.3041 | 2746.4419 | 4831.495 | 9572.9904 | 0 | 13017.6153 | 8219.5878 | 0 | 8271.0286 | 8760 | 15623.7381 | 454.6 | 411.525 | 1446.5 | 1700244.9144 | 186766.0544 | 2728.575
323 | C | SOK | STR | FC | ET | WC | OFF0 | 0.45591 | 31 | 1.55 | 8760 | 142874.4896 | 0 | 159752.1055 | 0 | 135001.1402 | 52096.5 | 164972.25 | 117217.125 | 104193 | 53144.0048 | 8760 | 1150.2925 | 10817.5309 | 0 | 0 | 0 | 7614.6428 | 3585.7184 | -1309.5951 | 4830.8608 | 2973.0428 | 8760 | 4831.6413 | 1979.3038 | 2852.3375 | 4831.495 | 9572.9904 | 0 | 13033.5206 | 8237.2133 | 0 | 8713.1708 | 8760 | 15638.6637 | 477.975 | 390.3 | 1446.5 | 1700143.1462 | 186766.0544 | 2684.025
324 | C | SOK | STR | FC | ET | WC | OFF0 | 0.45591 | 31 | 2.35 | 8760 | 145054.2952 | 0 | 158589.683 | 0 | 135001.1402 | 52200 | 165300 | 117450 | 104400 | 53132.7564 | 8760 | 1150.2925 | 11065.3155 | 0 | 0 | 0 | 7513.896 | 3447.49 | -1311.6231 | 4972.3316 | 2953.3968 | 8760 | 4832.0076 | 1909.1126 | 2922.8949 | 4831.495 | 9572.9904 | 0 | 13046.0149 | 8249.6096 | 0 | 8984.2489 | 8760 | 15652.9362 | 496.025 | 373.975 | 1446.5 | 1700121.6923 | 186766.0544 | 2662.8
325 | C | SOK | STR | FC | ET | WC | OFF | 0.45591 | 38 | 0.95 | 8760 | 142696.8015 | 0 | 156033.8534 | 0 | 135001.1402 | 51607.5 | 163423.75 | 116116.875 | 103215 | 55299.2529 | 8760 | 1150.2925 | 11398.9322 | 0 | 0 | 0 | 7408.4428 | 3120.2075 | -1319.0711 | 5289.1847 | 2995.8816 | 8760 | 4832.3724 | 1690.3367 | 3142.0357 | 4831.495 | 9572.9904 | 0 | 13044.5486 | 8246.6905 | 0 | 9250.2411 | 8760 | 15635.063 | 512.95 | 347.175 | 1446.5 | 1700351.2516 | 186766.0544 | 2843.975
326 | C | SOK | STR | FC | ET | WC | OFF | 0.45591 | 38 | 1.9 | 8760 | 148562.4763 | 0 | 151824.384 | 0 | 135001.1402 | 51775.5 | 163955.75 | 116494.875 | 103551 | 54070.8902 | 8760 | 1150.2925 | 12064.6029 | 0 | 0 | 0 | 7136.0311 | 2795.6845 | -1342.3613 | 5614.8363 | 2987.1751 | 8760 | 4831.8244 | 1519.4901 | 3312.3343 | 4831.495 | 9572.9904 | 0 | 13064.8198 | 8269.5869 | 0 | 9923.2151 | 8760 | 15654.5816 | 551.825 | 311.1 | 1446.5 | 1700308.049 | 186766.0544 | 2788.6
327 | C | SOK | STR | FC | ET | WC | OFF | 0.45591 | 38 | 2.85 | 8760 | 151313.5294 | 0 | 149453.7921 | 0 | 135001.1402 | 51778.5 | 163965.25 | 116501.625 | 103557 | 54694.1822 | 8760 | 1150.2925 | 12383.7812 | 0 | 0 | 0 | 6995.4393 | 2595.4506 | -1343.4731 | 5805.2174 | 2964.4194 | 8760 | 4831.4838 | 1428.9931 | 3402.4906 | 4831.495 | 9572.9904 | 0 | 13067.7013 | 8274.9708 | 0 | 10268.0857 | 8760 | 15664.2918 | 578.125 | 284.85 | 1446.5 | 1700061.2333 | 186766.0544 | 2761.175
328 | C | SOK | STR | FC | ET | WC | OFF | 0.45591 | 44.5 | 1.1 | 8760 | 147811.8753 | 0 | 150074.0008 | 0 | 135001.1402 | 51390 | 162735 | 115627.5 | 102780 | 56169.4434 | 8760 | 1150.2925 | 12220.9492 | 0 | 0 | 0 | 7044.731 | 2680.3474 | -1342.7505 | 5722.3828 | 2999.9863 | 8760 | 4831.3288 | 1435.8302 | 3395.4986 | 4831.495 | 9572.9904 | 0 | 13062.1497 | 8266.0172 | 0 | 10052.117 | 8760 | 15643.0937 | 552.4 | 304.1 | 1446.5 | 1700020.6261 | 186766.0544 | 2935.425
329 | C | SOK | STR | FC | ET | WC | OFF | 0.45591 | 44.5 | 2.25 | 8760 | 154325.9369 | 0 | 145638.0465 | 0 | 135001.1402 | 51513 | 163124.5 | 115904.25 | 103026 | 55741.3637 | 8760 | 1150.2925 | 13013.0166 | 0 | 0 | 0 | 6734.985 | 2225.071 | -1363.8209 | 6173.6609 | 2982.3064 | 8760 | 4831.206 | 1203.9647 | 3627.2414 | 4831.495 | 9572.9904 | 0 | 13084.6314 | 8291.0679 | 0 | 10857.4591 | 8760 | 15667.6258 | 607.95 | 250.6 | 1446.5 | 1700246.9295 | 186766.0544 | 2879.7
330 | C | SOK | STR | FC | ET | WC | OFF | 0.45591 | 44.5 | 3.35 | 8760 | 157738.6314 | 0 | 143647.6792 | 0 | 135001.1402 | 51507 | 163105.5 | 115890.75 | 103014 | 55885.0914 | 8760 | 1150.2925 | 13395.1178 | 0 | 0 | 0 | 6626.3496 | 1967.379 | -1374.4166 | 6423.8507 | 2973.9506 | 8760 | 4832.2601 | 1080.2265 | 3752.0336 | 4831.495 | 9572.9904 | 0 | 13092.3783 | 8301.456 | 0 | 11251.034 | 8760 | 15679.488 | 639.75 | 218.7 | 1446.5 | 1700140.4685 | 186766.0544 | 2849.85
331 | C | SOK | STR | FC | FP | HC | OFF0 | 0.28797 | 11.5 | 0.288 | 8760 | 103158.1366 | 0 | 178346.3658 | 0 | 117547.8381 | 23542.5 | 54932.5 | 52970.625 | 47085 | 21655.5811 | 8760 | 1150.2925 | 3880.09 | 0 | 0 | 0 | 5953.5166 | 3898.0458 | -1060.0636 | 864.1039 | 2157.2251 | 8760 | 3051.7153 | 2473.7003 | 578.0149 | 3051.699 | 6046.5519 | 0 | 7443.6003 | 4534.3028 | 0 | 2601.8256 | 8760 | 0 | 69.825 | 322.55 | 1446.5 | 1056774.2755 | 186766.0544 | 2934.425 | -13.0977
332 | C | SOK | STR | FC | FP | HC | OFF0 | 0.28797 | 11.5 | 0.575 | 8760 | 102499.6334 | 0 | 176904.2119 | 0 | 117547.8381 | 23581.5 | 55023.5 | 53058.375 | 47163 | 20769.8624 | 8760 | 1150.2925 | 3953.3642 | 0 | 0 | 0 | 5882.055 | 3910.1153 | -1115.7004 | 849.299 | 2110.8258 | 8760 | 3052.2794 | 2485.1868 | 567.0927 | 3051.699 | 6046.5519 | 0 | 7446.8986 | 4535.8864 | 0 | 2716.1282 | 8760 | 0 | 69.325 | 323.7 | 1446.5 | 1056758.5971 | 186766.0544 | 2964.475 | -12.7274
333 | C | SOK | STR | FC | FP | HC | OFF0 | 0.28797 | 11.5 | 0.863 | 8760 | 101891.1077 | 0 | 176561.4848 | 0 | 117547.8381 | 23611.5 | 55093.5 | 53125.875 | 47223 | 21525.9891 | 8760 | 1150.2925 | 3970.5133 | 0 | 0 | 0 | 5860.4789 | 3930.5831 | -1144.7446 | 830.186 | 2090.6384 | 8760 | 3052.5837 | 2496.6555 | 555.9283 | 3051.699 | 6046.5519 | 0 | 7448.1596 | 4536.7784 | 0 | 2749.5277 | 8760 | 0 | 67.5 | 326.025 | 1446.5 | 1056775.281 | 186766.0544 | 2985.35 | -12.7321
334 | C | SOK | STR | FC | FP | HC | OFF0 | 0.28797 | 15.5 | 0.388 | 8760 | 103517.5178 | 0 | 172094.7826 | 0 | 117547.8381 | 23215.5 | 54169.5 | 52234.875 | 46431 | 19021.5609 | 8760 | 1150.2925 | 4688.2429 | 0 | 0 | 0 | 5720.3036 | 3458.9774 | -1125.1793 | 1282.5227 | 2192.7921 | 8760 | 3051.8059 | 2195.6829 | 856.123 | 3051.699 | 6046.5519 | 0 | 7439.603 | 4532.4974 | 0 | 3352.015 | 8760 | 0 | 102.7 | 284.225 | 1446.5 | 1056488.823 | 186766.0544 | 3027.05 | -12.8523
335 | C | SOK | STR | FC | FP | HC | OFF0 | 0.28797 | 15.5 | 0.775 | 8760 | 103319.8805 | 0 | 170429.8936 | 0 | 117547.8381 | 23221.5 | 54183.5 | 52248.375 | 46443 | 18945.2465 | 8760 | 1150.2925 | 4838.4727 | 0 | 0 | 0 | 5625.1573 | 3400.7742 | -1176.7489 | 1331.5375 | 2142.493 | 8760 | 3051.9893 | 2162.4027 | 889.5865 | 3051.699 | 6046.5519 | 0 | 7438.9175 | 4533.1442 | 0 | 3546.2997 | 8760 | 0 | 106.95 | 280.075 | 1446.5 | 1056414.53 | 186766.0544 | 3052.3 | -13.6517
336 | C | SOK | STR | FC | FP | HC | OFF0 | 0.28797 | 15.5 | 1.163 | 8760 | 103545.3837 | 0 | 169042.4861 | 0 | 117547.8381 | 23226 | 54194 | 52258.5 | 46452 | 19519.55 | 8760 | 1150.2925 | 4931.4078 | 0 | 0 | 0 | 5552.4325 | 3380.1182 | -1187.2888 | 1351.3323 | 2116.143 | 8760 | 3052.547 | 2150.8739 | 901.6731 | 3051.699 | 6046.5519 | 0 | 7440.6828 | 4533.4039 | 0 | 3662.1784 | 8760 | 0 | 109.35 | 277.75 | 1446.5 | 1056350.0347 | 186766.0544 | 3056.95 | -11.3696
337 | C | SOK | STR | FC | FP | HC | OFF0 | 0.28797 | 20 | 0.5 | 8760 | 102973.0887 | 0 | 166665.8945 | 0 | 117547.8381 | 22935 | 53515 | 51603.75 | 45870 | 18308.7889 | 8760 | 1150.2925 | 5374.1523 | 0 | 0 | 0 | 5485.2927 | 3107.1992 | -1179.2774 | 1613.6805 | 2203.4426 | 8760 | 3051.8418 | 1975.2513 | 1076.5905 | 3051.699 | 6046.5519 | 0 | 7435.0036 | 4528.8034 | 0 | 4001.7194 | 8760 | 0 | 128.875 | 253.375 | 1446.5 | 1056737.1079 | 186766.0544 | 3135.7 | -12.1625
338 | C | SOK | STR | FC | FP | HC | OFF0 | 0.28797 | 20 | 1 | 8760 | 104518.7188 | 0 | 164031.3202 | 0 | 117547.8381 | 22833 | 53277 | 51374.25 | 45666 | 17694.7498 | 8760 | 1150.2925 | 5679.2196 | 0 | 0 | 0 | 5358.9788 | 2938.0571 | -1226.0252 | 1769.38 | 2160.3075 | 8760 | 3051.9889 | 1870.8825 | 1181.1064 | 3051.699 | 6046.5519 | 0 | 7432.1344 | 4528.4398 | 0 | 4346.4125 | 8760 | 0 | 141.225 | 239.325 | 1446.5 | 1056685.5448 | 186766.0544 | 3136.35 | -11.2008
339 | C | SOK | STR | FC | FP | HC | OFF0 | 0.28797 | 20 | 1.5 | 8760 | 105838.4643 | 0 | 162510.4216 | 0 | 117547.8381 | 22812 | 53228 | 51327 | 45624 | 17047.4143 | 8760 | 1150.2925 | 5839.389 | 0 | 0 | 0 | 5281.8129 | 2862.1901 | -1240.1368 | 1838.5315 | 2145.1637 | 8760 | 3052.8255 | 1826.7767 | 1226.0488 | 3051.699 | 6046.5519 | 0 | 7432.8562 | 4530.0027 | 0 | 4522.2242 | 8760 | 0 | 147.475 | 232.725 | 1446.5 | 1056422.0752 | 186766.0544 | 3126 | -11.2066
340 | C | SOK | STR | FC | FP | HC | OFF | 0.28797 | 24 | 0.6 | 8760 | 103614.7164 | 0 | 162464.6746 | 0 | 117547.8381 | 22837.5 | 53287.5 | 51384.375 | 45675 | 18495.9497 | 8760 | 1150.2925 | 5905.0385 | 0 | 0 | 0 | 5304.1277 | 2868.927 | -1215.28 | 1852.1157 | 2207.3439 | 8760 | 3052.0286 | 1816.7888 | 1235.2398 | 3051.699 | 6046.5519 | 0 | 7432.259 | 4527.7266 | 0 | 4509.8183 | 8760 | 0 | 148.75 | 231.875 | 1446.5 | 1056392.8487 | 186766.0544 | 3208.925 | -13.6546
341 | C | SOK | STR | FC | FP | HC | OFF | 0.28797 | 24 | 1.2 | 8760 | 106269.0581 | 0 | 158396.1959 | 0 | 117547.8381 | 22671 | 52899 | 51009.75 | 45342 | 17343.5888 | 8760 | 1150.2925 | 6319.6019 | 0 | 0 | 0 | 5126.6853 | 2646.9017 | -1258.7478 | 2055.817 | 2170.4453 | 8760 | 3052.3997 | 1682.5072 | 1369.8925 | 3051.699 | 6046.5519 | 0 | 7430.3225 | 4527.3999 | 0 | 4961.5933 | 8760 | 0 | 165.1 | 212.75 | 1446.5 | 1056211.4396 | 186766.0544 | 3194.425 | -11.888
342 | C | SOK | STR | FC | FP | HC | OFF | 0.28797 | 24 | 1.8 | 8760 | 107520.3225 | 0 | 157001.2889 | 0 | 117547.8381 | 22603.5 | 52741.5 | 50857.875 | 45207 | 17066.8816 | 8760 | 1150.2925 | 6529.0756 | 0 | 0 | 0 | 5021.525 | 2538.8847 | -1274.5157 | 2146.5365 | 2146.3755 | 8760 | 3052.5742 | 1623.1935 | 1429.3807 | 3051.699 | 6046.5519 | 0 | 7430.3393 | 4527.6965 | 0 | 5193.9016 | 8760 | 0 | 172.65 | 204.075 | 1446.5 | 1056526.2079 | 186766.0544 | 3187.325 | -9.8327
343 | C | SOK | STR | FC | FP | HC | OFF | 0.28797 | 28.5 | 0.713 | 8760 | 104917.5409 | 0 | 157652.9954 | 0 | 117547.8381 | 22672.5 | 52902.5 | 51013.125 | 45345 | 20572.1203 | 8760 | 1150.2925 | 6391.2483 | 0 | 0 | 0 | 5104.9669 | 2605.045 | -1247.5407 | 2109.9097 | 2208.2056 | 8760 | 3052.0442 | 1648.4379 | 1403.6064 | 3051.699 | 6046.5519 | 0 | 7431.943 | 4522.9358 | 0 | 4980.2315 | 8760 | 0 | 170.75 | 207.125 | 1446.5 | 1056772.2989 | 186766.0544 | 3278.5 | -12.1373
344 | C | SOK | STR | FC | FP | HC | OFF | 0.28797 | 28.5 | 1.425 | 8760 | 107530.1489 | 0 | 153221.5409 | 0 | 117547.8381 | 22455 | 52395 | 50523.75 | 44910 | 17123.0649 | 8760 | 1150.2925 | 6890.0913 | 0 | 0 | 0 | 4883.0984 | 2335.4693 | -1288.8404 | 2335.8716 | 2171.2445 | 8760 | 3052.5513 | 1499.1824 | 1553.3689 | 3051.699 | 6046.5519 | 0 | 7428.7309 | 4523.3825 | 0 | 5515.6987 | 8760 | 0 | 188.6 | 185.65 | 1446.5 | 1056680.8213 | 186766.0544 | 3267.175 | -11.21
345 | C | SOK | STR | FC | FP | HC | OFF | 0.28797 | 28.5 | 2.138 | 8760 | 109253.7601 | 0 | 151095.4327 | 0 | 117547.8381 | 22410 | 52290 | 50422.5 | 44820 | 17956.9882 | 8760 | 1150.2925 | 7164.9799 | 0 | 0 | 0 | 4761.0335 | 2218.3238 | -1301.0618 | 2445.7408 | 2145.5291 | 8760 | 3052.29 | 1425.4689 | 1626.821 | 3051.699 | 6046.5519 | 0 | 7428.3791 | 4523.3378 | 0 | 5813.5473 | 8760 | 0 | 197.65 | 175.85 | 1446.5 | 1056601.5827 | 186766.0544 | 3254.25 | -8.4129
346 | C | SOK | TOU | CC | ET | HC | R100 | 3.2558 | 16.5 | 0.413 | 8760 | 146290.9616 | 0 | 170641.3795 | 65533.1035 | 194629.3775 | 15337.5 | 35787.5 | 34509.375 | 30675 | 19183.9594 | 8760 | 1482.4089 | 10071.3076 | 0 | 0 | 1862.0937 | 18828.9954 | 2253.5643 | -1102.4126 | 1103.5288 | 2979.0114 | 8760 | 2357.246 | 1580.5987 | 776.6473 | 2362.3049 | 20758.9881 | 4876.3514 | 5440.3747 | 3242.2372 | 0 | 7866.9404 | 8760 | 0 | 86.475 | 169.15 | 850.5 | 759296.8135 | 210834.9497 | 2253.525 | -60.0888
347 | C | SOK | TOU | CC | ET | HC | R100 | 3.2558 | 16.5 | 0.825 | 8760 | 154872.918 | 0 | 167811.8181 | 65533.1035 | 194629.3775 | 15366 | 35854 | 34573.5 | 30732 | 18670.4386 | 8760 | 1482.4089 | 10789.3971 | 0 | 0 | 1683.4179 | 18501.8584 | 2174.347 | -1162.4444 | 1171.0899 | 2952.3326 | 8760 | 2355.1054 | 1522.5732 | 832.5322 | 2362.3049 | 20758.9881 | 4926.7454 | 5435.9845 | 3240.6129 | 0 | 8599.2085 | 8760 | 0 | 90.175 | 165.925 | 850.5 | 759208.3238 | 210834.9497 | 2142.475 | -57.9257
348 | C | SOK | TOU | CC | ET | HC | R100 | 3.2558 | 16.5 | 1.238 | 8760 | 157797.2424 | 0 | 166404.162 | 65533.1035 | 194629.3775 | 15349.5 | 35815.5 | 34536.375 | 30699 | 18546.0886 | 8760 | 1482.4089 | 11020.6314 | 0 | 0 | 1671.5537 | 18356.9203 | 2119.0097 | -1173.209 | 1220.533 | 2932.7046 | 8760 | 2355.5837 | 1483.6393 | 871.9444 | 2362.3049 | 20758.9881 | 4937.472 | 5440.9818 | 3241.7934 | 0 | 8849.5904 | 8760 | 0 | 92.7 | 163.125 | 850.5 | 759254.8438 | 210834.9497 | 2104.1 | -53.1217
349 | C | SOK | TOU | CC | ET | HC | R100 | 3.2558 | 22.5 | 0.563 | 8760 | 143916.3678 | 0 | 162994.8893 | 65533.1035 | 194629.3775 | 15025.5 | 35059.5 | 33807.375 | 30051 | 14487.5081 | 8760 | 1482.4089 | 12080.2912 | 0 | 0 | 1689.8403 | 17837.939 | 1800.1772 | -1183.5371 | 1537.0783 | 3089.3182 | 8760 | 2356.9074 | 1274.3783 | 1082.5291 | 2362.3049 | 20758.9881 | 4933.5758 | 5458.2033 | 3248.9363 | 0 | 9680.938 | 8760 | 0 | 118.55 | 131.875 | 850.5 | 759152.4729 | 210834.9497 | 2451.525 | -40.5796
350 | C | SOK | TOU | CC | ET | HC | R100 | 3.2558 | 22.5 | 1.125 | 8760 | 152647.0379 | 0 | 159613.3647 | 65533.1035 | 194629.3775 | 15012 | 35028 | 33777 | 30024 | 14088.5487 | 8760 | 1482.4089 | 12967.7988 | 0 | 0 | 1549.5114 | 17376.7053 | 1640.5203 | -1237.7781 | 1684.7652 | 3070.6335 | 8760 | 2357.915 | 1157.6019 | 1200.3131 | 2362.3049 | 20758.9881 | 4980.1665 | 5460.7498 | 3252.524 | 0 | 10573.5828 | 8760 | 0 | 126.275 | 123.925 | 850.5 | 759300.4641 | 210834.9497 | 2344.825 | -40.4916
351 | C | SOK | TOU | CC | ET | HC | R100 | 3.2558 | 22.5 | 1.688 | 8760 | 156125.5763 | 0 | 157828.4837 | 65533.1035 | 194629.3775 | 14979 | 34951 | 33702.75 | 29958 | 11793.6317 | 8760 | 1482.4089 | 13296.729 | 0 | 0 | 1502.72 | 17204.6587 | 1547.5807 | -1249.4717 | 1768.5074 | 3053.5612 | 8760 | 2356.9644 | 1093.3451 | 1263.6193 | 2362.3049 | 20758.9881 | 4983.9368 | 5460.0162 | 3252.9341 | 0 | 10918.9811 | 8760 | 0 | 131.625 | 118.025 | 850.5 | 759279.208 | 210834.9497 | 2301.175 | -38.8372
352 | C | SOK | TOU | CC | ET | HC | R100 | 3.2558 | 29 | 0.725 | 8760 | 142550.1228 | 0 | 156990.7896 | 65533.1035 | 194629.3775 | 14803.5 | 34541.5 | 33307.875 | 29607 | 18796.1927 | 8760 | 1482.4089 | 13710.377 | 0 | 0 | 1543.3759 | 16886.6495 | 1548.6777 | -1242.3929 | 1802.2455 | 3148.1206 | 8760 | 2357.8332 | 1076.9452 | 1280.8881 | 2362.3049 | 20758.9881 | 4974.0523 | 5429.3136 | 3246.7539 | 0 | 11197.6319 | 8760 | 0 | 135.75 | 110.975 | 850.5 | 759269.3502 | 210834.9497 | 2636.05 | -85.0763
353 | C | SOK | TOU | CC | ET | HC | R100 | 3.2558 | 29 | 1.45 | 8760 | 151365.4153 | 0 | 152487.3398 | 65533.1035 | 194629.3775 | 14781 | 34489 | 33257.25 | 29562 | 14287.5642 | 8760 | 1482.4089 | 14736.1822 | 0 | 0 | 1423.3096 | 16292.7016 | 1334.3586 | -1291.4157 | 1999.4351 | 3129.9043 | 8760 | 2357.2148 | 932.2329 | 1424.9819 | 2362.3049 | 20758.9881 | 5022.2918 | 5452.9812 | 3250.9381 | 0 | 12212.9665 | 8760 | 0 | 149.175 | 97.175 | 850.5 | 759290.9377 | 210834.9497 | 2534.25 | -51.5595
354 | C | SOK | TOU | CC | ET | HC | R100 | 3.2558 | 29 | 2.175 | 8760 | 155179.3506 | 0 | 150828.4504 | 65533.1035 | 194629.3775 | 14767.5 | 34457.5 | 33226.875 | 29535 | 15310.7223 | 8760 | 1482.4089 | 15158.5169 | 0 | 0 | 1399.4786 | 16056.6568 | 1224.5713 | -1304.8443 | 2094.2459 | 3119.4935 | 8760 | 2358.5771 | 861.913 | 1496.6641 | 2362.3049 | 20758.9881 | 5029.8835 | 5456.3479 | 3253.808 | 0 | 12641.3154 | 8760 | 0 | 156.2 | 89.925 | 850.5 | 759343.064 | 210834.9497 | 2491.325 | -51.9473
355 | C | SOK | TOU | CC | ET | HC | R10 | 3.2558 | 35 | 0.875 | 8760 | 142749.8898 | 0 | 152042.6195 | 65533.1035 | 194629.3775 | 14478 | 33782 | 32575.5 | 28956 | 11842.1283 | 8760 | 1482.4089 | 14903.2765 | 0 | 0 | 1442.3207 | 16074.0986 | 1223.8036 | -1279.6417 | 2086.9315 | 3176.5959 | 8760 | 2359.179 | 879.6558 | 1479.5231 | 2362.3049 | 20758.9881 | 5002.83 | 5477.8358 | 3257.3995 | 0 | 12316.2469 | 8760 | 0 | 154.25 | 87.05 | 850.5 | 759274.1501 | 210834.9497 | 2776.9 | -29.3695
356 | C | SOK | TOU | CC | ET | HC | R10 | 3.2558 | 35 | 1.75 | 8760 | 151665.9982 | 0 | 146702.9755 | 65533.1035 | 194629.3775 | 14503.5 | 33841.5 | 32632.875 | 29007 | 12150.8906 | 8760 | 1482.4089 | 16036.1828 | 0 | 0 | 1341.9217 | 15441.4293 | 1050.4942 | -1328.2294 | 2255.5894 | 3167.3587 | 8760 | 2359.8222 | 752.2381 | 1607.584 | 2362.3049 | 20758.9881 | 5050.1242 | 5480.1976 | 3259.4986 | 0 | 13417.758 | 8760 | 0 | 165.725 | 76 | 850.5 | 759299.1428 | 210834.9497 | 2682.425 | -27.6504
357 | C | SOK | TOU | CC | ET | HC | R10 | 3.2558 | 35 | 2.625 | 8760 | 155395.9467 | 0 | 145338.8165 | 65533.1035 | 194629.3775 | 14496 | 33824 | 32616 | 28992 | 11912.2407 | 8760 | 1482.4089 | 16483.748 | 0 | 0 | 1341.4868 | 15141.8908 | 948.681 | -1342.3447 | 2347.9236 | 3153.9657 | 8760 | 2359.3586 | 682.7177 | 1676.6409 | 2362.3049 | 20758.9881 | 5057.4078 | 5482.9795 | 3260.5424 | 0 | 13872.403 | 8760 | 0 | 172.25 | 69.35 | 850.5 | 759262.7192 | 210834.9497 | 2642.575 | -23.2672
358 | C | SOK | TOU | CC | ET | HC | R10 | 3.2558 | 41 | 1.025 | 8760 | 144814.1337 | 0 | 147569.1677 | 65533.1035 | 194629.3775 | 14323.5 | 33421.5 | 32227.875 | 28647 | 12708.1917 | 8760 | 1482.4089 | 15960.0403 | 0 | 0 | 1372.322 | 15318.6502 | 1073.6932 | -1310.9731 | 2228.2012 | 3193.2182 | 8760 | 2359.5539 | 776.7582 | 1582.7957 | 2362.3049 | 20758.9881 | 5030.4724 | 5483.7933 | 3259.1363 | 0 | 13322.0211 | 8760 | 0 | 162.475 | 76.25 | 850.5 | 759280.6735 | 210834.9497 | 2891.125 | -22.8465
359 | C | SOK | TOU | CC | ET | HC | R10 | 3.2558 | 41 | 2.05 | 8760 | 153749.9659 | 0 | 142375.0141 | 65533.1035 | 194629.3775 | 14221.5 | 33183.5 | 31998.375 | 28443 | 10603.1787 | 8760 | 1482.4089 | 17157.8804 | 0 | 0 | 1267.9514 | 14646.9518 | 852.3982 | -1356.0139 | 2441.8853 | 3172.7375 | 8760 | 2359.4942 | 613.9964 | 1745.4978 | 2362.3049 | 20758.9881 | 5066.561 | 5484.1396 | 3260.9228 | 0 | 14492.1412 | 8760 | 0 | 174.925 | 62.1 | 850.5 | 759381.716 | 210834.9497 | 2802.475 | -21.703
360 | C | SOK | TOU | CC | ET | HC | R10 | 3.2558 | 41 | 3.075 | 8760 | 158090.1421 | 0 | 140212.9082 | 65533.1035 | 194629.3775 | 14304 | 33376 | 32184 | 28608 | 10994.4249 | 8760 | 1482.4089 | 17729.8967 | 0 | 0 | 1264.3415 | 14277.1038 | 717.3864 | -1366.8092 | 2569.802 | 3160.4844 | 8760 | 2359.7868 | 520.2733 | 1839.5136 | 2362.3049 | 20758.9881 | 5073.1109 | 5487.7712 | 3263.3231 | 0 | 15068.6808 | 8760 | 0 | 185.95 | 52.45 | 850.5 | 759316.9743 | 210834.9497 | 2760.35 | -19.6871
361 | C | SOK | TOU | CC | ET | HC | R600 | 3.8366 | 16.5 | 0.413 | 8760 | 147722.6165 | 0 | 154994.4227 | 65533.1035 | 135297.3232 | 19096.5 | 44558.5 | 42967.125 | 38193 | 20762.8983 | 8760 | 1475.3019 | 10069.6946 | 0 | 0 | 1810.8699 | 11801.6519 | 3005.5526 | -1160.0911 | 1288.1921 | 2958.465 | 8760 | 3061.4646 | 2149.7614 | 911.7032 | 3066.6602 | 12891.6972 | 5505.3109 | 7056.0837 | 4166.8489 | 0 | 7799.9243 | 8760 | 0 | 100.075 | 218.2 | 1048.625 | 972734.8511 | 189624.8638 | 2239.825 | -69.4844
362 | C | SOK | TOU | CC | ET | HC | R600 | 3.8366 | 16.5 | 0.825 | 8760 | 155684.3505 | 0 | 153255.2886 | 65533.1035 | 135297.3232 | 19140 | 44660 | 43065 | 38280 | 20219.3431 | 8760 | 1475.3019 | 10723.471 | 0 | 0 | 1630.2511 | 11629.9289 | 2950.4649 | -1231.3375 | 1335.4496 | 2962.4685 | 8760 | 3060.1673 | 2103.9351 | 956.2322 | 3066.6602 | 12891.6972 | 5599.7586 | 7051.575 | 4166.2707 | 0 | 8430.2848 | 8760 | 0 | 100.825 | 218.175 | 1048.625 | 972717.708 | 189624.8638 | 2135.5 | -67.5642
363 | C | SOK | TOU | CC | ET | HC | R600 | 3.8366 | 16.5 | 1.238 | 8760 | 158798.4851 | 0 | 152563.0848 | 65533.1035 | 135297.3232 | 19179 | 44751 | 43152.75 | 38358 | 20798.8995 | 8760 | 1475.3019 | 10965.0366 | 0 | 0 | 1607.4986 | 11542.3915 | 2881.4507 | -1253.4096 | 1404.5437 | 2963.151 | 8760 | 3060.5246 | 2047.9319 | 1012.5928 | 3066.6602 | 12891.6972 | 5625.4861 | 7056.9021 | 4168.4058 | 0 | 8671.2158 | 8760 | 0 | 104.475 | 215.175 | 1048.625 | 972732.0439 | 189624.8638 | 2095.2 | -63.6897
364 | C | SOK | TOU | CC | ET | HC | R600 | 3.8366 | 22.5 | 0.563 | 8760 | 144303.221 | 0 | 148560.6016 | 65533.1035 | 135297.3232 | 18715.5 | 43669.5 | 42109.875 | 37431 | 15867.2812 | 8760 | 1475.3019 | 11938.2825 | 0 | 0 | 1609.9358 | 11160.2891 | 2470.0841 | -1253.2639 | 1807.0549 | 3085.6556 | 8760 | 3061.4468 | 1778.8699 | 1282.5769 | 3066.6602 | 12891.6972 | 5599.5309 | 7073.5192 | 4175.1393 | 0 | 9455.0072 | 8760 | 0 | 136.35 | 175.575 | 1048.625 | 972629.247 | 189624.8638 | 2451 | -50.0733
365 | C | SOK | TOU | CC | ET | HC | R600 | 3.8366 | 22.5 | 1.125 | 8760 | 152032.5215 | 0 | 145788.7865 | 65533.1035 | 135297.3232 | 18757.5 | 43767.5 | 42204.375 | 37515 | 16006.956 | 8760 | 1475.3019 | 12708.0554 | 0 | 0 | 1499.9718 | 10898.8653 | 2282.3458 | -1313.1669 | 1989.0336 | 3088.9666 | 8760 | 3062.2771 | 1632.7359 | 1429.5412 | 3066.6602 | 12891.6972 | 5672.9554 | 7078.0017 | 4179.135 | 0 | 10204.0961 | 8760 | 0 | 145.725 | 166.9 | 1048.625 | 972651.2031 | 189624.8638 | 2356.625 | -45.8643
366 | C | SOK | TOU | CC | ET | HC | R600 | 3.8366 | 22.5 | 1.688 | 8760 | 155458.0281 | 0 | 144275.3874 | 65533.1035 | 135297.3232 | 18744 | 43736 | 42174 | 37488 | 14674.674 | 8760 | 1475.3019 | 13035.6986 | 0 | 0 | 1485.0194 | 10763.6081 | 2161.3608 | -1331.1395 | 2108.9965 | 3089.1318 | 8760 | 3061.5281 | 1539.0583 | 1522.4698 | 3066.6602 | 12891.6972 | 5690.8735 | 7080.7277 | 4180.3161 | 0 | 10527.4542 | 8760 | 0 | 152.5 | 159.9 | 1048.625 | 972679.8342 | 189624.8638 | 2314.575 | -40.9008
367 | C | SOK | TOU | CC | ET | HC | R600 | 3.8366 | 29 | 0.725 | 8760 | 141609.7613 | 0 | 142797.9859 | 65533.1035 | 135297.3232 | 18472.5 | 43102.5 | 41563.125 | 36945 | 20427.5733 | 8760 | 1475.3019 | 13359.0127 | 0 | 0 | 1479.6113 | 10505.9494 | 2142.0854 | -1313.9128 | 2150.0366 | 3142.4036 | 8760 | 3062.0561 | 1523.9015 | 1538.1545 | 3066.6602 | 12891.6972 | 5657.6671 | 7039.5734 | 4173.0777 | 0 | 10762.5435 | 8760 | 0 | 158.775 | 149.1 | 1048.625 | 972624.5662 | 189624.8638 | 2649.975 | -101.6002
368 | C | SOK | TOU | CC | ET | HC | R600 | 3.8366 | 29 | 1.45 | 8760 | 149135.8894 | 0 | 139463.7082 | 65533.1035 | 135297.3232 | 18408 | 42952 | 41418 | 36816 | 17608.065 | 8760 | 1475.3019 | 14221.6245 | 0 | 0 | 1372.533 | 10152.3486 | 1851.3695 | -1361.5231 | 2416.6558 | 3140.317 | 8760 | 3062.0691 | 1319.3516 | 1742.7174 | 3066.6602 | 12891.6972 | 5712.0713 | 7061.1664 | 4178.9982 | 0 | 11599.2842 | 8760 | 0 | 173.925 | 132.875 | 1048.625 | 972687.4686 | 189624.8638 | 2563.475 | -73.9077
369 | C | SOK | TOU | CC | ET | HC | R600 | 3.8366 | 29 | 2.175 | 8760 | 153275.6266 | 0 | 137673.5775 | 65533.1035 | 135297.3232 | 18417 | 42973 | 41438.25 | 36834 | 19040.9753 | 8760 | 1475.3019 | 14678.5319 | 0 | 0 | 1366.2688 | 9953.0785 | 1699.3681 | -1376.6079 | 2569.948 | 3134.6863 | 8760 | 3062.7026 | 1201.4704 | 1861.2322 | 3066.6602 | 12891.6972 | 5728.0181 | 7067.7681 | 4181.8366 | 0 | 12057.3679 | 8760 | 0 | 183.35 | 123.6 | 1048.625 | 972715.0073 | 189624.8638 | 2516.975 | -67.9075
370 | C | SOK | TOU | CC | ET | HC | R60 | 3.8366 | 35 | 0.875 | 8760 | 140912.0787 | 0 | 138085.3001 | 65533.1035 | 135297.3232 | 18117 | 42273 | 40763.25 | 36234 | 16281.6418 | 8760 | 1475.3019 | 14365.761 | 0 | 0 | 1364.5382 | 9948.8829 | 1775.5592 | -1353.1496 | 2486.1625 | 3173.3781 | 8760 | 3062.2648 | 1285.5334 | 1776.7314 | 3066.6602 | 12891.6972 | 5691.9518 | 7090.555 | 4181.5586 | 0 | 11697.5837 | 8760 | 0 | 179.85 | 122.1 | 1048.625 | 972676.7682 | 189624.8638 | 2798 | -37.9747
371 | C | SOK | TOU | CC | ET | HC | R60 | 3.8366 | 35 | 1.75 | 8760 | 148811.0399 | 0 | 134084.3168 | 65533.1035 | 135297.3232 | 18090 | 42210 | 40702.5 | 36180 | 14301.551 | 8760 | 1475.3019 | 15385.0434 | 0 | 0 | 1281.553 | 9499.1165 | 1477.5852 | -1396.1263 | 2770.7789 | 3164.0288 | 8760 | 3063.3467 | 1065.8439 | 1997.5028 | 3066.6602 | 12891.6972 | 5740.1908 | 7103.143 | 4188.8396 | 0 | 12686.1926 | 8760 | 0 | 195.825 | 105.675 | 1048.625 | 972736.2382 | 189624.8638 | 2716.2 | -24.9692
372 | C | SOK | TOU | CC | ET | HC | R60 | 3.8366 | 35 | 2.625 | 8760 | 152918.9414 | 0 | 132241.6897 | 65533.1035 | 135297.3232 | 18061.5 | 42143.5 | 40638.375 | 36123 | 14857.71 | 8760 | 1475.3019 | 15881.5847 | 0 | 0 | 1255.9659 | 9293.3505 | 1293.6319 | -1410.057 | 2945.8388 | 3157.6085 | 8760 | 3063.0342 | 933.6028 | 2129.4314 | 3066.6602 | 12891.6972 | 5753.2001 | 7106.2877 | 4190.3251 | 0 | 13182.6866 | 8760 | 0 | 207.375 | 93.65 | 1048.625 | 972710.3092 | 189624.8638 | 2673.875 | -21.3126
373 | C | SOK | TOU | CC | ET | HC | R60 | 3.8366 | 41 | 1.025 | 8760 | 142068.3226 | 0 | 134085.0668 | 65533.1035 | 135297.3232 | 17892 | 41748 | 40257 | 35784 | 16207.8068 | 8760 | 1475.3019 | 15258.521 | 0 | 0 | 1275.9616 | 9421.2734 | 1553.9429 | -1385.6143 | 2696.959 | 3179.455 | 8760 | 3063.5591 | 1130.0125 | 1933.5466 | 3066.6602 | 12891.6972 | 5720.2526 | 7098.6445 | 4185.8984 | 0 | 12547.9899 | 8760 | 0 | 191.275 | 106.925 | 1048.625 | 972761.6665 | 189624.8638 | 2920.9 | -34.2618
374 | C | SOK | TOU | CC | ET | HC | R60 | 3.8366 | 41 | 2.05 | 8760 | 150631.2623 | 0 | 129606.3654 | 65533.1035 | 135297.3232 | 17809.5 | 41555.5 | 40071.375 | 35619 | 13356.011 | 8760 | 1475.3019 | 16404.7098 | 0 | 0 | 1181.4046 | 8915.2893 | 1211.0095 | -1426.5043 | 3024.2877 | 3173.8432 | 8760 | 3064.1102 | 883.0074 | 2181.1027 | 3066.6602 | 12891.6972 | 5766.2155 | 7109.4948 | 4193.495 | 0 | 13658.2032 | 8760 | 0 | 210.85 | 85.975 | 1048.625 | 972716.3623 | 189624.8638 | 2836.875 | -21.9763
375 | C | SOK | TOU | CC | ET | HC | R60 | 3.8366 | 41 | 3.075 | 8760 | 154931.109 | 0 | 127206.5254 | 65533.1035 | 135297.3232 | 17823 | 41587 | 40101.75 | 35646 | 13541.3657 | 8760 | 1475.3019 | 16975.883 | 0 | 0 | 1159.6229 | 8667.7998 | 1037.9854 | -1440.3681 | 3196.6308 | 3177.0304 | 8760 | 3063.2538 | 751.1104 | 2312.1433 | 3066.6602 | 12891.6972 | 5780.5285 | 7108.8466 | 4194.0389 | 0 | 14215.2731 | 8760 | 0 | 222.6 | 74.45 | 1048.625 | 972664.3613 | 189624.8638 | 2796.425 | -22.0846
376 | C | SOK | TOU | CC | FP | HC | R100 | 3.2558 | 16.5 | 0.413 | 8760 | 148649.5748 | 0 | 173802.4187 | 65533.1035 | 194629.3775 | 15616.5 | 36438.5 | 35137.125 | 31233 | 22930.5029 | 8760 | 1482.4089 | 8508.3611 | 0 | 0 | 1967.9037 | 19176.3149 | 2629.5661 | -1026.7274 | 742.8253 | 2522.8605 | 8760 | 2355.3738 | 1836.1921 | 519.1816 | 2362.3049 | 20758.9881 | 4818.6923 | 5448.9337 | 3235.5814 | 0 | 6862.4037 | 8760 | 0 | 60.5 | 199.775 | 850.5 | 759231.6235 | 210834.9497 | 2341.05 | -62.5614
377 | C | SOK | TOU | CC | FP | HC | R100 | 3.2558 | 16.5 | 0.825 | 8760 | 153691.2547 | 0 | 170875.3639 | 65533.1035 | 194629.3775 | 15636 | 36484 | 35181 | 31272 | 23312.9994 | 8760 | 1482.4089 | 9143.985 | 0 | 0 | 1768.4567 | 18807.492 | 2627.0219 | -1086.2705 | 737.2574 | 2468.4581 | 8760 | 2354.551 | 1832.9314 | 521.6196 | 2362.3049 | 20758.9881 | 4864.5217 | 5446.638 | 3235.2946 | 0 | 7552.2548 | 8760 | 0 | 58.175 | 202.425 | 850.5 | 759183.0688 | 210834.9497 | 2300.15 | -62.3957
378 | C | SOK | TOU | CC | FP | HC | R100 | 3.2558 | 16.5 | 1.238 | 8760 | 155511.0772 | 0 | 169601.1988 | 65533.1035 | 194629.3775 | 15651 | 36519 | 35214.75 | 31302 | 23264.4215 | 8760 | 1482.4089 | 9397.2925 | 0 | 0 | 1715.4041 | 18628.0768 | 2604.0729 | -1103.0697 | 755.3509 | 2434.5674 | 8760 | 2354.7348 | 1817.4984 | 537.2364 | 2362.3049 | 20758.9881 | 4879.0674 | 5447.3157 | 3235.5536 | 0 | 7839.0894 | 8760 | 0 | 58.825 | 202.025 | 850.5 | 759243.5282 | 210834.9497 | 2289.15 | -63.4012
379 | C | SOK | TOU | CC | FP | HC | R100 | 3.2558 | 22.5 | 0.563 | 8760 | 150496.7246 | 0 | 167743.5727 | 65533.1035 | 194629.3775 | 15414 | 35966 | 34681.5 | 30828 | 19188.1244 | 8760 | 1482.4089 | 10128.4491 | 0 | 0 | 1772.8287 | 18363.5733 | 2315.603 | -1115.1076 | 1041.8094 | 2591.1041 | 8760 | 2356.1505 | 1625.7954 | 730.3551 | 2362.3049 | 20758.9881 | 4884.5798 | 5457.937 | 3239.9629 | 0 | 8371.3923 | 8760 | 0 | 82.85 | 174.05 | 850.5 | 759310.1998 | 210834.9497 | 2499.475 | -54.3957
380 | C | SOK | TOU | CC | FP | HC | R100 | 3.2558 | 22.5 | 1.125 | 8760 | 155778.6051 | 0 | 163896.3292 | 65533.1035 | 194629.3775 | 15432 | 36008 | 34722 | 30864 | 19972.7539 | 8760 | 1482.4089 | 10959.4892 | 0 | 0 | 1625.1791 | 17829.7161 | 2253.052 | -1170.0727 | 1103.9492 | 2535.7319 | 8760 | 2355.1598 | 1571.7215 | 783.4383 | 2362.3049 | 20758.9881 | 4927.0842 | 5458.428 | 3239.4818 | 0 | 9258.2353 | 8760 | 0 | 85.325 | 171.875 | 850.5 | 759258.6834 | 210834.9497 | 2462.55 | -50.2112
381 | C | SOK | TOU | CC | FP | HC | R100 | 3.2558 | 22.5 | 1.688 | 8760 | 157085.8381 | 0 | 162005.7052 | 65533.1035 | 194629.3775 | 15456 | 36064 | 34776 | 30912 | 19813.0454 | 8760 | 1482.4089 | 11261.3165 | 0 | 0 | 1586.1352 | 17612.5061 | 2204.3527 | -1185.4462 | 1153.1077 | 2497.1023 | 8760 | 2356.5193 | 1533.9109 | 822.6085 | 2362.3049 | 20758.9881 | 4934.5628 | 5463.1527 | 3243.0235 | 0 | 9596.0951 | 8760 | 0 | 87.875 | 169.725 | 850.5 | 759276.2536 | 210834.9497 | 2465.3 | -49.8364
382 | C | SOK | TOU | CC | FP | HC | R100 | 3.2558 | 29 | 0.725 | 8760 | 153682.6143 | 0 | 162032.7034 | 65533.1035 | 194629.3775 | 15294 | 35686 | 34411.5 | 30588 | 17862.0345 | 8760 | 1482.4089 | 11484.1466 | 0 | 0 | 1645.6255 | 17536.5748 | 2076.7216 | -1180.6402 | 1281.1928 | 2624.3287 | 8760 | 2356.2677 | 1452.3279 | 903.9397 | 2362.3049 | 20758.9881 | 4933.6082 | 5463.5306 | 3242.9388 | 0 | 9658.8643 | 8760 | 0 | 99.9 | 155 | 850.5 | 759200.2363 | 210834.9497 | 2642 | -50.1868
383 | C | SOK | TOU | CC | FP | HC | R100 | 3.2558 | 29 | 1.45 | 8760 | 158388.5517 | 0 | 157805.2353 | 65533.1035 | 194629.3775 | 15343.5 | 35801.5 | 34522.875 | 30687 | 19487.2593 | 8760 | 1482.4089 | 12450.8764 | 0 | 0 | 1513.1536 | 16920.8762 | 1982.2286 | -1231.0022 | 1378.1738 | 2561.4166 | 8760 | 2357.0789 | 1374.2905 | 982.7884 | 2362.3049 | 20758.9881 | 4969.1688 | 5457.7597 | 3243.7719 | 0 | 10684.8487 | 8760 | 0 | 105.225 | 150.5 | 850.5 | 759302.3714 | 210834.9497 | 2622.375 | -60.2331
384 | C | SOK | TOU | CC | FP | HC | R100 | 3.2558 | 29 | 2.175 | 8760 | 160029.687 | 0 | 155682.8768 | 65533.1035 | 194629.3775 | 15361.5 | 35843.5 | 34563.375 | 30723 | 19674.8135 | 8760 | 1482.4089 | 12877.9781 | 0 | 0 | 1460.752 | 16649.2715 | 1907.3972 | -1243.988 | 1448.8626 | 2525.8171 | 8760 | 2356.3646 | 1319.0088 | 1037.3558 | 2362.3049 | 20758.9881 | 4973.6978 | 5456.3825 | 3243.0578 | 0 | 11144.7563 | 8760 | 0 | 110.125 | 145.9 | 850.5 | 759241.4045 | 210834.9497 | 2621 | -60.5061
385 | C | SOK | TOU | CC | FP | HC | R10 | 3.2558 | 35 | 0.875 | 8760 | 158114.7065 | 0 | 157838.2331 | 65533.1035 | 194629.3775 | 15154.5 | 35360.5 | 34097.625 | 30309 | 16755.9449 | 8760 | 1482.4089 | 12566.9238 | 0 | 0 | 1550.5179 | 16831.4651 | 1865.1173 | -1224.4947 | 1464.7568 | 2636.4658 | 8760 | 2357.7636 | 1323.2255 | 1034.5381 | 2362.3049 | 20758.9881 | 4964.8215 | 5478.5949 | 3247.5973 | 0 | 10702.4691 | 8760 | 0 | 113.575 | 139 | 850.5 | 759215.2843 | 210834.9497 | 2749.925 | -36.4592
386 | C | SOK | TOU | CC | FP | HC | R10 | 3.2558 | 35 | 1.75 | 8760 | 162731.613 | 0 | 152431.0936 | 65533.1035 | 194629.3775 | 15165 | 35385 | 34121.25 | 30330 | 17534.3932 | 8760 | 1482.4089 | 13605.3253 | 0 | 0 | 1426.4764 | 16169.8526 | 1734.6942 | -1275.2443 | 1602.553 | 2574.675 | 8760 | 2357.5244 | 1217.9991 | 1139.5253 | 2362.3049 | 20758.9881 | 5001.2354 | 5479.7768 | 3247.8552 | 0 | 11798.0645 | 8760 | 0 | 122.15 | 130.6 | 850.5 | 759301.3695 | 210834.9497 | 2735.525 | -34.3314
387 | C | SOK | TOU | CC | FP | HC | R10 | 3.2558 | 35 | 2.625 | 8760 | 165050.14 | 0 | 150295.9859 | 65533.1035 | 194629.3775 | 15204 | 35476 | 34209 | 30408 | 18173.8712 | 8760 | 1482.4089 | 14123.7983 | 0 | 0 | 1382.1605 | 15828.8217 | 1646.3453 | -1287.5375 | 1680.172 | 2543.4106 | 8760 | 2356.9985 | 1160.1207 | 1196.8778 | 2362.3049 | 20758.9881 | 5006.8748 | 5478.358 | 3247.9123 | 0 | 12345.3551 | 8760 | 0 | 128.3 | 125.1 | 850.5 | 759233.1457 | 210834.9497 | 2725.825 | -34.8281
388 | C | SOK | TOU | CC | FP | HC | R10 | 3.2558 | 41 | 1.025 | 8760 | 163798.6646 | 0 | 153770.5043 | 65533.1035 | 194629.3775 | 15037.5 | 35087.5 | 33834.375 | 30075 | 17282.8781 | 8760 | 1482.4089 | 13506.0778 | 0 | 0 | 1478.2207 | 16207.7993 | 1735.0512 | -1258.2457 | 1591.2731 | 2641.3241 | 8760 | 2359.0654 | 1234.7904 | 1124.275 | 2362.3049 | 20758.9881 | 4989.3204 | 5483.6183 | 3248.921 | 0 | 11616.6114 | 8760 | 0 | 122.4 | 128.225 | 850.5 | 759326.9999 | 210834.9497 | 2842.075 | -34.1977
389 | C | SOK | TOU | CC | FP | HC | R10 | 3.2558 | 41 | 2.05 | 8760 | 167864.0035 | 0 | 148339.3664 | 65533.1035 | 194629.3775 | 15045 | 35105 | 33851.25 | 30090 | 17482.7945 | 8760 | 1482.4089 | 14631.3906 | 0 | 0 | 1342.3826 | 15509.1065 | 1556.806 | -1308.0388 | 1758.1937 | 2577.0605 | 8760 | 2359.3425 | 1107.5826 | 1251.7599 | 2362.3049 | 20758.9881 | 5024.8683 | 5486.0978 | 3251.6445 | 0 | 12799.1613 | 8760 | 0 | 133.125 | 117.625 | 850.5 | 759282.0183 | 210834.9497 | 2842.5 | -31.5123
390 | C | SOK | TOU | CC | FP | HC | R10 | 3.2558 | 41 | 3.075 | 8760 | 169460.5512 | 0 | 145878.0305 | 65533.1035 | 194629.3775 | 15064.5 | 35150.5 | 33895.125 | 30129 | 18883.2863 | 8760 | 1482.4089 | 15154.008 | 0 | 0 | 1333.0094 | 15103.8569 | 1490.3314 | -1321.3625 | 1827.6768 | 2541.205 | 8760 | 2358.797 | 1056.4747 | 1302.3223 | 2362.3049 | 20758.9881 | 5033.2271 | 5487.2127 | 3252.6938 | 0 | 13352.3154 | 8760 | 0 | 137.975 | 113.1 | 850.5 | 759181.0216 | 210834.9497 | 2842.475 | -30.6143
391 | C | SOK | TOU | CC | FP | HC | R600 | 3.8366 | 16.5 | 0.413 | 8760 | 149636.3137 | 0 | 158495.1893 | 65533.1035 | 135297.3232 | 19396.5 | 45258.5 | 43642.125 | 38793 | 25798.5905 | 8760 | 1475.3019 | 8398.8181 | 0 | 0 | 1980.0426 | 12064.8455 | 3464.6174 | -1073.2834 | 847.7137 | 2485.247 | 8760 | 3061.2154 | 2465.1855 | 596.0299 | 3066.6602 | 12891.6972 | 5427.0851 | 7070.1053 | 4160.8615 | 0 | 6708.5712 | 8760 | 0 | 68.15 | 255.125 | 1048.625 | 972696.6437 | 189624.8638 | 2332.575 | -72.6467
392 | C | SOK | TOU | CC | FP | HC | R600 | 3.8366 | 16.5 | 0.825 | 8760 | 154007.2648 | 0 | 156015.1046 | 65533.1035 | 135297.3232 | 19420.5 | 45314.5 | 43696.125 | 38841 | 26211.5755 | 8760 | 1475.3019 | 8945.3345 | 0 | 0 | 1734.1229 | 11843.2113 | 3477.2134 | -1136.3345 | 827.3064 | 2435.3058 | 8760 | 3059.4467 | 2470.5846 | 588.8621 | 3066.6602 | 12891.6972 | 5499.3365 | 7063.9428 | 4158.538 | 0 | 7301.3433 | 8760 | 0 | 64.45 | 259.225 | 1048.625 | 972715.4645 | 189624.8638 | 2304.925 | -74.7026
393 | C | SOK | TOU | CC | FP | HC | R600 | 3.8366 | 16.5 | 1.238 | 8760 | 155413.3478 | 0 | 155316.9012 | 65533.1035 | 135297.3232 | 19465.5 | 45419.5 | 43797.375 | 38931 | 27253.8371 | 8760 | 1475.3019 | 9144.6009 | 0 | 0 | 1662.9273 | 11757.3665 | 3476.1328 | -1161.6571 | 829.0907 | 2413.4115 | 8760 | 3059.1654 | 2462.7006 | 596.4648 | 3066.6602 | 12891.6972 | 5522.2418 | 7062.7504 | 4159.0625 | 0 | 7519.9346 | 8760 | 0 | 62.775 | 261.65 | 1048.625 | 972707.9836 | 189624.8638 | 2303.175 | -74.8005
394 | C | SOK | TOU | CC | FP | HC | R600 | 3.8366 | 22.5 | 0.563 | 8760 | 150686.2479 | 0 | 153014.5547 | 65533.1035 | 135297.3232 | 19156.5 | 44698.5 | 43102.125 | 38313 | 21969.0257 | 8760 | 1475.3019 | 9880.5796 | 0 | 0 | 1736.493 | 11539.5764 | 3086.9443 | -1170.0857 | 1211.4607 | 2556.3935 | 8760 | 3060.5362 | 2205.4842 | 855.0519 | 3066.6602 | 12891.6972 | 5520.8861 | 7075.3735 | 4164.6507 | 0 | 8073.6868 | 8760 | 0 | 94.875 | 224.4 | 1048.625 | 972714.4699 | 189624.8638 | 2506.575 | -64.606
395 | C | SOK | TOU | CC | FP | HC | R600 | 3.8366 | 22.5 | 1.125 | 8760 | 155608.3462 | 0 | 149811.5182 | 65533.1035 | 135297.3232 | 19204.5 | 44810.5 | 43210.125 | 38409 | 22166.2204 | 8760 | 1475.3019 | 10578.7523 | 0 | 0 | 1562.1468 | 11234.4071 | 3004.0798 | -1235.5198 | 1292.5688 | 2510.016 | 8760 | 3060.8621 | 2134.9541 | 925.908 | 3066.6602 | 12891.6972 | 5593.5294 | 7079.2138 | 4167.5593 | 0 | 8814.7856 | 8760 | 0 | 97.25 | 222.825 | 1048.625 | 972650.0325 | 189624.8638 | 2478.8 | -59.3845
396 | C | SOK | TOU | CC | FP | HC | R600 | 3.8366 | 22.5 | 1.688 | 8760 | 156303.1983 | 0 | 148469.8577 | 65533.1035 | 135297.3232 | 19230 | 44870 | 43267.5 | 38460 | 21850.4414 | 8760 | 1475.3019 | 10839.7232 | 0 | 0 | 1535.8735 | 11069.1298 | 2956.2612 | -1255.261 | 1338.2809 | 2476.7617 | 8760 | 3061.1628 | 2097.4311 | 963.7317 | 3066.6602 | 12891.6972 | 5612.9924 | 7081.8939 | 4169.6597 | 0 | 9105.5366 | 8760 | 0 | 99.175 | 221.325 | 1048.625 | 972584.2731 | 189624.8638 | 2495.4 | -57.4943
397 | C | SOK | TOU | CC | FP | HC | R600 | 3.8366 | 29 | 0.725 | 8760 | 152680.768 | 0 | 148136.1299 | 65533.1035 | 135297.3232 | 19015.5 | 44369.5 | 42784.875 | 38031 | 22257.9237 | 8760 | 1475.3019 | 11051.5468 | 0 | 0 | 1573.7551 | 11027.6493 | 2824.4596 | -1242.1816 | 1477.9989 | 2593.1468 | 8760 | 3060.7822 | 2008.6329 | 1052.1493 | 3066.6602 | 12891.6972 | 5591.0579 | 7066.5355 | 4165.0803 | 0 | 9170.5343 | 8760 | 0 | 112.875 | 204.05 | 1048.625 | 972690.6158 | 189624.8638 | 2664.05 | -78.1199
398 | C | SOK | TOU | CC | FP | HC | R600 | 3.8366 | 29 | 1.45 | 8760 | 156952.8059 | 0 | 144546.8692 | 65533.1035 | 135297.3232 | 19035 | 44415 | 42828.75 | 38070 | 22218.4003 | 8760 | 1475.3019 | 11878.7811 | 0 | 0 | 1452.6734 | 10639.2882 | 2610.2241 | -1301.2448 | 1670.635 | 2536.5356 | 8760 | 3061.2161 | 1857.019 | 1204.197 | 3066.6602 | 12891.6972 | 5655.5455 | 7081.3758 | 4171.1341 | 0 | 10050.3304 | 8760 | 0 | 123.05 | 194.2 | 1048.625 | 972696.5781 | 189624.8638 | 2657.325 | -59.3823
399 | C | SOK | TOU | CC | FP | HC | R600 | 3.8366 | 29 | 2.175 | 8760 | 158272.2816 | 0 | 142668.9945 | 65533.1035 | 135297.3232 | 19063.5 | 44481.5 | 42892.875 | 38127 | 22256.8617 | 8760 | 1475.3019 | 12262.3235 | 0 | 0 | 1429.4441 | 10399.1353 | 2541.9695 | -1319.0184 | 1743.5521 | 2497.9152 | 8760 | 3061.4138 | 1799.6924 | 1261.7214 | 3066.6602 | 12891.6972 | 5671.7774 | 7088.1628 | 4172.3528 | 0 | 10466.1579 | 8760 | 0 | 127.125 | 190.6 | 1048.625 | 972754.9715 | 189624.8638 | 2663.6 | -53.1
400 | C | SOK | TOU | CC | FP | HC | R60 | 3.8366 | 35 | 0.875 | 8760 | 155750.1615 | 0 | 144269.3878 | 65533.1035 | 135297.3232 | 18861 | 44009 | 42437.25 | 37722 | 20011.3906 | 8760 | 1475.3019 | 11912.6744 | 0 | 0 | 1466.2293 | 10594.3701 | 2556.6075 | -1288.5897 | 1719.3721 | 2607.6447 | 8760 | 3062.4988 | 1838.4429 | 1224.0559 | 3066.6602 | 12891.6972 | 5635.6619 | 7097.9191 | 4173.0905 | 0 | 9992.4267 | 8760 | 0 | 129.9 | 184.45 | 1048.625 | 972751.1701 | 189624.8638 | 2787.475 | -45.6416
401 | C | SOK | TOU | CC | FP | HC | R60 | 3.8366 | 35 | 1.75 | 8760 | 159847.3204 | 0 | 140528.6372 | 65533.1035 | 135297.3232 | 18871.5 | 44033.5 | 42460.875 | 37743 | 20174.01 | 8760 | 1475.3019 | 12822.0809 | 0 | 0 | 1366.0058 | 10133.5031 | 2343.6516 | -1343.5416 | 1926.0442 | 2541.5072 | 8760 | 3062.3587 | 1677.4777 | 1384.881 | 3066.6602 | 12891.6972 | 5692.7264 | 7098.9775 | 4176.7438 | 0 | 10960.8938 | 8760 | 0 | 141.425 | 173.1 | 1048.625 | 972688.5937 | 189624.8638 | 2784.95 | -42.5129
402 | C | SOK | TOU | CC | FP | HC | R60 | 3.8366 | 35 | 2.625 | 8760 | 161499.108 | 0 | 138164.0448 | 65533.1035 | 135297.3232 | 18871.5 | 44033.5 | 42460.875 | 37743 | 21229.7856 | 8760 | 1475.3019 | 13314.4862 | 0 | 0 | 1348.76 | 9870.0244 | 2214.5043 | -1362.5498 | 2051.6899 | 2505.9922 | 8760 | 3062.7557 | 1581.3604 | 1481.3953 | 3066.6602 | 12891.6972 | 5710.9681 | 7099.952 | 4177.8906 | 0 | 11483.0247 | 8760 | 0 | 149.45 | 165.075 | 1048.625 | 972737.1458 | 189624.8638 | 2790.75 | -42.5148
403 | C | SOK | TOU | CC | FP | HC | R60 | 3.8366 | 41 | 1.025 | 8760 | 160828.7224 | 0 | 141241.0897 | 65533.1035 | 135297.3232 | 18756 | 43764 | 42201 | 37512 | 20354.5473 | 8760 | 1475.3019 | 12731.5333 | 0 | 0 | 1382.0696 | 10195.9853 | 2368.3921 | -1323.6322 | 1905.0885 | 2605.5687 | 8760 | 3063.0749 | 1703.8949 | 1359.18 | 3066.6602 | 12891.6972 | 5669.9121 | 7098.2879 | 4174.652 | 0 | 10790.6269 | 8760 | 0 | 142.7 | 169.9 | 1048.625 | 972818.5025 | 189624.8638 | 2885 | -46.7892
404 | C | SOK | TOU | CC | FP | HC | R60 | 3.8366 | 41 | 2.05 | 8760 | 164392.0577 | 0 | 136770.6377 | 65533.1035 | 135297.3232 | 18727.5 | 43697.5 | 42136.875 | 37455 | 20395.8096 | 8760 | 1475.3019 | 13740.7525 | 0 | 0 | 1290.7751 | 9670.6266 | 2096.6436 | -1375.1452 | 2163.0829 | 2540.4853 | 8760 | 3063.5312 | 1504.6474 | 1558.8838 | 3066.6602 | 12891.6972 | 5718.7776 | 7104.0749 | 4179.5669 | 0 | 11857.5819 | 8760 | 0 | 157.175 | 154.95 | 1048.625 | 972798.9978 | 189624.8638 | 2893.6 | -40.873
405 | C | SOK | TOU | CC | FP | HC | R60 | 3.8366 | 41 | 3.075 | 8760 | 166327.4349 | 0 | 134386.5467 | 65533.1035 | 135297.3232 | 18742.5 | 43732.5 | 42170.625 | 37485 | 20018.8115 | 8760 | 1475.3019 | 14231.3891 | 0 | 0 | 1254.1549 | 9402.1173 | 1931.9523 | -1393.3876 | 2307.6709 | 2505.6985 | 8760 | 3062.681 | 1393.0955 | 1669.5855 | 3066.6602 | 12891.6972 | 5733.9576 | 7105.6567 | 4181.1284 | 0 | 12379.0497 | 8760 | 0 | 166.35 | 146.025 | 1048.625 | 972663.4183 | 189624.8638 | 2892.025 | -37.3476
406 | C | SOK | TOU | FC | ET | HC | OFF0 | 0.24797 | 11.5 | 0.288 | 8760 | 145799.7447 | 0 | 133157.3786 | 0 | 75581.8652 | 32100 | 74900 | 72225 | 64200 | 61027.5227 | 8760 | 1475.304 | 7444.5364 | 0 | 0 | 0 | 2001.6592 | 3585.3643 | -1336.4781 | 2542.9861 | 3283.2477 | 8760 | 3865.6405 | 2188.95 | 1676.6905 | 3864.5241 | 2588.0754 | 0 | 9567.7616 | 5932.3097 | 0 | 5083.8428 | 8760 | 0 | 208.85 | 326.15 | 1821 | 1379254.4124 | 155421.1442 | 2115.15 | -88.255
407 | C | SOK | TOU | FC | ET | HC | OFF0 | 0.24797 | 11.5 | 0.575 | 8760 | 149138.3434 | 0 | 130033.0869 | 0 | 75581.8652 | 32073 | 74837 | 72164.25 | 64146 | 57537.252 | 8760 | 1475.304 | 7674.1038 | 0 | 0 | 0 | 1883.8631 | 3497.3045 | -1372.8698 | 2628.2244 | 3272.8405 | 8760 | 3864.6825 | 2132.6018 | 1732.0806 | 3864.5241 | 2588.0754 | 0 | 9563.6747 | 5931.1926 | 0 | 5327.3558 | 8760 | 0 | 216.525 | 318.025 | 1821 | 1379608.2467 | 155421.1442 | 2071.125 | -86.2205
408 | C | SOK | TOU | FC | ET | HC | OFF0 | 0.24797 | 11.5 | 0.863 | 8760 | 150846.9555 | 0 | 127875.4808 | 0 | 75581.8652 | 32077.5 | 74847.5 | 72174.375 | 64155 | 57368.9925 | 8760 | 1475.304 | 7797.4843 | 0 | 0 | 0 | 1820.1828 | 3437.5046 | -1382.0903 | 2684.0101 | 3262.6605 | 8760 | 3864.7899 | 2094.2583 | 1770.5316 | 3864.5241 | 2588.0754 | 0 | 9561.1113 | 5931.3558 | 0 | 5462.4984 | 8760 | 0 | 221.325 | 313.3 | 1821 | 1379735.5261 | 155421.1442 | 2049.5 | -88.4223
409 | C | SOK | TOU | FC | ET | HC | OFF0 | 0.24797 | 15.5 | 0.388 | 8760 | 141241.13 | 0 | 122486.3401 | 0 | 75581.8652 | 31096.5 | 72558.5 | 69967.125 | 62193 | 49970.0911 | 8760 | 1475.304 | 8924.0322 | 0 | 0 | 0 | 1685.4654 | 2651.7436 | -1412.8721 | 3425.5529 | 3393.4985 | 8760 | 3865.6491 | 1610.9342 | 2254.7149 | 3864.5241 | 2588.0754 | 0 | 9565.5751 | 5922.2277 | 0 | 6418.8484 | 8760 | 0 | 277.05 | 241.225 | 1821 | 1379361.6842 | 155421.1442 | 2298.275 | -67.1506
410 | C | SOK | TOU | FC | ET | HC | OFF0 | 0.24797 | 15.5 | 0.775 | 8760 | 145952.3714 | 0 | 117493.9229 | 0 | 75581.8652 | 30922.5 | 72152.5 | 69575.625 | 61845 | 48982.255 | 8760 | 1475.304 | 9317.5576 | 0 | 0 | 0 | 1527.3599 | 2446.5673 | -1447.7883 | 3615.1542 | 3386.2561 | 8760 | 3865.2285 | 1483.8996 | 2381.3289 | 3864.5241 | 2588.0754 | 0 | 9555.8997 | 5919.4338 | 0 | 6824.604 | 8760 | 0 | 292.05 | 223.325 | 1821 | 1379339.8422 | 155421.1442 | 2238.575 | -66.3203
411 | C | SOK | TOU | FC | ET | HC | OFF0 | 0.24797 | 15.5 | 1.163 | 8760 | 147912.498 | 0 | 116291.7531 | 0 | 75581.8652 | 30865.5 | 72019.5 | 69447.375 | 61731 | 49074.6571 | 8760 | 1475.304 | 9478.5525 | 0 | 0 | 0 | 1488.0586 | 2354.6461 | -1463.1247 | 3700.0196 | 3386.0986 | 8760 | 3864.8487 | 1429.3575 | 2435.4912 | 3864.5241 | 2588.0754 | 0 | 9553.8195 | 5918.2055 | 0 | 6985.9672 | 8760 | 0 | 299.8 | 214.625 | 1821 | 1379152.0707 | 155421.1442 | 2214.025 | -65.1467
412 | C | SOK | TOU | FC | ET | HC | OFF0 | 0.24797 | 20 | 0.5 | 8760 | 136840.535 | 0 | 113432.9437 | 0 | 75581.8652 | 30199.5 | 70465.5 | 67948.875 | 60399 | 36694.9657 | 8760 | 1475.304 | 10173.1314 | 0 | 0 | 0 | 1401.8549 | 1912.6538 | -1470.9727 | 4123.6314 | 3465.271 | 8760 | 3864.7946 | 1155.2164 | 2709.5782 | 3864.5241 | 2588.0754 | 0 | 9567.0052 | 5912.0848 | 0 | 7562.0789 | 8760 | 0 | 330.5 | 172.825 | 1821 | 1379005.298 | 155421.1442 | 2484.85 | -37.7016
413 | C | SOK | TOU | FC | ET | HC | OFF0 | 0.24797 | 20 | 1 | 8760 | 141897.7689 | 0 | 108391.0298 | 0 | 75581.8652 | 29979 | 69951 | 67452.75 | 59958 | 35107.1417 | 8760 | 1475.304 | 10650.2604 | 0 | 0 | 0 | 1237.83 | 1649.7664 | -1510.6386 | 4365.7599 | 3469.5297 | 8760 | 3865.514 | 996.046 | 2869.468 | 3864.5241 | 2588.0754 | 0 | 9562.846 | 5910.7024 | 0 | 8037.4171 | 8760 | 0 | 349.825 | 149.825 | 1821 | 1379352.6542 | 155421.1442 | 2421.55 | -33.1131
414 | C | SOK | TOU | FC | ET | HC | OFF0 | 0.24797 | 20 | 1.5 | 8760 | 144248.6761 | 0 | 106592.6497 | 0 | 75581.8652 | 29926.5 | 69828.5 | 67334.625 | 59853 | 31688.3847 | 8760 | 1475.304 | 10874.0554 | 0 | 0 | 0 | 1168.1208 | 1512.5469 | -1525.5681 | 4493.2359 | 3467.259 | 8760 | 3865.6311 | 912.1231 | 2953.508 | 3864.5241 | 2588.0754 | 0 | 9564.2913 | 5912.4846 | 0 | 8265.3831 | 8760 | 0 | 360.425 | 138.35 | 1821 | 1379215.0942 | 155421.1442 | 2393.4 | -28.2835
415 | C | SOK | TOU | FC | ET | HC | OFF | 0.24797 | 24 | 0.6 | 8760 | 133831.7828 | 0 | 107609.5819 | 0 | 75581.8652 | 29907 | 69783 | 67290.75 | 59814 | 31678.3658 | 8760 | 1475.304 | 11040.5793 | 0 | 0 | 0 | 1174.8373 | 1574.5041 | -1508.1233 | 4489.7844 | 3500.7397 | 8760 | 3865.7741 | 917.2562 | 2948.5179 | 3864.5241 | 2588.0754 | 0 | 9567.9475 | 5911.2717 | 0 | 8366.9362 | 8760 | 0 | 359.875 | 138.575 | 1821 | 1379161.3916 | 155421.1442 | 2630.525 | -32.128
416 | C | SOK | TOU | FC | ET | HC | OFF | 0.24797 | 24 | 1.2 | 8760 | 138515.9345 | 0 | 102197.9427 | 0 | 75581.8652 | 29578.5 | 69016.5 | 66551.625 | 59157 | 29222.1884 | 8760 | 1475.304 | 11504.3409 | 0 | 0 | 0 | 1004.6059 | 1251.7654 | -1551.1963 | 4763.2322 | 3505.3225 | 8760 | 3865.2948 | 734.733 | 3130.5618 | 3864.5241 | 2588.0754 | 0 | 9560.2668 | 5907.7886 | 0 | 8828.1077 | 8760 | 0 | 380.475 | 112.5 | 1821 | 1378961.9377 | 155421.1442 | 2571.025 | -28.2634
417 | C | SOK | TOU | FC | ET | HC | OFF | 0.24797 | 24 | 1.8 | 8760 | 140319.4195 | 0 | 100223.3244 | 0 | 75581.8652 | 29401.5 | 68603.5 | 66153.375 | 58803 | 25336.9624 | 8760 | 1475.304 | 11684.2374 | 0 | 0 | 0 | 937.1327 | 1082.2554 | -1564.6657 | 4904.2047 | 3505.6468 | 8760 | 3865.6204 | 645.3397 | 3220.2807 | 3864.5241 | 2588.0754 | 0 | 9558.957 | 5907.9501 | 0 | 9009.1831 | 8760 | 0 | 391.925 | 98.1 | 1821 | 1378838.2874 | 155421.1442 | 2548.325 | -23.2764
418 | C | SOK | TOU | FC | ET | HC | OFF | 0.24797 | 28.5 | 0.713 | 8760 | 129801.256 | 0 | 101743.473 | 0 | 75581.8652 | 29424 | 68656 | 66204 | 58848 | 31595.7743 | 8760 | 1475.304 | 11597.2383 | 0 | 0 | 0 | 946.6982 | 1236.6287 | -1547.069 | 4808.5535 | 3527.9466 | 8760 | 3865.7992 | 703.3698 | 3162.4294 | 3864.5241 | 2588.0754 | 0 | 9531.1732 | 5898.5751 | 0 | 8873.6553 | 8760 | 0 | 382.675 | 107.725 | 1821 | 1379299.5815 | 155421.1442 | 2785.225 | -64.3027
419 | C | SOK | TOU | FC | ET | HC | OFF | 0.24797 | 28.5 | 1.425 | 8760 | 134584.1585 | 0 | 95561.6352 | 0 | 75581.8652 | 29020.5 | 67714.5 | 65296.125 | 58041 | 26277.0245 | 8760 | 1475.304 | 12115.445 | 0 | 0 | 0 | 757.6635 | 896.0919 | -1589.8095 | 5096.5505 | 3533.3897 | 8760 | 3864.6063 | 514.4552 | 3350.151 | 3864.5241 | 2588.0754 | 0 | 9528.6347 | 5895.4129 | 0 | 9388.5354 | 8760 | 0 | 404.55 | 79.125 | 1821 | 1378640.9971 | 155421.1442 | 2726.9 | -53.3253
420 | C | SOK | TOU | FC | ET | HC | OFF | 0.24797 | 28.5 | 2.138 | 8760 | 136132.9933 | 0 | 93065.0516 | 0 | 75581.8652 | 28864.5 | 67350.5 | 64945.125 | 57729 | 19808.4518 | 8760 | 1475.304 | 12287.312 | 0 | 0 | 0 | 670.3401 | 739.4604 | -1599.2084 | 5226.2508 | 3530.8475 | 8760 | 3865.7819 | 439.5236 | 3426.2583 | 3864.5241 | 2588.0754 | 0 | 9547.2337 | 5898.9488 | 0 | 9562.3229 | 8760 | 0 | 416.675 | 64.4 | 1821 | 1379112.2764 | 155421.1442 | 2707.2 | -25.2755
421 | C | SOK | TOU | FC | ET | HC | R100 | 2.1548 | 11.5 | 0.288 | 8760 | 144861.3721 | 0 | 172346.7658 | 65533.1035 | 159043.7645 | 14661 | 34209 | 32987.25 | 29322 | 37319.6596 | 8760 | 1482.4089 | 7603.6419 | 0 | 0 | 1384.8956 | 12693.5344 | 2113.3809 | -1048.0667 | 674.1633 | 2899.1949 | 8760 | 1717.5594 | 1297.3961 | 420.1633 | 1717.6274 | 13739.0387 | 3520.863 | 4178.2064 | 2643.4937 | 0 | 5576.4738 | 8760 | 0 | 61.975 | 182.375 | 1024.225 | 611213.1019 | 210834.9497 | 2119.3 | -109.367
422 | C | SOK | TOU | FC | ET | HC | R100 | 2.1548 | 11.5 | 0.575 | 8760 | 152018.8181 | 0 | 169690.4429 | 65533.1035 | 159043.7645 | 14719.5 | 34345.5 | 33118.875 | 29439 | 33381.098 | 8760 | 1482.4089 | 8057.4608 | 0 | 0 | 1245.7405 | 12490.4997 | 2090.2004 | -1112.8132 | 694.3205 | 2868.8208 | 8760 | 1718.1628 | 1279.078 | 439.0848 | 1717.6274 | 13739.0387 | 3545.6525 | 4185.7345 | 2650.4672 | 0 | 6053.4832 | 8760 | 0 | 62.125 | 183.2 | 1024.225 | 610836.7034 | 210834.9497 | 2021.425 | -110.8824
423 | C | SOK | TOU | FC | ET | HC | R100 | 2.1548 | 11.5 | 0.863 | 8760 | 154584.7563 | 0 | 168488.273 | 65533.1035 | 159043.7645 | 14667 | 34223 | 33000.75 | 29334 | 32234.4593 | 8760 | 1482.4089 | 8220.3574 | 0 | 0 | 1224.3033 | 12395.6642 | 2028.1226 | -1125.3591 | 742.9517 | 2849.7312 | 8760 | 1717.615 | 1243.6802 | 473.9347 | 1717.6274 | 13739.0387 | 3549.4186 | 4186.5194 | 2648.8327 | 0 | 6237.0878 | 8760 | 0 | 65.6 | 178.85 | 1024.225 | 611177.9835 | 210834.9497 | 1988.925 | -105.784
424 | C | SOK | TOU | FC | ET | HC | R100 | 2.1548 | 15.5 | 0.388 | 8760 | 139640.6173 | 0 | 164860.0149 | 65533.1035 | 159043.7645 | 14272.5 | 33302.5 | 32113.125 | 28545 | 29419.7799 | 8760 | 1482.4089 | 9110.1464 | 0 | 0 | 1244.718 | 12051.7684 | 1747.9975 | -1140.8702 | 1012.5725 | 3046.441 | 8760 | 1717.1731 | 1081.991 | 635.1821 | 1717.6274 | 13739.0387 | 3551.5147 | 4183.8479 | 2640.8495 | 0 | 6862.5773 | 8760 | 0 | 90.075 | 147.8 | 1024.225 | 610855.4757 | 210834.9497 | 2307.025 | -91.6114
425 | C | SOK | TOU | FC | ET | HC | R100 | 2.1548 | 15.5 | 0.775 | 8760 | 147065.3613 | 0 | 161913.4614 | 65533.1035 | 159043.7645 | 14275.5 | 33309.5 | 32119.875 | 28551 | 27066.1552 | 8760 | 1482.4089 | 9699.9795 | 0 | 0 | 1131.929 | 11768.2724 | 1645.7714 | -1198.5736 | 1097.3774 | 3026.4882 | 8760 | 1717.6095 | 1016.1731 | 701.4364 | 1717.6274 | 13739.0387 | 3572.8231 | 4188.2511 | 2643.7195 | 0 | 7464.835 | 8760 | 0 | 94.675 | 143.25 | 1024.225 | 611246.0597 | 210834.9497 | 2208.125 | -88.5804
426 | C | SOK | TOU | FC | ET | HC | R100 | 2.1548 | 15.5 | 1.163 | 8760 | 150410.514 | 0 | 160285.3199 | 65533.1035 | 159043.7645 | 14284.5 | 33330.5 | 32140.125 | 28569 | 27111.1344 | 8760 | 1482.4089 | 9950.5711 | 0 | 0 | 1099.1093 | 11657.5939 | 1541.4237 | -1212.3462 | 1191.9011 | 3009.8098 | 8760 | 1718.6206 | 950.5653 | 768.0553 | 1717.6274 | 13739.0387 | 3574.0031 | 4194.0955 | 2648.1384 | 0 | 7733.447 | 8760 | 0 | 101.75 | 136.325 | 1024.225 | 611198.9139 | 210834.9497 | 2164.3 | -84.8664
427 | C | SOK | TOU | FC | ET | HC | R100 | 2.1548 | 20 | 0.5 | 8760 | 135830.8863 | 0 | 158427.6938 | 65533.1035 | 159043.7645 | 13968 | 32592 | 31428 | 27936 | 21035.3935 | 8760 | 1482.4089 | 10485.8801 | 0 | 0 | 1132.9304 | 11386.1943 | 1437.7049 | -1207.0388 | 1297.754 | 3140.5298 | 8760 | 1718.0055 | 900.5732 | 817.4323 | 1717.6274 | 13739.0387 | 3570.6452 | 4198.1705 | 2641.0576 | 0 | 8077.1555 | 8760 | 0 | 113.5 | 119.3 | 1024.225 | 610942.6079 | 210834.9497 | 2480.65 | -66.9843
428 | C | SOK | TOU | FC | ET | HC | R100 | 2.1548 | 20 | 1 | 8760 | 143750.0513 | 0 | 154423.7107 | 65533.1035 | 159043.7645 | 13963.5 | 32581.5 | 31417.875 | 27927 | 19158.1055 | 8760 | 1482.4089 | 11217.4881 | 0 | 0 | 1029.7138 | 11033.992 | 1286.0403 | -1265.1874 | 1437.1092 | 3129.7887 | 8760 | 1717.7227 | 798.8061 | 918.9166 | 1717.6274 | 13739.0387 | 3595.5253 | 4202.49 | 2644.0336 | 0 | 8811.4194 | 8760 | 0 | 122.55 | 110.175 | 1024.225 | 610827.2508 | 210834.9497 | 2377.8 | -59.9006
429 | C | SOK | TOU | FC | ET | HC | R100 | 2.1548 | 20 | 1.5 | 8760 | 146897.7526 | 0 | 152512.0882 | 65533.1035 | 159043.7645 | 13929 | 32501 | 31340.25 | 27858 | 17875.9633 | 8760 | 1482.4089 | 11492.3343 | 0 | 0 | 1010.5636 | 10866.7671 | 1201.9552 | -1277.088 | 1508.2844 | 3113.702 | 8760 | 1717.7995 | 749.7545 | 968.0451 | 1717.6274 | 13739.0387 | 3599.2555 | 4204.688 | 2645.605 | 0 | 9100.6659 | 8760 | 0 | 127.8 | 104.35 | 1024.225 | 610990.1625 | 210834.9497 | 2336.55 | -55.797
430 | C | SOK | TOU | FC | ET | HC | R10 | 2.1548 | 24 | 0.6 | 8760 | 134129.6598 | 0 | 153549.269 | 65533.1035 | 159043.7645 | 13878 | 32382 | 31225.5 | 27756 | 18194.9731 | 8760 | 1482.4089 | 11548.3427 | 0 | 0 | 1053.0332 | 10854.2815 | 1276.7268 | -1252.0637 | 1464.8414 | 3193.426 | 8760 | 1718.4967 | 791.4044 | 927.0923 | 1717.6274 | 13739.0387 | 3585.7962 | 4201.9088 | 2640.2518 | 0 | 9040.1139 | 8760 | 0 | 127.3 | 104 | 1024.225 | 611178.0961 | 210834.9497 | 2606.375 | -58.3948
431 | C | SOK | TOU | FC | ET | HC | R10 | 2.1548 | 24 | 1.2 | 8760 | 141516.0345 | 0 | 148683.5934 | 65533.1035 | 159043.7645 | 13818 | 32242 | 31090.5 | 27636 | 17969.1072 | 8760 | 1482.4089 | 12307.8157 | 0 | 0 | 973.0934 | 10448.4436 | 1106.8756 | -1304.3525 | 1607.165 | 3177.748 | 8760 | 1718.4259 | 689.0886 | 1029.3373 | 1717.6274 | 13739.0387 | 3610.6611 | 4203.7264 | 2641.9909 | 0 | 9800.1545 | 8760 | 0 | 137 | 93.3 | 1024.225 | 611162.1632 | 210834.9497 | 2512.925 | -52.3482
432 | C | SOK | TOU | FC | ET | HC | R10 | 2.1548 | 24 | 1.8 | 8760 | 144669.8966 | 0 | 146813.2182 | 65533.1035 | 159043.7645 | 13753.5 | 32091.5 | 30945.375 | 27507 | 16145.3397 | 8760 | 1482.4089 | 12623.2685 | 0 | 0 | 963.7043 | 10240.175 | 1000.1156 | -1319.6268 | 1700.6744 | 3169.5401 | 8760 | 1717.8354 | 625.4192 | 1092.4162 | 1717.6274 | 13739.0387 | 3613.8938 | 4209.2808 | 2643.5151 | 0 | 10124.6869 | 8760 | 0 | 143.825 | 85.4 | 1024.225 | 610959.9752 | 210834.9497 | 2474.575 | -44.2016
433 | C | SOK | TOU | FC | ET | HC | R10 | 2.1548 | 28.5 | 0.713 | 8760 | 132004.3528 | 0 | 148596.5992 | 65533.1035 | 159043.7645 | 13581 | 31689 | 30557.25 | 27162 | 22570.9657 | 8760 | 1482.4089 | 12404.5647 | 0 | 0 | 989.8676 | 10288.2587 | 1141.2725 | -1288.0656 | 1586.5044 | 3225.0729 | 8760 | 1718.3327 | 705.4994 | 1012.8333 | 1717.6274 | 13739.0387 | 3600.222 | 4167.7357 | 2629.9682 | 0 | 9827.7956 | 8760 | 0 | 135.275 | 91.075 | 1024.225 | 611130.9634 | 210834.9497 | 2737.65 | -95.5841
434 | C | SOK | TOU | FC | ET | HC | R10 | 2.1548 | 28.5 | 1.425 | 8760 | 138935.6194 | 0 | 143535.9367 | 65533.1035 | 159043.7645 | 13512 | 31528 | 30402 | 27024 | 20390.4728 | 8760 | 1482.4089 | 13189.0474 | 0 | 0 | 914.1193 | 9860.1583 | 951.053 | -1338.4557 | 1756.743 | 3207.2581 | 8760 | 1717.806 | 584.6504 | 1133.1557 | 1717.6274 | 13739.0387 | 3620.1055 | 4174.9063 | 2632.7581 | 0 | 10609.0838 | 8760 | 0 | 146.7 | 78.5 | 1024.225 | 611128.6341 | 210834.9497 | 2655.8 | -87.096
435 | C | SOK | TOU | FC | ET | HC | R10 | 2.1548 | 28.5 | 2.138 | 8760 | 142571.724 | 0 | 141384.3301 | 65533.1035 | 159043.7645 | 13537.5 | 31587.5 | 30459.375 | 27075 | 16927.1894 | 8760 | 1482.4089 | 13582.0586 | 0 | 0 | 904.3321 | 9608.5101 | 843.2431 | -1350.7148 | 1844.6087 | 3201.4117 | 8760 | 1717.5982 | 529.881 | 1187.7173 | 1717.6274 | 13739.0387 | 3622.5223 | 4191.5758 | 2635.8317 | 0 | 11004.7363 | 8760 | 0 | 155.225 | 70.4 | 1024.225 | 610857.8403 | 210834.9497 | 2612.225 | -62.6639
436 | C | SOK | TOU | FC | ET | HC | R600 | 2.4559 | 11.5 | 0.288 | 8760 | 145396.058 | 0 | 156335.3333 | 65533.1035 | 111858.2722 | 17280 | 40320 | 38880 | 34560 | 37925.8913 | 8760 | 1475.3019 | 7556.4684 | 0 | 0 | 1352.172 | 7731.3799 | 2615.3118 | -1102.2386 | 739.6868 | 2869.29 | 8760 | 2104.8871 | 1641.6135 | 463.2737 | 2105.0158 | 8252.2271 | 3919.8083 | 5128.5508 | 3202.3764 | 0 | 5467.4058 | 8760 | 0 | 67.475 | 220.525 | 1166.025 | 740679.0944 | 189624.8638 | 2114.025 | -108.743
437 | C | SOK | TOU | FC | ET | HC | R600 | 2.4559 | 11.5 | 0.575 | 8760 | 152510.9031 | 0 | 154437.2098 | 65533.1035 | 111858.2722 | 17355 | 40495 | 39048.75 | 34710 | 33234.3592 | 8760 | 1475.3019 | 8007.2598 | 0 | 0 | 1174.2646 | 7632.2791 | 2588.9031 | -1173.8274 | 767.761 | 2858.7282 | 8760 | 2105.16 | 1615.5851 | 489.5749 | 2105.0158 | 8252.2271 | 3969.1778 | 5131.55 | 3206.7586 | 0 | 5915.5087 | 8760 | 0 | 67.875 | 221.375 | 1166.025 | 740592.5266 | 189624.8638 | 2016.8 | -110.1155
438 | C | SOK | TOU | FC | ET | HC | R600 | 2.4559 | 11.5 | 0.863 | 8760 | 155025.1607 | 0 | 154035.2366 | 65533.1035 | 111858.2722 | 17400 | 40600 | 39150 | 34800 | 32445.4362 | 8760 | 1475.3019 | 8163.8725 | 0 | 0 | 1142.7842 | 7589.574 | 2563.6415 | -1199.8558 | 791.2602 | 2863.9903 | 8760 | 2105.1169 | 1595.9236 | 509.1932 | 2105.0158 | 8252.2271 | 3983.8482 | 5130.0476 | 3208.8186 | 0 | 6069.3761 | 8760 | 0 | 69.025 | 220.975 | 1166.025 | 740570.5429 | 189624.8638 | 1985.025 | -110.9515
439 | C | SOK | TOU | FC | ET | HC | R600 | 2.4559 | 15.5 | 0.388 | 8760 | 139561.5192 | 0 | 149696.0259 | 65533.1035 | 111858.2722 | 16822.5 | 39252.5 | 37850.625 | 33645 | 29434.4984 | 8760 | 1475.3019 | 8990.8556 | 0 | 0 | 1170.7414 | 7305.4298 | 2192.1844 | -1206.2087 | 1133.3086 | 3031.8113 | 8760 | 2105.6628 | 1390.5108 | 715.152 | 2105.0158 | 8252.2271 | 3976.0545 | 5132.7954 | 3198.8658 | 0 | 6665.5821 | 8760 | 0 | 99.475 | 180.9 | 1166.025 | 740351.7216 | 189624.8638 | 2310.875 | -91.4161
440 | C | SOK | TOU | FC | ET | HC | R600 | 2.4559 | 15.5 | 0.775 | 8760 | 146616.6374 | 0 | 147232.4402 | 65533.1035 | 111858.2722 | 16872 | 39368 | 37962 | 33744 | 26707.7589 | 8760 | 1475.3019 | 9535.0097 | 0 | 0 | 1072.9622 | 7156.1647 | 2070.804 | -1274.1972 | 1244.1543 | 3037.2841 | 8760 | 2106.0219 | 1304.8059 | 801.2159 | 2105.0158 | 8252.2271 | 4019.9354 | 5135.2979 | 3202.5033 | 0 | 7191.4595 | 8760 | 0 | 105.9 | 175.3 | 1166.025 | 740486.058 | 189624.8638 | 2217.275 | -88.5586
441 | C | SOK | TOU | FC | ET | HC | R600 | 2.4559 | 15.5 | 1.163 | 8760 | 149713.5549 | 0 | 145993.5228 | 65533.1035 | 111858.2722 | 16867.5 | 39357.5 | 37951.875 | 33735 | 26198.1092 | 8760 | 1475.3019 | 9767.433 | 0 | 0 | 1050.9906 | 7077.9049 | 1976.7683 | -1295.6809 | 1330.1695 | 3041.3491 | 8760 | 2105.3707 | 1239.9628 | 865.4079 | 2105.0158 | 8252.2271 | 4027.5244 | 5136.1211 | 3204.1655 | 0 | 7420.171 | 8760 | 0 | 110.85 | 170.275 | 1166.025 | 740419.1976 | 189624.8638 | 2176.725 | -84.1279
442 | C | SOK | TOU | FC | ET | HC | R600 | 2.4559 | 20 | 0.5 | 8760 | 134842.9776 | 0 | 143580.1837 | 65533.1035 | 111858.2722 | 16464 | 38416 | 37044 | 32928 | 20157.8209 | 8760 | 1475.3019 | 10234.6671 | 0 | 0 | 1056.8426 | 6866.7562 | 1827.6777 | -1280.4402 | 1472.8816 | 3133.0711 | 8760 | 2105.5645 | 1169.9259 | 935.6386 | 2105.0158 | 8252.2271 | 4011.7828 | 5143.1293 | 3196.76 | 0 | 7743.1836 | 8760 | 0 | 126.35 | 148.05 | 1166.025 | 740478.1256 | 189624.8638 | 2494.875 | -65.9925
443 | C | SOK | TOU | FC | ET | HC | R600 | 2.4559 | 20 | 1 | 8760 | 141889.9545 | 0 | 140322.4009 | 65533.1035 | 111858.2722 | 16453.5 | 38391.5 | 37020.375 | 32907 | 17778.2072 | 8760 | 1475.3019 | 10879.7994 | 0 | 0 | 978.3412 | 6652.6294 | 1625.381 | -1335.4828 | 1659.5438 | 3132.7404 | 8760 | 2105.2868 | 1031.0956 | 1074.1912 | 2105.0158 | 8252.2271 | 4043.092 | 5144.3177 | 3199.2727 | 0 | 8372.1784 | 8760 | 0 | 137.975 | 136.25 | 1166.025 | 740493.9454 | 189624.8638 | 2404.975 | -59.6685
444 | C | SOK | TOU | FC | ET | HC | R600 | 2.4559 | 20 | 1.5 | 8760 | 145255.4968 | 0 | 138829.2505 | 65533.1035 | 111858.2722 | 16464 | 38416 | 37044 | 32928 | 17981.3387 | 8760 | 1475.3019 | 11176.4672 | 0 | 0 | 959.9466 | 6529.0634 | 1513.6382 | -1352.9786 | 1768.0802 | 3133.0737 | 8760 | 2105.7127 | 955.8885 | 1149.8242 | 2105.0158 | 8252.2271 | 4051.0015 | 5147.0961 | 3202.4484 | 0 | 8668.6105 | 8760 | 0 | 146.025 | 128.375 | 1166.025 | 740620.4786 | 189624.8638 | 2361.35 | -57.252
445 | C | SOK | TOU | FC | ET | HC | R60 | 2.4559 | 24 | 0.6 | 8760 | 132307.4688 | 0 | 138967.2413 | 65533.1035 | 111858.2722 | 16336.5 | 38118.5 | 36757.125 | 32673 | 18769.5833 | 8760 | 1475.3019 | 11170.825 | 0 | 0 | 979.4955 | 6499.0205 | 1624.1303 | -1324.8395 | 1673.4901 | 3177.4716 | 8760 | 2105.5615 | 1035.9815 | 1069.58 | 2105.0158 | 8252.2271 | 4031.9262 | 5144.0009 | 3195.0134 | 0 | 8586.5322 | 8760 | 0 | 142.575 | 129.7 | 1166.025 | 740411.2106 | 189624.8638 | 2631.325 | -59.7306
446 | C | SOK | TOU | FC | ET | HC | R60 | 2.4559 | 24 | 1.2 | 8760 | 139238.4918 | 0 | 135213.7415 | 65533.1035 | 111858.2722 | 16293 | 38017 | 36659.25 | 32586 | 17131.5214 | 8760 | 1475.3019 | 11869.1524 | 0 | 0 | 907.3524 | 6225.2496 | 1385.0555 | -1372.7675 | 1896.663 | 3174.8983 | 8760 | 2105.5725 | 876.7466 | 1228.8259 | 2105.0158 | 8252.2271 | 4056.9888 | 5145.694 | 3198.839 | 0 | 9270.9607 | 8760 | 0 | 157.55 | 114 | 1166.025 | 740394.0851 | 189624.8638 | 2544.35 | -52.2011
447 | C | SOK | TOU | FC | ET | HC | R60 | 2.4559 | 24 | 1.8 | 8760 | 142695.1314 | 0 | 133599.0992 | 65533.1035 | 111858.2722 | 16275 | 37975 | 36618.75 | 32550 | 16986.6396 | 8760 | 1475.3019 | 12210.1235 | 0 | 0 | 880.2039 | 6107.3781 | 1234.9111 | -1392.5505 | 2031.5775 | 3181.521 | 8760 | 2105.8839 | 781.2887 | 1324.5952 | 2105.0158 | 8252.2271 | 4065.5008 | 5149.9567 | 3202.0431 | 0 | 9605.0485 | 8760 | 0 | 166.85 | 104.4 | 1166.025 | 740273.0852 | 189624.8638 | 2503 | -49.2863
448 | C | SOK | TOU | FC | ET | HC | R60 | 2.4559 | 28.5 | 0.713 | 8760 | 129794.1717 | 0 | 134408.2952 | 65533.1035 | 111858.2722 | 16125 | 37625 | 36281.25 | 32250 | 24746.5862 | 8760 | 1475.3019 | 11927.5013 | 0 | 0 | 910.3998 | 6108.3651 | 1468.3321 | -1364.6676 | 1836.3538 | 3211.7367 | 8760 | 2105.9274 | 919.8172 | 1186.1102 | 2105.0158 | 8252.2271 | 4049.034 | 5109.2763 | 3186.708 | 0 | 9272.4087 | 8760 | 0 | 153.45 | 115.3 | 1166.025 | 740430.9718 | 189624.8638 | 2766.8 | -104.5669
449 | C | SOK | TOU | FC | ET | HC | R60 | 2.4559 | 28.5 | 1.425 | 8760 | 136586.9269 | 0 | 130341.3164 | 65533.1035 | 111858.2722 | 15978 | 37282 | 35950.5 | 31956 | 21562.7141 | 8760 | 1475.3019 | 12688.2176 | 0 | 0 | 825.9392 | 5803.1283 | 1174.3136 | -1409.8692 | 2098.7482 | 3209.3273 | 8760 | 2105.5426 | 735.3141 | 1370.2284 | 2105.0158 | 8252.2271 | 4071.8341 | 5115.5706 | 3189.5738 | 0 | 10016.1239 | 8760 | 0 | 170.95 | 95.35 | 1166.025 | 740365.7853 | 189624.8638 | 2686.675 | -87.1761
450 | C | SOK | TOU | FC | ET | HC | R60 | 2.4559 | 28.5 | 2.138 | 8760 | 139748.133 | 0 | 127732.2403 | 65533.1035 | 111858.2722 | 15933 | 37177 | 35849.25 | 31866 | 19451.3681 | 8760 | 1475.3019 | 13042.1098 | 0 | 0 | 805.6681 | 5633.1973 | 1046.4977 | -1426.3076 | 2213.2514 | 3209.8848 | 8760 | 2106.0235 | 658.2471 | 1447.7764 | 2105.0158 | 8252.2271 | 4080.5922 | 5126.4028 | 3191.8543 | 0 | 10366.3027 | 8760 | 0 | 179.55 | 86 | 1166.025 | 740273.8576 | 189624.8638 | 2650.475 | -72.1096
451 | C | SOK | TOU | FC | FP | HC | OFF0 | 0.24797 | 11.5 | 0.288 | 8760 | 127500.9992 | 0 | 142085.5334 | 0 | 75581.8652 | 32811 | 76559 | 73824.75 | 65622 | 64396.7643 | 8760 | 1475.304 | 5370.8741 | 0 | 0 | 0 | 2223.6002 | 4670.216 | -1251.6044 | 1527.2665 | 2570.1577 | 8760 | 3864.5401 | 2867.5742 | 996.9659 | 3864.5241 | 2588.0754 | 0 | 9568.2989 | 5933.7769 | 0 | 3674.558 | 8760 | 0 | 129.4 | 417.45 | 1821 | 1379489.8258 | 155421.1442 | 2628.875 | -97.0665
452 | C | SOK | TOU | FC | FP | HC | OFF0 | 0.24797 | 11.5 | 0.575 | 8760 | 127403.3807 | 0 | 137930.8104 | 0 | 75581.8652 | 32830.5 | 76604.5 | 73868.625 | 65661 | 62205.0768 | 8760 | 1475.304 | 5524.9369 | 0 | 0 | 0 | 2065.9825 | 4684.2296 | -1306.7334 | 1513.3275 | 2512.9251 | 8760 | 3865.7711 | 2878.5675 | 987.2036 | 3864.5241 | 2588.0754 | 0 | 9567.6913 | 5936.2832 | 0 | 3878.8886 | 8760 | 0 | 128.4 | 418.775 | 1821 | 1379718.9373 | 155421.1442 | 2651.975 | -99.8312
453 | C | SOK | TOU | FC | FP | HC | OFF0 | 0.24797 | 11.5 | 0.863 | 8760 | 127235.6837 | 0 | 135818.2012 | 0 | 75581.8652 | 32836.5 | 76618.5 | 73882.125 | 65673 | 62665.1905 | 8760 | 1475.304 | 5602.6652 | 0 | 0 | 0 | 1985.3084 | 4674.2419 | -1323.3781 | 1521.8263 | 2479.1193 | 8760 | 3865.5611 | 2873.1832 | 992.3779 | 3864.5241 | 2588.0754 | 0 | 9566.9137 | 5935.1158 | 0 | 3984.9898 | 8760 | 0 | 129.7 | 417.575 | 1821 | 1379825.4689 | 155421.1442 | 2665.675 | -99.3295
454 | C | SOK | TOU | FC | FP | HC | OFF0 | 0.24797 | 15.5 | 0.388 | 8760 | 125444.1439 | 0 | 133530.1038 | 0 | 75581.8652 | 32236.5 | 75218.5 | 72532.125 | 64473 | 56992.0214 | 8760 | 1475.304 | 6399.3085 | 0 | 0 | 0 | 1969.935 | 4038.9937 | -1318.5687 | 2130.8045 | 2600.2005 | 8760 | 3865.4979 | 2477.8477 | 1387.6502 | 3864.5241 | 2588.0754 | 0 | 9569.6012 | 5928.828 | 0 | 4640.7796 | 8760 | 0 | 178.85 | 358.425 | 1821 | 1379348.5034 | 155421.1442 | 2774.95 | -85.5772
455 | C | SOK | TOU | FC | FP | HC | OFF0 | 0.24797 | 15.5 | 0.775 | 8760 | 126672.558 | 0 | 128365.1981 | 0 | 75581.8652 | 32179.5 | 75085.5 | 72403.875 | 64359 | 56329.7021 | 8760 | 1475.304 | 6687.643 | 0 | 0 | 0 | 1780.0295 | 3943.3336 | -1368.7841 | 2211.7901 | 2542.422 | 8760 | 3864.555 | 2426.5058 | 1438.0493 | 3864.5241 | 2588.0754 | 0 | 9562.1929 | 5926.6771 | 0 | 4979.848 | 8760 | 0 | 186.8 | 349.525 | 1821 | 1379647.276 | 155421.1442 | 2779.975 | -86.1754
456 | C | SOK | TOU | FC | FP | HC | OFF0 | 0.24797 | 15.5 | 1.163 | 8760 | 127645.9235 | 0 | 126038.8532 | 0 | 75581.8652 | 32163 | 75047 | 72366.75 | 64326 | 57433.4501 | 8760 | 1475.304 | 6829.634 | 0 | 0 | 0 | 1693.9071 | 3896.4942 | -1390.1658 | 2252.484 | 2517.9391 | 8760 | 3864.9763 | 2399.6875 | 1465.2887 | 3864.5241 | 2588.0754 | 0 | 9562.7661 | 5927.0121 | 0 | 5143.1469 | 8760 | 0 | 190.35 | 345.7 | 1821 | 1379249.4703 | 155421.1442 | 2776.6 | -86.5729
457 | C | SOK | TOU | FC | FP | HC | OFF0 | 0.24797 | 20 | 0.5 | 8760 | 124622.565 | 0 | 126356.832 | 0 | 75581.8652 | 31678.5 | 73916.5 | 71276.625 | 63357 | 50176.4232 | 8760 | 1475.304 | 7336.4389 | 0 | 0 | 0 | 1739.9068 | 3453.6155 | -1374.5535 | 2682.0051 | 2620.2785 | 8760 | 3865.5595 | 2120.733 | 1744.8265 | 3864.5241 | 2588.0754 | 0 | 9575.5515 | 5922.4514 | 0 | 5526.3412 | 8760 | 0 | 223.65 | 304.325 | 1821 | 1379183.6311 | 155421.1442 | 2903.9 | -64.4461
458 | C | SOK | TOU | FC | FP | HC | OFF0 | 0.24797 | 20 | 1 | 8760 | 127460.8088 | 0 | 119605.0322 | 0 | 75581.8652 | 31557 | 73633 | 71003.25 | 63114 | 50626.9057 | 8760 | 1475.304 | 7758.3016 | 0 | 0 | 0 | 1524.268 | 3273.6064 | -1424.7196 | 2848.1576 | 2569.8449 | 8760 | 3864.9421 | 2015.343 | 1849.5991 | 3864.5241 | 2588.0754 | 0 | 9569.8851 | 5920.5565 | 0 | 5995.9198 | 8760 | 0 | 238.975 | 286.975 | 1821 | 1379126.6721 | 155421.1442 | 2886.15 | -60.4597
459 | C | SOK | TOU | FC | FP | HC | OFF0 | 0.24797 | 20 | 1.5 | 8760 | 129064.0139 | 0 | 116901.4624 | 0 | 75581.8652 | 31528.5 | 73566.5 | 70939.125 | 63057 | 51811.5685 | 8760 | 1475.304 | 7997.2699 | 0 | 0 | 0 | 1432.3106 | 3139.2132 | -1445.7384 | 2966.3754 | 2546.4599 | 8760 | 3865.8088 | 1935.6985 | 1930.1103 | 3864.5241 | 2588.0754 | 0 | 9573.9413 | 5921.8634 | 0 | 6257.6095 | 8760 | 0 | 248.9 | 276.575 | 1821 | 1379386.6025 | 155421.1442 | 2875.6 | -55.8094
460 | C | SOK | TOU | FC | FP | HC | OFF | 0.24797 | 24 | 0.6 | 8760 | 124433.1765 | 0 | 121021.6877 | 0 | 75581.8652 | 31456.5 | 73398.5 | 70777.125 | 62913 | 45648.1333 | 8760 | 1475.304 | 7981.1976 | 0 | 0 | 0 | 1574.5694 | 3130.8013 | -1409.5809 | 3012.8031 | 2630.8824 | 8760 | 3865.6825 | 1909.1017 | 1956.5808 | 3864.5241 | 2588.0754 | 0 | 9580.7685 | 5920.834 | 0 | 6138.2856 | 8760 | 0 | 252.225 | 272.05 | 1821 | 1378840.0432 | 155421.1442 | 3001.025 | -51.6596
461 | C | SOK | TOU | FC | FP | HC | OFF | 0.24797 | 24 | 1.2 | 8760 | 128528.6025 | 0 | 113547.686 | 0 | 75581.8652 | 31240.5 | 72894.5 | 70291.125 | 62481 | 43954.8936 | 8760 | 1475.304 | 8553.855 | 0 | 0 | 0 | 1332.8391 | 2804.5801 | -1463.0384 | 3298.0529 | 2584.4701 | 8760 | 3865.8127 | 1723.1194 | 2142.6933 | 3864.5241 | 2588.0754 | 0 | 9578.125 | 5919.8659 | 0 | 6757.0733 | 8760 | 0 | 276.575 | 244.1 | 1821 | 1379123.7675 | 155421.1442 | 2968.85 | -48.1405
462 | C | SOK | TOU | FC | FP | HC | OFF | 0.24797 | 24 | 0.8 | 8760 | 126203.3272 | 0 | 117395.6795 | 0 | 75581.8652 | 31350 | 73150 | 70537.5 | 62700 | 45696.1103 | 8760 | 1475.304 | 8230.6214 | 0 | 0 | 0 | 1455.1704 | 3001.3937 | -1435.9248 | 3125.9013 | 2605.6653 | 8760 | 3865.6235 | 1835.1554 | 2030.4681 | 3864.5241 | 2588.0754 | 0 | 9579.0564 | 5918.9535 | 0 | 6412.3317 | 8760 | 0 | 261.825 | 260.675 | 1821 | 1379599.9738 | 155421.1442 | 2986.2 | -49.7153
463 | C | SOK | TOU | FC | FP | HC | OFF | 0.24797 | 28.5 | 0.713 | 8760 | 123269.828 | 0 | 116087.7667 | 0 | 75581.8652 | 31284 | 72996 | 70389 | 62568 | 47941.5535 | 8760 | 1475.304 | 8489.7814 | 0 | 0 | 0 | 1394.2466 | 2842.2986 | -1447.6358 | 3293.0099 | 2619.6396 | 8760 | 3865.8153 | 1726.5602 | 2139.2552 | 3864.5241 | 2588.0754 | 0 | 9562.4054 | 5914.7976 | 0 | 6637.1292 | 8760 | 0 | 276.75 | 244.65 | 1821 | 1379359.3978 | 155421.1442 | 3112.775 | -75.1293
464 | C | SOK | TOU | FC | FP | HC | OFF | 0.24797 | 28.5 | 1.425 | 8760 | 128308.7011 | 0 | 108041.5531 | 0 | 75581.8652 | 30976.5 | 72278.5 | 69697.125 | 61953 | 44933.8927 | 8760 | 1475.304 | 9150.7195 | 0 | 0 | 0 | 1137.6192 | 2450.8384 | -1502.4489 | 3635.6829 | 2580.6082 | 8760 | 3865.6761 | 1495.8786 | 2369.7975 | 3864.5241 | 2588.0754 | 0 | 9553.6655 | 5912.8315 | 0 | 7337.2485 | 8760 | 0 | 303.15 | 213.125 | 1821 | 1378982.0233 | 155421.1442 | 3072.375 | -72.5596
465 | C | SOK | TOU | FC | FP | HC | OFF | 0.24797 | 28.5 | 2.138 | 8760 | 129691.6906 | 0 | 105439.9766 | 0 | 75581.8652 | 30865.5 | 72019.5 | 69447.375 | 61731 | 43109.4788 | 8760 | 1475.304 | 9446.0504 | 0 | 0 | 0 | 1033.301 | 2262.9187 | -1523.6703 | 3794.0416 | 2555.5852 | 8760 | 3865.4144 | 1390.8046 | 2474.6099 | 3864.5241 | 2588.0754 | 0 | 9563.3228 | 5913.8298 | 0 | 7655.5834 | 8760 | 0 | 315.875 | 198.55 | 1821 | 1379148.2927 | 155421.1442 | 3067.4 | -53.2318
466 | C | SOK | TOU | FC | FP | HC | R100 | 2.1548 | 11.5 | 0.288 | 8760 | 144276.6959 | 0 | 175248.3223 | 65533.1035 | 159043.7645 | 14910 | 34790 | 33547.5 | 29820 | 42237.4385 | 8760 | 1482.4089 | 6443.6632 | 0 | 0 | 1483.3464 | 12894.0276 | 2373.9746 | -973.6603 | 442.4371 | 2480.5969 | 8760 | 1718.7616 | 1446.3789 | 272.3826 | 1717.6274 | 13739.0387 | 3495.0534 | 4203.0383 | 2648.9304 | 0 | 4890.6854 | 8760 | 0 | 41.825 | 206.675 | 1024.225 | 611199.7006 | 210834.9497 | 2240.25 | -113.1765
467 | C | SOK | TOU | FC | FP | HC | R100 | 2.1548 | 11.5 | 0.575 | 8760 | 147842.721 | 0 | 172139.7796 | 65533.1035 | 159043.7645 | 14959.5 | 34905.5 | 33658.875 | 29919 | 39148.6512 | 8760 | 1482.4089 | 6853.9752 | 0 | 0 | 1315.5738 | 12662.207 | 2392.7343 | -1035.2413 | 423.8854 | 2418.0552 | 8760 | 1716.8063 | 1452.9429 | 263.8634 | 1717.6274 | 13739.0387 | 3517.713 | 4204.5928 | 2649.4159 | 0 | 5362.4952 | 8760 | 0 | 39.5 | 209.825 | 1024.225 | 611116.7481 | 210834.9497 | 2213.925 | -109.7786
468 | C | SOK | TOU | FC | FP | HC | R100 | 2.1548 | 11.5 | 0.863 | 8760 | 148799.6299 | 0 | 171061.3515 | 65533.1035 | 159043.7645 | 14949 | 34881 | 33635.25 | 29898 | 38423.6953 | 8760 | 1482.4089 | 7004.3424 | 0 | 0 | 1267.4429 | 12554.3558 | 2377.2861 | -1055.0248 | 425.6399 | 2388.2658 | 8760 | 1717.1019 | 1445.2591 | 271.8429 | 1717.6274 | 13739.0387 | 3523.3967 | 4204.4128 | 2650.9697 | 0 | 5542.0955 | 8760 | 0 | 37.85 | 211.3 | 1024.225 | 611193.2046 | 210834.9497 | 2215.6 | -110.4219
469 | C | SOK | TOU | FC | FP | HC | R100 | 2.1548 | 15.5 | 0.388 | 8760 | 142755.8497 | 0 | 169097.9824 | 65533.1035 | 159043.7645 | 14643 | 34167 | 32946.75 | 29286 | 35815.9439 | 8760 | 1482.4089 | 7664.0847 | 0 | 0 | 1312.3842 | 12355.7586 | 2097.9591 | -1066.3314 | 687.8764 | 2564.5973 | 8760 | 1717.4836 | 1291.0726 | 426.4111 | 1717.6274 | 13739.0387 | 3528.3376 | 4205.5324 | 2647.2085 | 0 | 5989.6419 | 8760 | 0 | 63.3 | 180.75 | 1024.225 | 610926.0831 | 210834.9497 | 2393.3 | -99.5824
470 | C | SOK | TOU | FC | FP | HC | R100 | 2.1548 | 15.5 | 0.775 | 8760 | 147172.6741 | 0 | 165383.48 | 65533.1035 | 159043.7645 | 14692.5 | 34282.5 | 33058.125 | 29385 | 33839.1187 | 8760 | 1482.4089 | 8209.116 | 0 | 0 | 1191.747 | 12022.1442 | 2065.9741 | -1124.4997 | 721.383 | 2510.2119 | 8760 | 1717.4606 | 1261.6963 | 455.7644 | 1717.6274 | 13739.0387 | 3547.3008 | 4207.3055 | 2647.9914 | 0 | 6591.0538 | 8760 | 0 | 64.2 | 180.675 | 1024.225 | 611048.3927 | 210834.9497 | 2358.875 | -98.1339
471 | C | SOK | TOU | FC | FP | HC | R100 | 2.1548 | 15.5 | 1.163 | 8760 | 148140.9402 | 0 | 163681.0935 | 65533.1035 | 159043.7645 | 14731.5 | 34373.5 | 33145.875 | 29463 | 32478.4585 | 8760 | 1482.4089 | 8388.0333 | 0 | 0 | 1154.674 | 11899.2461 | 2055.1819 | -1146.1289 | 735.1673 | 2479.997 | 8760 | 1717.3063 | 1250.4628 | 466.8435 | 1717.6274 | 13739.0387 | 3552.1555 | 4209.4925 | 2649.9709 | 0 | 6799.5194 | 8760 | 0 | 64.85 | 180.675 | 1024.225 | 610922.0374 | 210834.9497 | 2363.7 | -95.224
472 | C | SOK | TOU | FC | FP | HC | R100 | 2.1548 | 20 | 0.5 | 8760 | 142302.9044 | 0 | 163263.3714 | 65533.1035 | 159043.7645 | 14416.5 | 33638.5 | 32437.125 | 28833 | 29409.0209 | 8760 | 1482.4089 | 8762.8374 | 0 | 0 | 1208.4936 | 11783.421 | 1887.6309 | -1139.2278 | 881.3482 | 2617.014 | 8760 | 1717.885 | 1167.5609 | 550.3241 | 1717.6274 | 13739.0387 | 3552.8305 | 4210.1524 | 2645.4348 | 0 | 6999.443 | 8760 | 0 | 79.175 | 161.1 | 1024.225 | 611056.6587 | 210834.9497 | 2532.975 | -86.4422
473 | C | SOK | TOU | FC | FP | HC | R100 | 2.1548 | 20 | 1 | 8760 | 146539.4412 | 0 | 158817.6678 | 65533.1035 | 159043.7645 | 14454 | 33726 | 32521.5 | 28908 | 29681.4271 | 8760 | 1482.4089 | 9411.0514 | 0 | 0 | 1098.1463 | 11398.1048 | 1797.2372 | -1194.1475 | 970.2623 | 2566.5197 | 8760 | 1717.7259 | 1099.6097 | 618.1162 | 1717.6274 | 13739.0387 | 3569.4426 | 4214.0219 | 2646.5544 | 0 | 7700.5362 | 8760 | 0 | 84.2 | 156.7 | 1024.225 | 610973.5238 | 210834.9497 | 2508.025 | -79.4618
474 | C | SOK | TOU | FC | FP | HC | R100 | 2.1548 | 20 | 1.5 | 8760 | 147291.3801 | 0 | 156960.7916 | 65533.1035 | 159043.7645 | 14457 | 33733 | 32528.25 | 28914 | 27941.4145 | 8760 | 1482.4089 | 9668.8742 | 0 | 0 | 1055.8732 | 11228.477 | 1728.0174 | -1209.7896 | 1035.373 | 2524.7941 | 8760 | 1717.056 | 1052.2519 | 664.804 | 1717.6274 | 13739.0387 | 3572.0186 | 4219.9351 | 2647.9526 | 0 | 7996.1999 | 8760 | 0 | 89.1 | 151.85 | 1024.225 | 611276.5547 | 210834.9497 | 2519.85 | -72.7825
475 | C | SOK | TOU | FC | FP | HC | R10 | 2.1548 | 24 | 0.6 | 8760 | 142913.0697 | 0 | 159142.3961 | 65533.1035 | 159043.7645 | 14370 | 33530 | 32332.5 | 28740 | 26301.5893 | 8760 | 1482.4089 | 9584.6722 | 0 | 0 | 1137.5965 | 11346.0085 | 1769.3734 | -1187.5448 | 1010.8081 | 2650.4762 | 8760 | 1717.5531 | 1082.8087 | 634.7443 | 1717.6274 | 13739.0387 | 3568.2821 | 4215.4965 | 2644.7541 | 0 | 7762.3939 | 8760 | 0 | 89.9 | 149.6 | 1024.225 | 610881.0647 | 210834.9497 | 2635.725 | -74.3884
476 | C | SOK | TOU | FC | FP | HC | R10 | 2.1548 | 24 | 1.2 | 8760 | 146960.8203 | 0 | 154212.2248 | 65533.1035 | 159043.7645 | 14431.5 | 33673.5 | 32470.875 | 28863 | 25367.8874 | 8760 | 1482.4089 | 10331.7836 | 0 | 0 | 1038.5653 | 10898.4679 | 1644.8546 | -1239.6242 | 1137.6418 | 2589.6326 | 8760 | 1718.5959 | 993.1381 | 725.4577 | 1717.6274 | 13739.0387 | 3586.032 | 4227.2463 | 2650.6378 | 0 | 8569.6744 | 8760 | 0 | 99 | 141.525 | 1024.225 | 611038.5509 | 210834.9497 | 2619.825 | -66.2901
477 | C | SOK | TOU | FC | FP | HC | R10 | 2.1548 | 24 | 1.8 | 8760 | 147885.4656 | 0 | 151328.6671 | 65533.1035 | 159043.7645 | 14298 | 33362 | 32170.5 | 28596 | 23991.8558 | 8760 | 1482.4089 | 10612.803 | 0 | 0 | 1000.7044 | 10673.136 | 1542.8598 | -1255.6916 | 1205.2697 | 2548.7642 | 8760 | 1717.6794 | 945.1051 | 772.5742 | 1717.6274 | 13739.0387 | 3589.1373 | 4230.8861 | 2649.663 | 0 | 8887.5319 | 8760 | 0 | 103.35 | 134.95 | 1024.225 | 611255.5665 | 210834.9497 | 2627.15 | -58.6562
478 | C | SOK | TOU | FC | FP | HC | R10 | 2.1548 | 28.5 | 0.713 | 8760 | 144191.5764 | 0 | 154620.9476 | 65533.1035 | 159043.7645 | 14256 | 33264 | 32076 | 28512 | 24200.4078 | 8760 | 1482.4089 | 10331.0741 | 0 | 0 | 1073.7468 | 10875.5363 | 1607.1131 | -1227.4814 | 1158.4415 | 2671.4706 | 8760 | 1718.619 | 987.5155 | 731.1035 | 1717.6274 | 13739.0387 | 3580.314 | 4212.3863 | 2644.0551 | 0 | 8465.941 | 8760 | 0 | 102.1 | 135.5 | 1024.225 | 610948.3054 | 210834.9497 | 2736.975 | -77.7372
479 | C | SOK | TOU | FC | FP | HC | R10 | 2.1548 | 28.5 | 1.425 | 8760 | 147631.7255 | 0 | 149134.3134 | 65533.1035 | 159043.7645 | 14235 | 33215 | 32028.75 | 28470 | 26600.3366 | 8760 | 1482.4089 | 11117.4705 | 0 | 0 | 970.3924 | 10388.2429 | 1507.4109 | -1282.5351 | 1254.5177 | 2604.6028 | 8760 | 1717.8445 | 912.6712 | 805.1733 | 1717.6274 | 13739.0387 | 3600.0453 | 4201.6686 | 2644.1371 | 0 | 9313.5089 | 8760 | 0 | 108 | 129.25 | 1024.225 | 610754.0385 | 210834.9497 | 2734.625 | -92.4918
480 | C | SOK | TOU | FC | FP | HC | R10 | 2.1548 | 28.5 | 2.138 | 8760 | 149112.5402 | 0 | 146641.4796 | 65533.1035 | 159043.7645 | 14197.5 | 33127.5 | 31944.375 | 28395 | 26101.8137 | 8760 | 1482.4089 | 11496.4182 | 0 | 0 | 957.5522 | 10119.3071 | 1402.0642 | -1295.5032 | 1352.2828 | 2564.8214 | 8760 | 1717.7919 | 848.8481 | 868.9438 | 1717.6274 | 13739.0387 | 3602.9665 | 4202.4011 | 2644.7851 | 0 | 9730.0648 | 8760 | 0 | 116.225 | 120.4 | 1024.225 | 610852.4396 | 210834.9497 | 2735.05 | -92.2488
481 | C | SOK | TOU | FC | FP | HC | R600 | 2.4559 | 11.5 | 0.288 | 8760 | 144430.5284 | 0 | 159088.3997 | 65533.1035 | 111858.2722 | 17530.5 | 40904.5 | 39443.625 | 35061 | 43352.6011 | 8760 | 1475.3019 | 6350.1379 | 0 | 0 | 1494.6054 | 7878.7037 | 2887.5095 | -1017.4343 | 492.8333 | 2430.0483 | 8760 | 2105.102 | 1800.2302 | 304.8718 | 2105.0158 | 8252.2271 | 3879.7644 | 5151.9936 | 3205.6991 | 0 | 4757.2151 | 8760 | 0 | 46.4 | 245.775 | 1166.025 | 740551.0128 | 189624.8638 | 2246.075 | -112.9828
482 | C | SOK | TOU | FC | FP | HC | R600 | 2.4559 | 11.5 | 0.575 | 8760 | 147784.737 | 0 | 156832.5501 | 65533.1035 | 111858.2722 | 17623.5 | 41121.5 | 39652.875 | 35247 | 39810.6793 | 8760 | 1475.3019 | 6709.6636 | 0 | 0 | 1268.943 | 7755.3551 | 2926.3898 | -1083.03 | 454.7147 | 2379.1169 | 8760 | 2104.5989 | 1819.3649 | 285.234 | 2105.0158 | 8252.2271 | 3917.1688 | 5155.081 | 3208.864 | 0 | 5167.0208 | 8760 | 0 | 41.95 | 251.775 | 1166.025 | 740657.6509 | 189624.8638 | 2221.15 | -110.8997
483 | C | SOK | TOU | FC | FP | HC | R600 | 2.4559 | 11.5 | 0.863 | 8760 | 148736.8225 | 0 | 156089.3497 | 65533.1035 | 111858.2722 | 17664 | 41216 | 39744 | 35328 | 38822.8599 | 8760 | 1475.3019 | 6839.4921 | 0 | 0 | 1206.4768 | 7709.1535 | 2931.4065 | -1109.2069 | 451.2607 | 2356.1778 | 8760 | 2104.33 | 1815.6273 | 288.7026 | 2105.0158 | 8252.2271 | 3930.4116 | 5154.588 | 3209.9378 | 0 | 5318.4555 | 8760 | 0 | 40.2 | 254.2 | 1166.025 | 740640.6977 | 189624.8638 | 2224.625 | -111.2298
484 | C | SOK | TOU | FC | FP | HC | R600 | 2.4559 | 15.5 | 0.388 | 8760 | 142797.7418 | 0 | 153598.7657 | 65533.1035 | 111858.2722 | 17239.5 | 40225.5 | 38788.875 | 34479 | 35410.2527 | 8760 | 1475.3019 | 7484.6365 | 0 | 0 | 1280.4001 | 7537.9218 | 2597.7391 | -1119.2593 | 760.3173 | 2525.0956 | 8760 | 2105.8858 | 1631.9667 | 473.9191 | 2105.0158 | 8252.2271 | 3933.4407 | 5154.197 | 3204.3088 | 0 | 5760.9442 | 8760 | 0 | 69.1 | 218.225 | 1166.025 | 740481.1247 | 189624.8638 | 2399.875 | -101.8081
485 | C | SOK | TOU | FC | FP | HC | R600 | 2.4559 | 15.5 | 0.775 | 8760 | 146419.1573 | 0 | 150703.2088 | 65533.1035 | 111858.2722 | 17313 | 40397 | 38954.25 | 34626 | 34407.9858 | 8760 | 1475.3019 | 7933.0818 | 0 | 0 | 1128.6454 | 7352.9291 | 2561.895 | -1186.4095 | 791.0612 | 2478.7461 | 8760 | 2104.7274 | 1598.2002 | 506.5272 | 2105.0158 | 8252.2271 | 3970.6525 | 5150.8352 | 3205.7505 | 0 | 6253.1124 | 8760 | 0 | 68.85 | 219.7 | 1166.025 | 740643.4213 | 189624.8638 | 2382.325 | -104.8089
486 | C | SOK | TOU | FC | FP | HC | R600 | 2.4559 | 15.5 | 1.163 | 8760 | 147458.0767 | 0 | 149399.7957 | 65533.1035 | 111858.2722 | 17359.5 | 40505.5 | 39058.875 | 34719 | 33513.1179 | 8760 | 1475.3019 | 8104.2421 | 0 | 0 | 1080.3108 | 7276.216 | 2538.6286 | -1213.7792 | 816.6219 | 2451.9605 | 8760 | 2104.4073 | 1577.8546 | 526.5527 | 2105.0158 | 8252.2271 | 3983.6225 | 5153.6839 | 3207.8572 | 0 | 6447.5898 | 8760 | 0 | 70.25 | 219.075 | 1166.025 | 740662.8752 | 189624.8638 | 2388.55 | -101.5434
487 | C | SOK | TOU | FC | FP | HC | R600 | 2.4559 | 20 | 0.5 | 8760 | 141887.6818 | 0 | 148514.1047 | 65533.1035 | 111858.2722 | 16992 | 39648 | 38232 | 33984 | 30022.2566 | 8760 | 1475.3019 | 8471.8027 | 0 | 0 | 1141.4367 | 7182.1495 | 2339.0331 | -1198.5085 | 998.3077 | 2583.395 | 8760 | 2105.7904 | 1477.3435 | 628.4469 | 2105.0158 | 8252.2271 | 3971.4271 | 5159.1537 | 3201.5441 | 0 | 6653.2615 | 8760 | 0 | 88.45 | 194.75 | 1166.025 | 740516.0543 | 189624.8638 | 2545.475 | -85.1756
488 | C | SOK | TOU | FC | FP | HC | R600 | 2.4559 | 20 | 1 | 8760 | 145633.859 | 0 | 145037.3366 | 65533.1035 | 111858.2722 | 17044.5 | 39770.5 | 38350.125 | 34089 | 29312.3374 | 8760 | 1475.3019 | 9028.0428 | 0 | 0 | 1027.9655 | 6938.8041 | 2228.546 | -1263.1111 | 1103.7829 | 2536.373 | 8760 | 2105.0567 | 1393.701 | 711.3556 | 2105.0158 | 8252.2271 | 4009.8175 | 5160.9015 | 3204.6547 | 0 | 7254.0331 | 8760 | 0 | 93.875 | 190.2 | 1166.025 | 740486.1054 | 189624.8638 | 2534.525 | -79.8295
489 | C | SOK | TOU | FC | FP | HC | R600 | 2.4559 | 20 | 1.5 | 8760 | 145563.7182 | 0 | 143583.9335 | 65533.1035 | 111858.2722 | 17070 | 39830 | 38407.5 | 34140 | 28767.9493 | 8760 | 1475.3019 | 9201.8604 | 0 | 0 | 998.3213 | 6831.8697 | 2198.9007 | -1285.8242 | 1133.1532 | 2499.052 | 8760 | 2104.6086 | 1368.6745 | 735.9341 | 2105.0158 | 8252.2271 | 4018.9345 | 5164.1388 | 3206.7844 | 0 | 7460.3741 | 8760 | 0 | 94.75 | 189.75 | 1166.025 | 740410.8763 | 189624.8638 | 2562.225 | -74.8068
490 | C | SOK | TOU | FC | FP | HC | R60 | 2.4559 | 24 | 0.6 | 8760 | 141754.2035 | 0 | 144615.1147 | 65533.1035 | 111858.2722 | 16915.5 | 39469.5 | 38059.875 | 33831 | 26796.0279 | 8760 | 1475.3019 | 9182.9081 | 0 | 0 | 1053.5717 | 6906.1428 | 2176.235 | -1249.7568 | 1161.3532 | 2610.5458 | 8760 | 2105.0987 | 1368.945 | 736.1537 | 2105.0158 | 8252.2271 | 3996.3431 | 5160.339 | 3201.8168 | 0 | 7308.785 | 8760 | 0 | 101.7 | 180.225 | 1166.025 | 740378.9896 | 189624.8638 | 2659.6 | -78.1364
491 | C | SOK | TOU | FC | FP | HC | R60 | 2.4559 | 24 | 1.2 | 8760 | 144517.0036 | 0 | 140634.3801 | 65533.1035 | 111858.2722 | 16890 | 39410 | 38002.5 | 33780 | 25864.0859 | 8760 | 1475.3019 | 9782.1333 | 0 | 0 | 968.2174 | 6597.2896 | 2023.3639 | -1309.335 | 1303.7968 | 2551.3769 | 8760 | 2106.0327 | 1264.1514 | 841.8813 | 2105.0158 | 8252.2271 | 4031.9733 | 5167.123 | 3204.9959 | 0 | 7962.958 | 8760 | 0 | 110.1 | 171.4 | 1166.025 | 740582.0505 | 189624.8638 | 2669.275 | -68.3736
492 | C | SOK | TOU | FC | FP | HC | R60 | 2.4559 | 24 | 1.8 | 8760 | 145335.6677 | 0 | 138874.2475 | 65533.1035 | 111858.2722 | 16893 | 39417 | 38009.25 | 33786 | 25983.4382 | 8760 | 1475.3019 | 10064.0342 | 0 | 0 | 940.5362 | 6467.8907 | 1928.1438 | -1331.3046 | 1398.9957 | 2510.0444 | 8760 | 2105.8666 | 1196.6768 | 909.1898 | 2105.0158 | 8252.2271 | 4040.7472 | 5172.3155 | 3206.7988 | 0 | 8283.1197 | 8760 | 0 | 117.025 | 164.525 | 1166.025 | 740575.8325 | 189624.8638 | 2682.725 | -62.5246
493 | C | SOK | TOU | FC | FP | HC | R60 | 2.4559 | 28.5 | 0.713 | 8760 | 141726.4035 | 0 | 141108.3485 | 65533.1035 | 111858.2722 | 16767 | 39123 | 37725.75 | 33534 | 27349.3555 | 8760 | 1475.3019 | 9794.1043 | 0 | 0 | 981.5546 | 6615.0947 | 2001.7757 | -1294.0583 | 1321.8588 | 2622.9398 | 8760 | 2105.2254 | 1261.2912 | 843.9342 | 2105.0158 | 8252.2271 | 4019.9472 | 5152.3249 | 3197.6876 | 0 | 7882.5032 | 8760 | 0 | 114.425 | 165.025 | 1166.025 | 740555.9783 | 189624.8638 | 2779.55 | -83.2357
494 | C | SOK | TOU | FC | FP | HC | R60 | 2.4559 | 28.5 | 1.425 | 8760 | 144115.4615 | 0 | 136568.1512 | 65533.1035 | 111858.2722 | 16758 | 39102 | 37705.5 | 33516 | 26069.7806 | 8760 | 1475.3019 | 10454.0095 | 0 | 0 | 906.0372 | 6256.7933 | 1838.8592 | -1350.394 | 1479.6595 | 2553.9711 | 8760 | 2105.3393 | 1143.5012 | 961.8381 | 2105.0158 | 8252.2271 | 4048.3205 | 5151.8015 | 3201.5371 | 0 | 8606.3642 | 8760 | 0 | 123.425 | 155.875 | 1166.025 | 740440.2597 | 189624.8638 | 2795.425 | -83.4724
495 | C | SOK | TOU | FC | FP | HC | R60 | 2.4559 | 28.5 | 2.138 | 8760 | 146157.1706 | 0 | 134316.0514 | 65533.1035 | 111858.2722 | 16762.5 | 39112.5 | 37715.625 | 33525 | 29420.1439 | 8760 | 1475.3019 | 10838.6801 | 0 | 0 | 873.3507 | 6085.3319 | 1727.3736 | -1370.5986 | 1595.7919 | 2523.7491 | 8760 | 2105.9207 | 1065.6576 | 1040.2631 | 2105.0158 | 8252.2271 | 4055.9677 | 5153.1052 | 3203.5538 | 0 | 9019.9219 | 8760 | 0 | 133.2 | 146.175 | 1166.025 | 740340.1437 | 189624.8638 | 2791.025 | -83.5545
496 | C | SOK | TOU | FC | FP | WC | OFF0 | 0.39259 | 18 | 0.45 | 8760 | 130771.038 | 0 | 150275.7373 | 0 | 82698.0092 | 67075.5 | 212405.75 | 150919.875 | 134151 | 77081.9782 | 8760 | 1475.304 | 7527.5665 | 0 | 0 | 0 | 3199.9959 | 7591.4604 | -1315.9802 | 3019.1085 | 2612.7022 | 8760 | 6116.6185 | 4359.7888 | 1756.8297 | 6118.3717 | 4097.4792 | 0 | 16468.0522 | 10342.0345 | 0 | 5760.5047 | 8760 | 20160.4288 | 310.925 | 807 | 1821 | 2220085.2526 | 155421.1442 | 2793.1
497 | C | SOK | TOU | FC | FP | WC | OFF0 | 0.39259 | 18 | 0.9 | 8760 | 130989.6189 | 0 | 146365.498 | 0 | 82698.0092 | 67158 | 212667 | 151105.5 | 134316 | 76498.216 | 8760 | 1475.304 | 7756.0138 | 0 | 0 | 0 | 2965.367 | 7606.0905 | -1357.7125 | 3013.6802 | 2552.6433 | 8760 | 6116.6774 | 4370.7063 | 1745.9711 | 6118.3717 | 4097.4792 | 0 | 16470.7741 | 10346.6709 | 0 | 6041.5453 | 8760 | 20164.2654 | 312.575 | 806.725 | 1821 | 2220196.3085 | 155421.1442 | 2805.1
498 | C | SOK | TOU | FC | FP | WC | OFF0 | 0.39259 | 18 | 1.35 | 8760 | 131360.3816 | 0 | 143985.9066 | 0 | 82698.0092 | 67237.5 | 212918.75 | 151284.375 | 134475 | 76511.9129 | 8760 | 1475.304 | 7889.1279 | 0 | 0 | 0 | 2849.5767 | 7599.1101 | -1368.3763 | 3021.8635 | 2528.1774 | 8760 | 6116.6353 | 4372.6398 | 1743.9955 | 6118.3717 | 4097.4792 | 0 | 16475.6744 | 10352.3753 | 0 | 6199.7123 | 8760 | 20171.2993 | 315.275 | 805.35 | 1821 | 2220204.5518 | 155421.1442 | 2806.9
499 | C | SOK | TOU | FC | FP | WC | OFF0 | 0.39259 | 24.5 | 0.6 | 8760 | 133529.7064 | 0 | 141226.0906 | 0 | 82698.0092 | 67201.5 | 212804.75 | 151203.375 | 134403 | 76413.3734 | 8760 | 1475.304 | 9078.3396 | 0 | 0 | 0 | 2828.7467 | 6719.1518 | -1373.7907 | 3963.481 | 2623.4186 | 8760 | 6116.5457 | 3812.1945 | 2304.3512 | 6118.3717 | 4097.4792 | 0 | 16524.8256 | 10399.0849 | 0 | 7267.0714 | 8760 | 20207.6613 | 404.6 | 715.425 | 1821 | 2220079.5423 | 155421.1442 | 2928.55
500 | C | SOK | TOU | FC | FP | WC | OFF0 | 0.39259 | 24.5 | 1.25 | 8760 | 135124.7878 | 0 | 135984.6901 | 0 | 82698.0092 | 67297.5 | 213108.75 | 151419.375 | 134595 | 75599.2267 | 8760 | 1475.304 | 9453.162 | 0 | 0 | 0 | 2536.8711 | 6635.6976 | -1412.1858 | 4050.5857 | 2570.6415 | 8760 | 6115.8418 | 3769.9569 | 2345.8849 | 6118.3717 | 4097.4792 | 0 | 16533.2423 | 10409.6134 | 0 | 7688.9548 | 8760 | 20214.9715 | 415.6 | 706.025 | 1821 | 2220129.4949 | 155421.1442 | 2919.85
501 | C | SOK | TOU | FC | FP | WC | OFF0 | 0.39259 | 24.5 | 1.85 | 8760 | 136040.9315 | 0 | 133047.136 | 0 | 82698.0092 | 67405.5 | 213450.75 | 151662.375 | 134811 | 75350.1499 | 8760 | 1475.304 | 9652.0262 | 0 | 0 | 0 | 2406.0313 | 6584.3937 | -1424.8582 | 4105.8893 | 2549.1039 | 8760 | 6117.5512 | 3744.2464 | 2373.3048 | 6118.3717 | 4097.4792 | 0 | 16544.5869 | 10420.2611 | 0 | 7910.6573 | 8760 | 20226.5022 | 422.8 | 700.625 | 1821 | 2219683.9717 | 155421.1442 | 2914.5
502 | C | SOK | TOU | FC | FP | WC | OFF0 | 0.39259 | 31 | 0.8 | 8760 | 133980.7602 | 0 | 133761.0884 | 0 | 82698.0092 | 66537 | 210700.5 | 149708.25 | 133074 | 78967.4661 | 8760 | 1475.304 | 9945.6321 | 0 | 0 | 0 | 2511.2394 | 5986.1128 | -1427.2433 | 4681.1265 | 2617.6298 | 8760 | 6117.0025 | 3376.0737 | 2740.9288 | 6118.3717 | 4097.4792 | 0 | 16534.9994 | 10409.0695 | 0 | 8114.3889 | 8760 | 20197.1124 | 467.075 | 641.875 | 1821 | 2220409.0745 | 155421.1442 | 3072.425
503 | C | SOK | TOU | FC | FP | WC | OFF0 | 0.39259 | 31 | 1.55 | 8760 | 137425.0421 | 0 | 127472.0077 | 0 | 82698.0092 | 66673.5 | 211132.75 | 150015.375 | 133347 | 78287.0598 | 8760 | 1475.304 | 10499.4504 | 0 | 0 | 0 | 2195.7504 | 5809.0703 | -1461.8042 | 4860.4274 | 2583.9507 | 8760 | 6116.9655 | 3290.6322 | 2826.3334 | 6118.3717 | 4097.4792 | 0 | 16547.7016 | 10424.381 | 0 | 8699.1145 | 8760 | 20211.9652 | 491.025 | 620.2 | 1821 | 2220409.3725 | 155421.1442 | 3042.975
504 | C | SOK | TOU | FC | FP | WC | OFF0 | 0.39259 | 31 | 2.35 | 8760 | 138543.9179 | 0 | 124455.7088 | 0 | 82698.0092 | 66811.5 | 211569.75 | 150325.875 | 133623 | 77451.8258 | 8760 | 1475.304 | 10757.0223 | 0 | 0 | 0 | 2063.3825 | 5683.184 | -1477.7517 | 4980.6926 | 2559.6403 | 8760 | 6116.8355 | 3236.8527 | 2879.9828 | 6118.3717 | 4097.4792 | 0 | 16557.9652 | 10436.2961 | 0 | 8982.4284 | 8760 | 20224.5626 | 508.525 | 605 | 1821 | 2220294.0243 | 155421.1442 | 3036.35
505 | C | SOK | TOU | FC | FP | WC | OFF | 0.39259 | 38 | 0.95 | 8760 | 136603.6133 | 0 | 128364.4482 | 0 | 82698.0092 | 66333 | 210054.5 | 149249.25 | 132666 | 82001.3278 | 8760 | 1475.304 | 10746.1854 | 0 | 0 | 0 | 2262.3008 | 5421.9643 | -1459.2036 | 5232.8046 | 2606.2922 | 8760 | 6115.6665 | 3055.3104 | 3060.3561 | 6118.3717 | 4097.4792 | 0 | 16555.7371 | 10429.8665 | 0 | 8903.3884 | 8760 | 20212.6358 | 519.9 | 585.65 | 1821 | 2220537.0892 | 155421.1442 | 3194.125
506 | C | SOK | TOU | FC | FP | WC | OFF | 0.39259 | 38 | 1.9 | 8760 | 141926.2117 | 0 | 119744.5229 | 0 | 82698.0092 | 66469.5 | 210486.75 | 149556.375 | 132939 | 81224.5705 | 8760 | 1475.304 | 11594.933 | 0 | 0 | 0 | 1874.4658 | 5042.7557 | -1495.9057 | 5600.6785 | 2572.1679 | 8760 | 6115.3447 | 2866.2683 | 3249.0764 | 6118.3717 | 4097.4792 | 0 | 16570.0215 | 10448.8563 | 0 | 9779.8952 | 8760 | 20228.7002 | 566.55 | 541.275 | 1821 | 2220169.1857 | 155421.1442 | 3152.3
507 | C | SOK | TOU | FC | FP | WC | OFF | 0.39259 | 38 | 2.85 | 8760 | 143424.944 | 0 | 117341.6831 | 0 | 82698.0092 | 66538.5 | 210705.25 | 149711.625 | 133077 | 81243.3897 | 8760 | 1475.304 | 11974.4369 | 0 | 0 | 0 | 1755.8836 | 4855.3082 | -1511.4898 | 5775.7621 | 2541.5198 | 8760 | 6115.8103 | 2793.5755 | 3322.2348 | 6118.3717 | 4097.4792 | 0 | 16576.711 | 10457.8478 | 0 | 10185.3317 | 8760 | 20238.621 | 593.525 | 515.45 | 1821 | 2220072.3135 | 155421.1442 | 3145.575
508 | C | SOK | TOU | FC | FP | WC | OFF | 0.39259 | 44.5 | 1.1 | 8760 | 140805.0697 | 0 | 122914.5615 | 0 | 82698.0092 | 65878.5 | 208615.25 | 148226.625 | 131757 | 84357.4681 | 8760 | 1475.304 | 11441.1964 | 0 | 0 | 0 | 2013.4816 | 4945.5164 | -1483.3644 | 5660.9337 | 2590.522 | 8760 | 6117.2348 | 2798.0883 | 3319.1464 | 6118.3717 | 4097.4792 | 0 | 16564.1825 | 10438.063 | 0 | 9598.2021 | 8760 | 20213.6527 | 557.125 | 540.85 | 1821 | 2220430.8089 | 155421.1442 | 3283.95
509 | C | SOK | TOU | FC | FP | WC | OFF | 0.39259 | 44.5 | 2.25 | 8760 | 147762.8967 | 0 | 113942.9097 | 0 | 82698.0092 | 66133.5 | 209422.75 | 148800.375 | 132267 | 82629.6801 | 8760 | 1475.304 | 12546.1291 | 0 | 0 | 0 | 1611.1786 | 4355.4552 | -1520.1485 | 6252.0826 | 2556.3014 | 8760 | 6115.6132 | 2491.2499 | 3624.3634 | 6118.3717 | 4097.4792 | 0 | 16585.3058 | 10466.2726 | 0 | 10723.5568 | 8760 | 20231.1745 | 631.65 | 470.575 | 1821 | 2219646.3743 | 155421.1442 | 3234.05
510 | C | SOK | TOU | FC | FP | WC | OFF | 0.39259 | 44.5 | 3.35 | 8760 | 149830.3255 | 0 | 110621.3811 | 0 | 82698.0092 | 66286.5 | 209907.25 | 149144.625 | 132573 | 82045.7593 | 8760 | 1475.304 | 12965.7604 | 0 | 0 | 0 | 1477.2161 | 4153.3074 | -1539.4844 | 6459.9311 | 2536.0361 | 8760 | 6115.9068 | 2418.5075 | 3697.3993 | 6118.3717 | 4097.4792 | 0 | 16608.116 | 10490.0209 | 0 | 11162.5934 | 8760 | 20262.3202 | 665.2 | 439.575 | 1821 | 2219944.5154 | 155421.1442 | 3225
511 | C | SOK | TOU | FC | FP | WC | R100 | 3.4115 | 18 | 0.45 | 8760 | 151656.1539 | 0 | 181029.6869 | 65533.1035 | 199668.8608 | 34375.5 | 108855.75 | 77344.875 | 68751 | 34377.5213 | 8760 | 1482.4089 | 9162.7808 | 0 | 0 | 1996.4757 | 19954.227 | 4043.0902 | -1041.9383 | 978.1382 | 2578.1741 | 8760 | 2716.7905 | 2172.959 | 543.8315 | 2719.3731 | 21751.8493 | 4996.7917 | 7553.7563 | 4857.6975 | 0 | 7487.922 | 8760 | 9126.3343 | 106.125 | 466.8 | 1024.225 | 983526.5368 | 210834.9497 | 2353.05
512 | C | SOK | TOU | FC | FP | WC | R100 | 3.4115 | 18 | 0.9 | 8760 | 156733.1379 | 0 | 178050.1355 | 65533.1035 | 199668.8608 | 34321.5 | 108684.75 | 77223.375 | 68643 | 34513.1624 | 8760 | 1482.4089 | 9829.5265 | 0 | 0 | 1802.0837 | 19540.1259 | 4041.5582 | -1097.9255 | 970.8728 | 2521.8832 | 8760 | 2717.0966 | 2182.9027 | 534.1939 | 2719.3731 | 21751.8493 | 5040.9136 | 7550.517 | 4853.9419 | 0 | 8211.44 | 8760 | 9125.2581 | 107.1 | 464.925 | 1024.225 | 983372.1236 | 210834.9497 | 2311.525
513 | C | SOK | TOU | FC | FP | WC | R100 | 3.4115 | 18 | 1.35 | 8760 | 158544.4848 | 0 | 176204.5086 | 65533.1035 | 199668.8608 | 34327.5 | 108703.75 | 77236.875 | 68655 | 34695.2772 | 8760 | 1482.4089 | 10109.2867 | 0 | 0 | 1757.2325 | 19332.4842 | 4014.9367 | -1112.7356 | 1000.8992 | 2487.5728 | 8760 | 2717.3127 | 2175.298 | 542.0147 | 2719.3731 | 21751.8493 | 5053.1817 | 7553.8866 | 4857.1925 | 0 | 8523.7055 | 8760 | 9129.1926 | 112.875 | 459.25 | 1024.225 | 983432.2595 | 210834.9497 | 2301.575
514 | C | SOK | TOU | FC | FP | WC | R100 | 3.4115 | 24.5 | 0.6 | 8760 | 155100.9913 | 0 | 174424.8772 | 65533.1035 | 199668.8608 | 34150.5 | 108143.25 | 76838.625 | 68301 | 34280.8545 | 8760 | 1482.4089 | 10924.0429 | 0 | 0 | 1814.3401 | 19089.801 | 3659.8053 | -1121.1984 | 1367.6702 | 2641.0257 | 8760 | 2717.6271 | 1956.4586 | 761.1685 | 2719.3731 | 21751.8493 | 5058.6838 | 7566.2152 | 4869.9712 | 0 | 9143.7642 | 8760 | 9131.2993 | 147 | 422.175 | 1024.225 | 983452.9404 | 210834.9497 | 2507.45
515 | C | SOK | TOU | FC | FP | WC | R100 | 3.4115 | 24.5 | 1.25 | 8760 | 160203.2047 | 0 | 170067.6677 | 65533.1035 | 199668.8608 | 34110 | 108015 | 76747.5 | 68220 | 33912.4021 | 8760 | 1482.4089 | 11805.9436 | 0 | 0 | 1659.0424 | 18500.6914 | 3607.779 | -1176.7048 | 1418.7358 | 2582.4251 | 8760 | 2717.1296 | 1937.9513 | 779.1783 | 2719.3731 | 21751.8493 | 5101.1752 | 7561.3725 | 4866.5584 | 0 | 10084.299 | 8760 | 9129.0302 | 155.325 | 413.175 | 1024.225 | 983438.6092 | 210834.9497 | 2475.725
516 | C | SOK | TOU | FC | FP | WC | R100 | 3.4115 | 24.5 | 1.85 | 8760 | 161417.8748 | 0 | 168291.0362 | 65533.1035 | 199668.8608 | 34201.5 | 108304.75 | 76953.375 | 68403 | 33531.0018 | 8760 | 1482.4089 | 12089.0421 | 0 | 0 | 1618.8321 | 18262.0365 | 3570.0324 | -1189.8186 | 1459.0695 | 2544.8647 | 8760 | 2717.7939 | 1925.5138 | 792.2802 | 2719.3731 | 21751.8493 | 5106.4798 | 7571.7142 | 4876.36 | 0 | 10402.1479 | 8760 | 9140.4078 | 161.9 | 408.125 | 1024.225 | 983527.2029 | 210834.9497 | 2474.775
517 | C | SOK | TOU | FC | FP | WC | R100 | 3.4115 | 31 | 0.8 | 8760 | 159540.4546 | 0 | 168188.293 | 65533.1035 | 199668.8608 | 33420 | 105830 | 75195 | 66840 | 34889.8259 | 8760 | 1482.4089 | 12316.4654 | 0 | 0 | 1678.1185 | 18232.301 | 3322.8708 | -1184.6203 | 1667.6871 | 2669.288 | 8760 | 2717.8952 | 1771.8521 | 946.043 | 2719.3731 | 21751.8493 | 5107.5104 | 7535.6435 | 4840.3576 | 0 | 10477.5031 | 8760 | 9089.889 | 173.45 | 383.55 | 1024.225 | 983348.153 | 210834.9497 | 2636.625
518 | C | SOK | TOU | FC | FP | WC | R100 | 3.4115 | 31 | 1.55 | 8760 | 163648.9527 | 0 | 163750.0889 | 65533.1035 | 199668.8608 | 33246 | 105279 | 74803.5 | 66492 | 34431.5608 | 8760 | 1482.4089 | 13244.1031 | 0 | 0 | 1555.0697 | 17617.6709 | 3209.3798 | -1229.8867 | 1766.728 | 2607.9612 | 8760 | 2717.875 | 1725.8556 | 992.0194 | 2719.3731 | 21751.8493 | 5138.1536 | 7525.5804 | 4831.9171 | 0 | 11462.2995 | 8760 | 9080.8377 | 187.625 | 366.475 | 1024.225 | 983409.2463 | 210834.9497 | 2621.5
519 | C | SOK | TOU | FC | FP | WC | R100 | 3.4115 | 31 | 2.35 | 8760 | 165047.2796 | 0 | 160953.5254 | 65533.1035 | 199668.8608 | 33373.5 | 105682.75 | 75090.375 | 66747 | 33858.3911 | 8760 | 1482.4089 | 13681.5257 | 0 | 0 | 1499.4077 | 17317.3066 | 3113.7171 | -1243.0691 | 1865.2344 | 2567.2356 | 8760 | 2718.7271 | 1686.1561 | 1032.5709 | 2719.3731 | 21751.8493 | 5145.3651 | 7539.0852 | 4846.0522 | 0 | 11933.9269 | 8760 | 9096.7204 | 202.05 | 354.175 | 1024.225 | 983679.6937 | 210834.9497 | 2625.15
520 | C | SOK | TOU | FC | FP | WC | R10 | 3.4115 | 38 | 0.95 | 8760 | 165585.037 | 0 | 163599.349 | 65533.1035 | 199668.8608 | 33312 | 105488 | 74952 | 66624 | 35482.3981 | 8760 | 1482.4089 | 13508.9961 | 0 | 0 | 1587.2594 | 17472.9185 | 3093.1879 | -1226.7331 | 1884.0406 | 2687.4602 | 8760 | 2718.7264 | 1657.1602 | 1061.5662 | 2719.3731 | 21751.8493 | 5138.2903 | 7548.3913 | 4850.3485 | 0 | 11624.2032 | 8760 | 9102.2608 | 196.825 | 358.375 | 1024.225 | 983471.4257 | 210834.9497 | 2753.85
521 | C | SOK | TOU | FC | FP | WC | R10 | 3.4115 | 38 | 1.9 | 8760 | 170537.118 | 0 | 157243.5227 | 65533.1035 | 199668.8608 | 33181.5 | 105074.75 | 74658.375 | 66363 | 34585.1905 | 8760 | 1482.4089 | 14648.1561 | 0 | 0 | 1452.9104 | 16744.5317 | 2878.754 | -1276.3009 | 2082.6585 | 2618.4984 | 8760 | 2718.8682 | 1565.3272 | 1153.5411 | 2719.3731 | 21751.8493 | 5175.5735 | 7544.6242 | 4850.4695 | 0 | 12825.1318 | 8760 | 9098.727 | 223.95 | 329.075 | 1024.225 | 983573.01 | 210834.9497 | 2739.25
522 | C | SOK | TOU | FC | FP | WC | R10 | 3.4115 | 38 | 2.85 | 8760 | 172772.2318 | 0 | 155089.6663 | 65533.1035 | 199668.8608 | 33109.5 | 104846.75 | 74496.375 | 66219 | 34087.3237 | 8760 | 1482.4089 | 15189.9977 | 0 | 0 | 1421.6304 | 16349.1143 | 2771.0052 | -1288.0479 | 2181.5526 | 2587.4781 | 8760 | 2718.8307 | 1518.4002 | 1200.4305 | 2719.3731 | 21751.8493 | 5182.8348 | 7544.6714 | 4851.4889 | 0 | 13393.1036 | 8760 | 9099.5589 | 237.45 | 314.375 | 1024.225 | 983579.4776 | 210834.9497 | 2730.675
523 | C | SOK | TOU | FC | FP | WC | R10 | 3.4115 | 44.5 | 1.1 | 8760 | 172819.7156 | 0 | 159147.6458 | 65533.1035 | 199668.8608 | 33288 | 105412 | 74898 | 66576 | 35132.3369 | 8760 | 1482.4089 | 14481.5104 | 0 | 0 | 1511.3432 | 16840.0519 | 2867.6061 | -1258.5856 | 2105.5248 | 2692.0511 | 8760 | 2718.1656 | 1537.504 | 1180.6616 | 2719.3731 | 21751.8493 | 5161.6307 | 7560.0737 | 4864.2265 | 0 | 12573.5301 | 8760 | 9108.7163 | 220.4 | 334.4 | 1024.225 | 983358.6581 | 210834.9497 | 2848.45
524 | C | SOK | TOU | FC | FP | WC | R10 | 3.4115 | 44.5 | 2.25 | 8760 | 177125.7381 | 0 | 152741.5729 | 65533.1035 | 199668.8608 | 33012 | 104538 | 74277 | 66024 | 34013.7446 | 8760 | 1482.4089 | 15756.9154 | 0 | 0 | 1372.9208 | 16037.5337 | 2600.0756 | -1309.5119 | 2346.7981 | 2615.1614 | 8760 | 2717.712 | 1423.2955 | 1294.4164 | 2719.3731 | 21751.8493 | 5200.6335 | 7549.2565 | 4856.2443 | 0 | 13915.3962 | 8760 | 9098.4419 | 252.825 | 297.375 | 1024.225 | 983392.363 | 210834.9497 | 2848.925
525 | C | SOK | TOU | FC | FP | WC | R10 | 3.4115 | 44.5 | 3.35 | 8760 | 179510.4945 | 0 | 149744.0227 | 65533.1035 | 199668.8608 | 32697 | 103540.5 | 73568.25 | 65394 | 34011.4922 | 8760 | 1482.4089 | 16393.6723 | 0 | 0 | 1362.9925 | 15645.582 | 2420.572 | -1322.0285 | 2503.9615 | 2583.5888 | 8760 | 2718.2626 | 1346.6171 | 1371.6455 | 2719.3731 | 21751.8493 | 5209.4457 | 7536.956 | 4845.8362 | 0 | 14577.3672 | 8760 | 9088.9205 | 272.725 | 272.225 | 1024.225 | 983469.6863 | 210834.9497 | 2844.625
526 | C | SOK | TOU | FC | FP | WC | R600 | 3.8882 | 18 | 0.45 | 8760 | 151902.1611 | 0 | 167048.369 | 65533.1035 | 136175.3067 | 41761.5 | 132244.75 | 93963.375 | 83523 | 39112.7251 | 8760 | 1475.3019 | 8954.9599 | 0 | 0 | 1928.6529 | 12105.0355 | 5017.288 | -1095.2268 | 1085.661 | 2539.4427 | 8760 | 3331.0684 | 2730.8621 | 600.2064 | 3332.6921 | 13065.0481 | 5500.9903 | 9264.2178 | 5932.1223 | 0 | 7229.6951 | 8760 | 11110.5206 | 118.75 | 577.275 | 1166.025 | 1190986.6738 | 189624.8638 | 2355.2
527 | C | SOK | TOU | FC | FP | WC | R600 | 3.8882 | 18 | 0.9 | 8760 | 155769.813 | 0 | 164645.5292 | 65533.1035 | 136175.3067 | 41811 | 132401.5 | 94074.75 | 83622 | 39212.9509 | 8760 | 1475.3019 | 9488.3127 | 0 | 0 | 1701.5718 | 11866.9892 | 5048.8852 | -1159.9707 | 1046.8343 | 2492.6097 | 8760 | 3331.0759 | 2756.6889 | 574.387 | 3332.6921 | 13065.0481 | 5572.4671 | 9265.1571 | 5932.4662 | 0 | 7805.6201 | 8760 | 11113.5815 | 116.175 | 580.675 | 1166.025 | 1191029.7742 | 189624.8638 | 2335.15
528 | C | SOK | TOU | FC | FP | WC | R600 | 3.8882 | 18 | 1.35 | 8760 | 157028.6535 | 0 | 163666.0945 | 65533.1035 | 136175.3067 | 41770.5 | 132273.25 | 93983.625 | 83541 | 39221.8001 | 8760 | 1475.3019 | 9685.1389 | 0 | 0 | 1645.1642 | 11765.7298 | 5041.6738 | -1182.6551 | 1052.3775 | 2469.3993 | 8760 | 3331.2354 | 2761.264 | 569.9714 | 3332.6921 | 13065.0481 | 5593.6838 | 9263.4006 | 5930.6747 | 0 | 8024.1765 | 8760 | 11112.21 | 118.825 | 577.35 | 1166.025 | 1191164.7038 | 189624.8638 | 2336.25
529 | C | SOK | TOU | FC | FP | WC | R600 | 3.8882 | 24.5 | 0.6 | 8760 | 154632.4599 | 0 | 161048.769 | 65533.1035 | 136175.3067 | 41526 | 131499 | 93433.5 | 83052 | 39201.4683 | 8760 | 1475.3019 | 10545.7893 | 0 | 0 | 1709.7872 | 11558.9211 | 4599.216 | -1183.4467 | 1514.7536 | 2605.7051 | 8760 | 3332.1946 | 2486.5589 | 845.6358 | 3332.6921 | 13065.0481 | 5588.4372 | 9273.5454 | 5941.4814 | 0 | 8710.7724 | 8760 | 11114.6071 | 162.625 | 529.475 | 1166.025 | 1191162.5642 | 189624.8638 | 2520.275
530 | C | SOK | TOU | FC | FP | WC | R600 | 3.8882 | 24.5 | 1.25 | 8760 | 158698.2989 | 0 | 157444.5093 | 65533.1035 | 136175.3067 | 41511 | 131451.5 | 93399.75 | 83022 | 39024.0901 | 8760 | 1475.3019 | 11265.1519 | 0 | 0 | 1546.2336 | 11211.5094 | 4521.2503 | -1248.1539 | 1590.1277 | 2553.3451 | 8760 | 3331.3437 | 2459.652 | 871.6917 | 3332.6921 | 13065.0481 | 5659.5147 | 9273.4663 | 5943.0494 | 0 | 9477.5663 | 8760 | 11115.8261 | 175.325 | 516.525 | 1166.025 | 1191025.783 | 189624.8638 | 2510.4
531 | C | SOK | TOU | FC | FP | WC | R600 | 3.8882 | 24.5 | 1.85 | 8760 | 159342.8703 | 0 | 155820.8676 | 65533.1035 | 136175.3067 | 41520 | 131480 | 93420 | 83040 | 38765.6454 | 8760 | 1475.3019 | 11505.4112 | 0 | 0 | 1519.4148 | 11027.2145 | 4497.2651 | -1267.846 | 1606.4135 | 2521.1827 | 8760 | 3331.9129 | 2464.4323 | 867.4806 | 3332.6921 | 13065.0481 | 5677.3884 | 9275.3992 | 5944.0829 | 0 | 9745.1349 | 8760 | 11122.61 | 181.175 | 510.825 | 1166.025 | 1190989.9416 | 189624.8638 | 2522.4
532 | C | SOK | TOU | FC | FP | WC | R600 | 3.8882 | 31 | 0.8 | 8760 | 157456.0522 | 0 | 155580.1336 | 65533.1035 | 136175.3067 | 40881 | 129456.5 | 91982.25 | 81762 | 40829.5958 | 8760 | 1475.3019 | 11694.9852 | 0 | 0 | 1553.1569 | 11026.0783 | 4257.4824 | -1253.0745 | 1828.1272 | 2635.2039 | 8760 | 3327.2168 | 2295.2977 | 1031.9191 | 3332.6921 | 13065.0481 | 5657.0188 | 9240.4729 | 5915.8434 | 0 | 9795.863 | 8760 | 11071.2361 | 192.175 | 489.175 | 1166.025 | 1191167.3964 | 189624.8638 | 2670.8
533 | C | SOK | TOU | FC | FP | WC | R600 | 3.8882 | 31 | 1.55 | 8760 | 160406.0796 | 0 | 151636.1466 | 65533.1035 | 136175.3067 | 40758 | 129067 | 91705.5 | 81516 | 39472.7219 | 8760 | 1475.3019 | 12441.1034 | 0 | 0 | 1447.4356 | 10629.6953 | 4065.2781 | -1306.1868 | 2000.3783 | 2576.0841 | 8760 | 3332.3668 | 2219.2329 | 1113.1339 | 3332.6921 | 13065.0481 | 5713.2375 | 9250.7677 | 5921.7444 | 0 | 10595.2494 | 8760 | 11085.3388 | 215.025 | 464.275 | 1166.025 | 1191182.3725 | 189624.8638 | 2676.875
534 | C | SOK | TOU | FC | FP | WC | R600 | 3.8882 | 31 | 2.35 | 8760 | 162216.8384 | 0 | 149669.0277 | 65533.1035 | 136175.3067 | 40713 | 128924.5 | 91604.25 | 81426 | 39493.3479 | 8760 | 1475.3019 | 12848.3682 | 0 | 0 | 1418.2339 | 10397.6533 | 3960.0518 | -1324.2188 | 2100.5938 | 2541.9721 | 8760 | 3330.6265 | 2171.9193 | 1158.7071 | 3332.6921 | 13065.0481 | 5728.1508 | 9244.965 | 5918.7746 | 0 | 11031.4306 | 8760 | 11080.9573 | 229.65 | 448.9 | 1166.025 | 1191208.0323 | 189624.8638 | 2676.25
535 | C | SOK | TOU | FC | FP | WC | R60 | 3.8882 | 38 | 0.95 | 8760 | 162219.5972 | 0 | 151003.9387 | 65533.1035 | 136175.3067 | 40569 | 128468.5 | 91280.25 | 81138 | 40990.3016 | 8760 | 1475.3019 | 12681.3873 | 0 | 0 | 1447.5752 | 10556.5729 | 3892.2637 | -1297.8085 | 2162.3385 | 2651.1153 | 8760 | 3332.494 | 2118.9435 | 1213.5506 | 3332.6921 | 13065.0481 | 5698.6952 | 9257.2997 | 5927.6502 | 0 | 10740.7483 | 8760 | 11082.5812 | 226.975 | 449.175 | 1166.025 | 1191074.0913 | 189624.8638 | 2802.1
536 | C | SOK | TOU | FC | FP | WC | R60 | 3.8882 | 38 | 1.9 | 8760 | 165566.4055 | 0 | 146489.9897 | 65533.1035 | 136175.3067 | 40578 | 128497 | 91300.5 | 81156 | 39748.8009 | 8760 | 1475.3019 | 13635.1124 | 0 | 0 | 1348.0541 | 10064.6519 | 3654.2451 | -1349.7143 | 2395.3039 | 2578.3075 | 8760 | 3332.5299 | 2013.5918 | 1318.9381 | 3332.6921 | 13065.0481 | 5749.0737 | 9263.2595 | 5935.7036 | 0 | 11757.3262 | 8760 | 11095.5252 | 260.15 | 416.15 | 1166.025 | 1191205.9922 | 189624.8638 | 2810.55
537 | C | SOK | TOU | FC | FP | WC | R60 | 3.8882 | 38 | 2.85 | 8760 | 167056.2093 | 0 | 143626.6806 | 65533.1035 | 136175.3067 | 40368 | 127832 | 90828 | 80736 | 39730.3065 | 8760 | 1475.3019 | 14101.575 | 0 | 0 | 1323.7932 | 9792.0438 | 3493.7035 | -1366.8638 | 2536.0193 | 2541.5474 | 8760 | 3332.1576 | 1939.1834 | 1392.9741 | 3332.6921 | 13065.0481 | 5764.5994 | 9253.1289 | 5926.1021 | 0 | 12253.4423 | 8760 | 11088.0423 | 277.325 | 395.475 | 1166.025 | 1191125.3626 | 189624.8638 | 2815.7
538 | C | SOK | TOU | FC | FP | WC | R60 | 3.8882 | 44.5 | 1.1 | 8760 | 168096.4982 | 0 | 147598.4158 | 65533.1035 | 136175.3067 | 40570.5 | 128473.25 | 91283.625 | 81141 | 40400.3568 | 8760 | 1475.3019 | 13478.1084 | 0 | 0 | 1370.4647 | 10142.024 | 3639.8059 | -1330.1913 | 2414.4403 | 2641.6827 | 8760 | 3332.5195 | 1985.6643 | 1346.8552 | 3332.6921 | 13065.0481 | 5730.5879 | 9273.7839 | 5943.624 | 0 | 11526.3434 | 8760 | 11094.0496 | 255.05 | 421.125 | 1166.025 | 1191213.3673 | 189624.8638 | 2906.675
539 | C | SOK | TOU | FC | FP | WC | R60 | 3.8882 | 44.5 | 2.25 | 8760 | 172473.6104 | 0 | 141690.3097 | 65533.1035 | 136175.3067 | 40260 | 127490 | 90585 | 80520 | 39771.8234 | 8760 | 1475.3019 | 14629.1141 | 0 | 0 | 1272.3077 | 9560.047 | 3284.3335 | -1380.9661 | 2736.664 | 2577.3316 | 8760 | 3332.4627 | 1833.2099 | 1499.2527 | 3332.6921 | 13065.0481 | 5773.8921 | 9264.3994 | 5937.3465 | 0 | 12732.0143 | 8760 | 11092.1823 | 298.35 | 372.65 | 1166.025 | 1191173.7695 | 189624.8638 | 2908.05
540 | C | SOK | TOU | FC | FP | WC | R60 | 3.8882 | 44.5 | 3.35 | 8760 | 174686.1717 | 0 | 138813.5015 | 65533.1035 | 136175.3067 | 40128 | 127072 | 90288 | 80256 | 39252.2757 | 8760 | 1475.3019 | 15178.0011 | 0 | 0 | 1227.7208 | 9267.4271 | 3099.7867 | -1397.431 | 2913.0904 | 2544.7 | 8760 | 3332.2994 | 1741.7672 | 1590.5322 | 3332.6921 | 13065.0481 | 5787.1507 | 9262.6071 | 5935.7513 | 0 | 13304.9947 | 8760 | 11093.3334 | 319.85 | 348.95 | 1166.025 | 1191248.2362 | 189624.8638 | 2903.175
541 | C | SOK | TOU | CC | FP | WC | R600 | 5.4272 | 23 | 0.6 | 8760 | 159908.8037 | 0 | 162355.9319 | 65533.1035 | 162408.4576 | 33901.5 | 107354.75 | 76278.375 | 67803 | 57625.444 | 8760 | 1475.3019 | 10937.7677 | 0 | 0 | 2434.1056 | 16739.3181 | 4935.8314 | -1133.9045 | 1431.7043 | 2546.0926 | 8760 | 4333.8033 | 3362.8556 | 970.9476 | 4338.0557 | 18236.4195 | 6955.8152 | 10564.632 | 6229.0999 | 0 | 9163.6567 | 8760 | 12694.3439 | 124.725 | 440.3 | 1048.625 | 1390758.668 | 189624.8638 | 2410.875
542 | C | SOK | TOU | CC | FP | WC | R600 | 5.4272 | 23 | 1.15 | 8760 | 164339.1058 | 0 | 160085.8332 | 65533.1035 | 162408.4576 | 33838.5 | 107155.25 | 76136.625 | 67677 | 58386.152 | 8760 | 1475.3019 | 11586.9309 | 0 | 0 | 2212.2457 | 16417.4193 | 4961.5041 | -1190.6705 | 1405.0409 | 2502.6475 | 8760 | 4334.7361 | 3394.109 | 940.6271 | 4338.0557 | 18236.4195 | 7043.3333 | 10562.7886 | 6225.796 | 0 | 9852.7336 | 8760 | 12692.9164 | 126.625 | 437.35 | 1048.625 | 1390846.2135 | 189624.8638 | 2384.825
543 | C | SOK | TOU | CC | FP | WC | R600 | 5.4272 | 23 | 1.75 | 8760 | 165249.5067 | 0 | 159218.891 | 65533.1035 | 162408.4576 | 33922.5 | 107421.25 | 76325.625 | 67845 | 58243.7999 | 8760 | 1475.3019 | 11854.8264 | 0 | 0 | 2168.8875 | 16246.3842 | 4949.8195 | -1211.5996 | 1423.1724 | 2472.398 | 8760 | 4334.9025 | 3393.5505 | 941.352 | 4338.0557 | 18236.4195 | 7071.2487 | 10569.9661 | 6232.1931 | 0 | 10146.7291 | 8760 | 12703.9112 | 131.8 | 433.575 | 1048.625 | 1390764.9669 | 189624.8638 | 2395.65
544 | C | SOK | TOU | CC | FP | WC | R600 | 5.4272 | 32 | 0.8 | 8760 | 165688.6017 | 0 | 156421.5775 | 65533.1035 | 162408.4576 | 33768 | 106932 | 75978 | 67536 | 58593.0927 | 8760 | 1475.3019 | 12759.684 | 0 | 0 | 2187.7527 | 15961.3474 | 4490.0626 | -1222.3513 | 1895.9058 | 2602.3776 | 8760 | 4329.9665 | 3052.6186 | 1277.3479 | 4338.0557 | 18236.4195 | 7076.7256 | 10575.9428 | 6240.5969 | 0 | 10884.1217 | 8760 | 12699.65 | 165.775 | 397.025 | 1048.625 | 1390618.634 | 189624.8638 | 2603.825
545 | C | SOK | TOU | CC | FP | WC | R600 | 5.4272 | 32 | 1.6 | 8760 | 169578.9341 | 0 | 153088.7997 | 65533.1035 | 162408.4576 | 33571.5 | 106309.75 | 75535.875 | 67143 | 59335.2097 | 8760 | 1475.3019 | 13645.9244 | 0 | 0 | 2033.8679 | 15524.2866 | 4312.4679 | -1281.4691 | 2039.9643 | 2549.2563 | 8760 | 4334.4564 | 2970.3107 | 1364.1456 | 4338.0557 | 18236.4195 | 7163.0174 | 10574.9143 | 6238.1003 | 0 | 11816.0173 | 8760 | 12705.7412 | 183.2 | 376.325 | 1048.625 | 1390799.352 | 189624.8638 | 2604.6
546 | C | SOK | TOU | CC | FP | WC | R600 | 5.4272 | 32 | 2.4 | 8760 | 171412.6979 | 0 | 151196.6759 | 65533.1035 | 162408.4576 | 33543 | 106219.5 | 75471.75 | 67086 | 59467.2105 | 8760 | 1475.3019 | 14071.7909 | 0 | 0 | 2018.6026 | 15232.3729 | 4215.1432 | -1297.6791 | 2132.5723 | 2515.8981 | 8760 | 4333.1213 | 2912.5464 | 1420.575 | 4338.0557 | 18236.4195 | 7180.0624 | 10572.748 | 6238.03 | 0 | 12268.9469 | 8760 | 12707.9651 | 193.95 | 365.1 | 1048.625 | 1390699.7914 | 189624.8638 | 2601.225
547 | C | SOK | TOU | CC | FP | WC | R600 | 5.4272 | 40.5 | 1 | 8760 | 173093.9323 | 0 | 151651.1456 | 65533.1035 | 162408.4576 | 33493.5 | 106062.75 | 75360.375 | 66987 | 58720.5874 | 8760 | 1475.3019 | 14111.0811 | 0 | 0 | 2040.342 | 15291.7798 | 4037.4846 | -1275.061 | 2322.6674 | 2619.8147 | 8760 | 4333.195 | 2770.8729 | 1562.3221 | 4338.0557 | 18236.4195 | 7146.1183 | 10592.1871 | 6255.6085 | 0 | 12187.5917 | 8760 | 12708.2108 | 201.5 | 356.725 | 1048.625 | 1390766.9933 | 189624.8638 | 2756.9
548 | C | SOK | TOU | CC | FP | WC | R600 | 5.4272 | 40.5 | 2.05 | 8760 | 177739.9709 | 0 | 147470.1743 | 65533.1035 | 162408.4576 | 33445.5 | 105910.75 | 75252.375 | 66891 | 58348.306 | 8760 | 1475.3019 | 15222.0327 | 0 | 0 | 1914.409 | 14705.8385 | 3797.2592 | -1333.4041 | 2550.0119 | 2555.8961 | 8760 | 4334.0652 | 2632.4285 | 1701.6367 | 4338.0557 | 18236.4195 | 7225.097 | 10598.9373 | 6263.1286 | 0 | 13351.245 | 8760 | 12727.4075 | 226.45 | 330.975 | 1048.625 | 1390715.2602 | 189624.8638 | 2753.125
549 | C | SOK | TOU | CC | FP | WC | R600 | 5.4272 | 40.5 | 3.05 | 8760 | 180194.7793 | 0 | 145011.8383 | 65533.1035 | 162408.4576 | 33486 | 106039 | 75343.5 | 66972 | 58490.6637 | 8760 | 1475.3019 | 15854.9979 | 0 | 0 | 1894.2122 | 14343.2079 | 3615.7171 | -1348.6768 | 2732.741 | 2515.8206 | 8760 | 4333.5111 | 2518.1931 | 1815.318 | 4338.0557 | 18236.4195 | 7241.0713 | 10602.0782 | 6268.6995 | 0 | 14013.9978 | 8760 | 12737.8894 | 246.975 | 311.125 | 1048.625 | 1390741.8156 | 189624.8638 | 2748.875
550 | C | SOK | TOU | CC | FP | WC | R60 | 5.4272 | 49 | 1.25 | 8760 | 183775.8437 | 0 | 147140.9463 | 65533.1035 | 162408.4576 | 33343.5 | 105587.75 | 75022.875 | 66687 | 57426.8084 | 8760 | 1475.3019 | 15336.8015 | 0 | 0 | 1904.0014 | 14666.1296 | 3625.4763 | -1320.6427 | 2726.3121 | 2613.9053 | 8760 | 4336.9027 | 2511.9031 | 1824.9995 | 4338.0557 | 18236.4195 | 7204.5321 | 10620.8626 | 6282.2137 | 0 | 13393.0307 | 8760 | 12734.6729 | 235.9 | 319.825 | 1048.625 | 1390903.0535 | 189624.8638 | 2875.625
551 | C | SOK | TOU | CC | FP | WC | R60 | 5.4272 | 49 | 2.45 | 8760 | 188662.9095 | 0 | 142669.7444 | 65533.1035 | 162408.4576 | 33336 | 105564 | 75006 | 66672 | 57435.2937 | 8760 | 1475.3019 | 16594.0251 | 0 | 0 | 1804.0115 | 14005.2073 | 3261.307 | -1367.1929 | 3077.0039 | 2556.1797 | 8760 | 4334.7766 | 2292.2833 | 2042.4934 | 4338.0557 | 18236.4195 | 7260.1365 | 10624.8387 | 6290.4091 | 0 | 14697.3397 | 8760 | 12748.9952 | 274.3 | 281.3 | 1048.625 | 1390723.3953 | 189624.8638 | 2871.9
552 | C | SOK | TOU | CC | FP | WC | R60 | 5.4272 | 49 | 3.7 | 8760 | 191061.3821 | 0 | 139543.2029 | 65533.1035 | 162408.4576 | 33493.5 | 106062.75 | 75360.375 | 66987 | 56931.1644 | 8760 | 1475.3019 | 17325.8423 | 0 | 0 | 1791.479 | 13550.432 | 3023.5805 | -1381.4698 | 3325.0687 | 2511.6171 | 8760 | 4336.2239 | 2131.8755 | 2204.3484 | 4338.0557 | 18236.4195 | 7277.3756 | 10644.6941 | 6309.7863 | 0 | 15462.8776 | 8760 | 12782.592 | 297.95 | 260.275 | 1048.625 | 1390855.7313 | 189624.8638 | 2872.45
553 | C | SOK | TOU | CC | FP | WC | R60 | 5.4272 | 58 | 1.45 | 8760 | 196867.22 | 0 | 143795.4194 | 65533.1035 | 162408.4576 | 33349.5 | 105606.75 | 75036.375 | 66699 | 56309.8293 | 8760 | 1475.3019 | 16403.5894 | 0 | 0 | 1808.4956 | 14101.3856 | 3330.3205 | -1350.3044 | 3035.0522 | 2602.2977 | 8760 | 4336.6424 | 2317.2689 | 2019.3735 | 4338.0557 | 18236.4195 | 7241.8221 | 10641.7107 | 6304.2383 | 0 | 14445.4501 | 8760 | 12754.4319 | 264.6 | 291.225 | 1048.625 | 1390896.7221 | 189624.8638 | 2986.9
554 | C | SOK | TOU | CC | FP | WC | R60 | 5.4272 | 58 | 2.9 | 8760 | 202577.0641 | 0 | 138204.5421 | 65533.1035 | 162408.4576 | 33514.5 | 106129.25 | 75407.625 | 67029 | 55662.2442 | 8760 | 1475.3019 | 17851.296 | 0 | 0 | 1701.8955 | 13306.596 | 2890.4894 | -1396.7701 | 3483.2454 | 2540.1811 | 8760 | 4337.3444 | 2037.4741 | 2299.8703 | 4338.0557 | 18236.4195 | 7291.9576 | 10665.807 | 6331.071 | 0 | 15945.8839 | 8760 | 12796.8292 | 311.35 | 247.225 | 1048.625 | 1390868.0013 | 189624.8638 | 2980.65
555 | C | SOK | TOU | CC | FP | WC | R60 | 5.4272 | 58 | 4.35 | 8760 | 205600.6824 | 0 | 134845.5161 | 65533.1035 | 162408.4576 | 33690 | 106685 | 75802.5 | 67380 | 55858.3205 | 8760 | 1475.3019 | 18675.1523 | 0 | 0 | 1663.9524 | 12832.7668 | 2605.056 | -1409.2088 | 3762.6429 | 2500.6149 | 8760 | 4334.2307 | 1857.7187 | 2476.5119 | 4338.0557 | 18236.4195 | 7304.418 | 10678.9819 | 6349.6974 | 0 | 16800.1332 | 8760 | 12816.6757 | 339.375 | 222.125 | 1048.625 | 1390737.6129 | 189624.8638 | 2972.825
556 | C | SOK | TOU | FC | ET | WC | OFF0 | 0.39259 | 18 | 0.45 | 8760 | 157918.253 | 0 | 140860.865 | 0 | 82698.0092 | 67102.5 | 212491.25 | 150980.625 | 134205 | 75059.8017 | 8760 | 1475.304 | 9922.0767 | 0 | 0 | 0 | 2925.8158 | 6245.578 | -1381.7 | 4380.299 | 3306.4262 | 8760 | 6117.5623 | 3583.4148 | 2534.1475 | 6118.3717 | 4097.4792 | 0 | 16530.6913 | 10406.9896 | 0 | 7523.1134 | 8760 | 20226.6112 | 453.05 | 665.325 | 1821 | 2220321.8024 | 155421.1442 | 2184.55
557 | C | SOK | TOU | FC | ET | WC | OFF0 | 0.39259 | 18 | 0.9 | 8760 | 160813.7613 | 0 | 137423.0942 | 0 | 82698.0092 | 67267.5 | 213013.75 | 151351.875 | 134535 | 74248.5412 | 8760 | 1475.304 | 10186.4529 | 0 | 0 | 0 | 2732.696 | 6193.433 | -1403.556 | 4444.4311 | 3280.3882 | 8760 | 6117.0542 | 3554.0156 | 2563.0386 | 6118.3717 | 4097.4792 | 0 | 16540.3268 | 10418.687 | 0 | 7812.3632 | 8760 | 20240.0967 | 462.15 | 658.975 | 1821 | 2219996.5405 | 155421.1442 | 2148.75
558 | C | SOK | TOU | FC | ET | WC | OFF0 | 0.39259 | 18 | 1.35 | 8760 | 162599.9276 | 0 | 135119.2478 | 0 | 82698.0092 | 67306.5 | 213137.25 | 151439.625 | 134613 | 74468.6314 | 8760 | 1475.304 | 10354.6169 | 0 | 0 | 0 | 2648.4512 | 6128.0001 | -1411.0237 | 4510.9864 | 3270.2245 | 8760 | 6116.7983 | 3518.81 | 2597.9883 | 6118.3717 | 4097.4792 | 0 | 16542.4887 | 10422.593 | 0 | 7993.3829 | 8760 | 20242.6396 | 470.375 | 651.4 | 1821 | 2219844.2913 | 155421.1442 | 2128.5
559 | C | SOK | TOU | FC | ET | WC | OFF0 | 0.39259 | 24.5 | 0.6 | 8760 | 161120.0074 | 0 | 130055.5854 | 0 | 82698.0092 | 67042.5 | 212301.25 | 150845.625 | 134085 | 75544.477 | 8760 | 1475.304 | 12066.2258 | 0 | 0 | 0 | 2487.8677 | 5100.0399 | -1445.3319 | 5627.5917 | 3380.055 | 8760 | 6117.4017 | 2856.1814 | 3261.2204 | 6118.3717 | 4097.4792 | 0 | 16597.4175 | 10474.4556 | 0 | 9558.4458 | 8760 | 20287.8344 | 574.3 | 543.075 | 1821 | 2219983.0723 | 155421.1442 | 2341.35
560 | C | SOK | TOU | FC | ET | WC | OFF0 | 0.39259 | 24.5 | 1.25 | 8760 | 164958.2156 | 0 | 124688.1933 | 0 | 82698.0092 | 67273.5 | 213032.75 | 151365.375 | 134547 | 74389.562 | 8760 | 1475.304 | 12462.8769 | 0 | 0 | 0 | 2240.2788 | 4830.9907 | -1468.6181 | 5889.884 | 3359.2084 | 8760 | 6117.5808 | 2719.6423 | 3397.9386 | 6118.3717 | 4097.4792 | 0 | 16625.4855 | 10505.5527 | 0 | 9976.2679 | 8760 | 20313.8995 | 603.975 | 517.25 | 1821 | 2220225.9 | 155421.1442 | 2294.775
561 | C | SOK | TOU | FC | ET | WC | OFF0 | 0.39259 | 24.5 | 1.85 | 8760 | 166640.5157 | 0 | 123752.2557 | 0 | 82698.0092 | 67399.5 | 213431.75 | 151648.875 | 134799 | 73570.6176 | 8760 | 1475.304 | 12631.7838 | 0 | 0 | 0 | 2189.1705 | 4731.1876 | -1477.4016 | 6002.3052 | 3354.4963 | 8760 | 6116.8554 | 2658.0073 | 3458.8481 | 6118.3717 | 4097.4792 | 0 | 16635.1081 | 10517.2124 | 0 | 10150.6622 | 8760 | 20320.2043 | 616.675 | 506.65 | 1821 | 2220362.7477 | 155421.1442 | 2275.85
562 | C | SOK | TOU | FC | ET | WC | OFF0 | 0.39259 | 31 | 0.8 | 8760 | 161463.9057 | 0 | 120516.2214 | 0 | 82698.0092 | 66096 | 209304 | 148716 | 132192 | 80457.5302 | 8760 | 1475.304 | 13331.0949 | 0 | 0 | 0 | 2085.6162 | 4125.9458 | -1489.1985 | 6603.7112 | 3421.4717 | 8760 | 6117.2704 | 2261.578 | 3855.6925 | 6118.3717 | 4097.4792 | 0 | 16603.3696 | 10484.2821 | 0 | 10754.4447 | 8760 | 20270.1351 | 658.525 | 443.075 | 1821 | 2220150.9417 | 155421.1442 | 2507
563 | C | SOK | TOU | FC | ET | WC | OFF0 | 0.39259 | 31 | 1.55 | 8760 | 165980 | 0 | 115758.5386 | 0 | 82698.0092 | 66439.5 | 210391.75 | 149488.875 | 132879 | 78590.6422 | 8760 | 1475.304 | 13836.921 | 0 | 0 | 0 | 1871.1741 | 3808.0451 | -1516.8589 | 6920.4011 | 3410.4682 | 8760 | 6117.5814 | 2098.1865 | 4019.3949 | 6118.3717 | 4097.4792 | 0 | 16643.7137 | 10525.6082 | 0 | 11269.0879 | 8760 | 20309.1426 | 695.2 | 412.125 | 1821 | 2220138.6718 | 155421.1442 | 2459.1
564 | C | SOK | TOU | FC | ET | WC | OFF0 | 0.39259 | 31 | 2.35 | 8760 | 169038.3544 | 0 | 113430.6938 | 0 | 82698.0092 | 66397.5 | 210258.75 | 149394.375 | 132795 | 77423.4399 | 8760 | 1475.304 | 14177.5272 | 0 | 0 | 0 | 1768.7979 | 3523.7716 | -1527.7866 | 7197.6108 | 3406.215 | 8760 | 6116.2959 | 1952.6113 | 4163.6846 | 6118.3717 | 4097.4792 | 0 | 16652.9223 | 10538.6226 | 0 | 11611.0647 | 8760 | 20309.8966 | 727.05 | 379.575 | 1821 | 2220069.5667 | 155421.1442 | 2428.4
565 | C | SOK | TOU | FC | ET | WC | OFF | 0.39259 | 38 | 0.95 | 8760 | 162427.6591 | 0 | 113318.2013 | 0 | 82698.0092 | 64902 | 205523 | 146029.5 | 129804 | 84770.6181 | 8760 | 1475.304 | 14245.8675 | 0 | 0 | 0 | 1749.3554 | 3293.5956 | -1526.1838 | 7364.5129 | 3447.9268 | 8760 | 6116.5527 | 1794.359 | 4322.1938 | 6118.3717 | 4097.4792 | 0 | 16591.8408 | 10475.1159 | 0 | 11618.9213 | 8760 | 20236.9976 | 721.475 | 360.225 | 1821 | 2219909.7448 | 155421.1442 | 2673.175
566 | C | SOK | TOU | FC | ET | WC | OFF | 0.39259 | 38 | 1.9 | 8760 | 168745.2316 | 0 | 107399.5959 | 0 | 82698.0092 | 65266.5 | 206677.25 | 146849.625 | 130533 | 83102.8242 | 8760 | 1475.304 | 14977.9429 | 0 | 0 | 0 | 1493.1506 | 2829.9819 | -1554.2797 | 7848.9257 | 3435.3123 | 8760 | 6117.3902 | 1545.5545 | 4571.8357 | 6118.3717 | 4097.4792 | 0 | 16635.1574 | 10521.8296 | 0 | 12356.1219 | 8760 | 20280.1125 | 778.925 | 308.85 | 1821 | 2220328.2686 | 155421.1442 | 2612.275
567 | C | SOK | TOU | FC | ET | WC | OFF | 0.39259 | 38 | 2.85 | 8760 | 172798.9087 | 0 | 104018.0714 | 0 | 82698.0092 | 65619 | 207793.5 | 147642.75 | 131238 | 81069.4431 | 8760 | 1475.304 | 15478.0084 | 0 | 0 | 0 | 1384.6417 | 2466.3122 | -1561.1895 | 8225.0431 | 3427.5326 | 8760 | 6117.5721 | 1365.672 | 4751.9001 | 6118.3717 | 4097.4792 | 0 | 16667.9725 | 10557.769 | 0 | 12857.5075 | 8760 | 20311.4364 | 828.95 | 264.7 | 1821 | 2219869.4438 | 155421.1442 | 2577.675
568 | C | SOK | TOU | FC | ET | WC | OFF | 0.39259 | 44.5 | 1.1 | 8760 | 166399.7147 | 0 | 107180.6105 | 0 | 82698.0092 | 64267.5 | 203513.75 | 144601.875 | 128535 | 85819.4959 | 8760 | 1475.304 | 15041.8208 | 0 | 0 | 0 | 1458.8396 | 2702.8518 | -1555.9629 | 7933.4603 | 3462.3211 | 8760 | 6116.7977 | 1456.6544 | 4660.1433 | 6118.3717 | 4097.4792 | 0 | 16606.1001 | 10490.6928 | 0 | 12386.1288 | 8760 | 20230.5542 | 769.35 | 301.775 | 1821 | 2219576.3648 | 155421.1442 | 2791.425
569 | C | SOK | TOU | FC | ET | WC | OFF | 0.39259 | 44.5 | 2.25 | 8760 | 174086.3612 | 0 | 99787.6034 | 0 | 82698.0092 | 64767 | 205095.5 | 145725.75 | 129534 | 83879.8541 | 8760 | 1475.304 | 16013.4015 | 0 | 0 | 0 | 1157.7173 | 2073.4321 | -1581.7339 | 8586.4561 | 3442.6504 | 8760 | 6116.6026 | 1140.721 | 4975.8816 | 6118.3717 | 4097.4792 | 0 | 16661.7046 | 10550.065 | 0 | 13361.6776 | 8760 | 20288.0918 | 853.95 | 225.5 | 1821 | 2219916.6376 | 155421.1442 | 2725.425
570 | C | SOK | TOU | FC | ET | WC | OFF | 0.39259 | 44.5 | 3.35 | 8760 | 177490.1884 | 0 | 96989.54 | 0 | 82698.0092 | 64485 | 204202.5 | 145091.25 | 128970 | 83734.9322 | 8760 | 1475.304 | 16415.9523 | 0 | 0 | 0 | 1028.0154 | 1839.6965 | -1593.7551 | 8791.0462 | 3436.1969 | 8760 | 6115.5706 | 1034.8371 | 5080.7335 | 6118.3717 | 4097.4792 | 0 | 16643.8284 | 10541.004 | 0 | 13765.5396 | 8760 | 20270.3783 | 879.025 | 195.725 | 1821 | 2219959.9208 | 155421.1442 | 2696
571 | C | SOK | TOU | FC | ET | WC | R100 | 3.4115 | 18 | 0.45 | 8760 | 162913.1111 | 0 | 181670.1442 | 65533.1035 | 199668.8608 | 34254 | 108471 | 77071.5 | 68508 | 34630.1761 | 8760 | 1482.4089 | 9389.0468 | 0 | 0 | 1975.0369 | 20173.6668 | 3921.6877 | -1073.2312 | 1082.4184 | 2865.9579 | 8760 | 2716.5002 | 2119.4667 | 597.0336 | 2719.3731 | 21751.8493 | 5021.9397 | 7546.7734 | 4850.9936 | 0 | 7449.0943 | 8760 | 9121.3644 | 120 | 450.9 | 1024.225 | 983458.8462 | 210834.9497 | 2099.125
572 | C | SOK | TOU | FC | ET | WC | R100 | 3.4115 | 18 | 0.9 | 8760 | 169474.2681 | 0 | 179645.2792 | 65533.1035 | 199668.8608 | 34251 | 108461.5 | 77064.75 | 68502 | 34587.6695 | 8760 | 1482.4089 | 9897.8111 | 0 | 0 | 1822.7921 | 19923.8637 | 3874.6706 | -1118.8756 | 1122.1129 | 2831.5003 | 8760 | 2716.472 | 2101.5394 | 614.9326 | 2719.3731 | 21751.8493 | 5059.494 | 7546.7047 | 4851.4114 | 0 | 7998.0912 | 8760 | 9123.7748 | 125.925 | 444.925 | 1024.225 | 983399.7646 | 210834.9497 | 2023.2
573 | C | SOK | TOU | FC | ET | WC | R100 | 3.4115 | 18 | 1.35 | 8760 | 172385.1741 | 0 | 178531.6034 | 65533.1035 | 199668.8608 | 34344 | 108756 | 77274 | 68688 | 34336.6132 | 8760 | 1482.4089 | 10108.3517 | 0 | 0 | 1797.7713 | 19796.5493 | 3848.4606 | -1134.3874 | 1159.3137 | 2813.668 | 8760 | 2717.2822 | 2087.1136 | 630.1686 | 2719.3731 | 21751.8493 | 5072.6217 | 7557.0241 | 4860.3415 | 0 | 8226.2318 | 8760 | 9136.2226 | 131.175 | 441.225 | 1024.225 | 983461.3966 | 210834.9497 | 1990.7
574 | C | SOK | TOU | FC | ET | WC | R100 | 3.4115 | 24.5 | 0.6 | 8760 | 165502.4413 | 0 | 174296.6358 | 65533.1035 | 199668.8608 | 34074 | 107901 | 76666.5 | 68148 | 34393.5271 | 8760 | 1482.4089 | 11355.8591 | 0 | 0 | 1799.8083 | 19311.9623 | 3387.6919 | -1154.1295 | 1624.471 | 2985.2607 | 8760 | 2717.4011 | 1819.0099 | 898.3912 | 2719.3731 | 21751.8493 | 5086.0815 | 7564.2054 | 4870.8257 | 0 | 9254.6914 | 8760 | 9135.8637 | 177.45 | 390.45 | 1024.225 | 983333.0687 | 210834.9497 | 2263.575
575 | C | SOK | TOU | FC | ET | WC | R100 | 3.4115 | 24.5 | 1.25 | 8760 | 173502.9148 | 0 | 171229.3403 | 65533.1035 | 199668.8608 | 34068 | 107882 | 76653 | 68136 | 33977.2597 | 8760 | 1482.4089 | 12048.283 | 0 | 0 | 1676.2055 | 18942.7488 | 3268.3343 | -1200.904 | 1743.5051 | 2960.2357 | 8760 | 2717.4898 | 1766.323 | 951.1668 | 2719.3731 | 21751.8493 | 5119.1401 | 7570.1132 | 4877.09 | 0 | 9977.3035 | 8760 | 9142.7348 | 193.825 | 373.975 | 1024.225 | 983538.5416 | 210834.9497 | 2173.025
576 | C | SOK | TOU | FC | ET | WC | R100 | 3.4115 | 24.5 | 1.85 | 8760 | 176703.1695 | 0 | 170033.92 | 65533.1035 | 199668.8608 | 34144.5 | 108124.25 | 76825.125 | 68289 | 33821.3416 | 8760 | 1482.4089 | 12327.9445 | 0 | 0 | 1643.2887 | 18806.5645 | 3163.8866 | -1210.2896 | 1850.0713 | 2951.7377 | 8760 | 2717.6257 | 1717.7476 | 999.8781 | 2719.3731 | 21751.8493 | 5120.3146 | 7580.3152 | 4888.035 | 0 | 10269.0358 | 8760 | 9154.8405 | 208.025 | 361.05 | 1024.225 | 983446.4895 | 210834.9497 | 2139.375
577 | C | SOK | TOU | FC | ET | WC | R100 | 3.4115 | 31 | 0.8 | 8760 | 169453.3187 | 0 | 168028.5537 | 65533.1035 | 199668.8608 | 33349.5 | 105606.75 | 75036.375 | 66699 | 35356.6535 | 8760 | 1482.4089 | 12905.8507 | 0 | 0 | 1654.5864 | 18475.2307 | 2948.117 | -1217.2221 | 2028.189 | 3052.1955 | 8760 | 2716.8857 | 1578.5852 | 1138.3005 | 2719.3731 | 21751.8493 | 5132.0272 | 7543.8793 | 4851.4538 | 0 | 10704.9682 | 8760 | 9105.6512 | 215.05 | 340.775 | 1024.225 | 983304.4936 | 210834.9497 | 2398.225
578 | C | SOK | TOU | FC | ET | WC | R100 | 3.4115 | 31 | 1.55 | 8760 | 177005.9442 | 0 | 164455.7919 | 65533.1035 | 199668.8608 | 33304.5 | 105464.25 | 74935.125 | 66609 | 34944.047 | 8760 | 1482.4089 | 13630.899 | 0 | 0 | 1554.623 | 18087.7104 | 2779.1324 | -1255.3238 | 2192.228 | 3038.5319 | 8760 | 2718.184 | 1506.3845 | 1211.7994 | 2719.3731 | 21751.8493 | 5157.1611 | 7549.8627 | 4858.6269 | 0 | 11447.2846 | 8760 | 9113.0742 | 237.6 | 317.475 | 1024.225 | 983431.5635 | 210834.9497 | 2319.75
579 | C | SOK | TOU | FC | ET | WC | R100 | 3.4115 | 31 | 2.35 | 8760 | 180878.91 | 0 | 162757.1551 | 65533.1035 | 199668.8608 | 33357 | 105630.5 | 75053.25 | 66714 | 34259.572 | 8760 | 1482.4089 | 14006.4105 | 0 | 0 | 1517.5309 | 17873.9333 | 2698.2847 | -1268.4048 | 2272.8301 | 3024.6115 | 8760 | 2718.1641 | 1481.8704 | 1236.2937 | 2719.3731 | 21751.8493 | 5166.3357 | 7561.1114 | 4869.2399 | 0 | 11834.3195 | 8760 | 9129.1013 | 251.15 | 304.8 | 1024.225 | 983633.7356 | 210834.9497 | 2280.525
580 | C | SOK | TOU | FC | ET | WC | R10 | 3.4115 | 38 | 0.95 | 8760 | 174267.2914 | 0 | 162703.9087 | 65533.1035 | 199668.8608 | 33133.5 | 104922.75 | 74550.375 | 66267 | 34593.34 | 8760 | 1482.4089 | 14183.5647 | 0 | 0 | 1562.031 | 17705.6975 | 2617.0659 | -1256.3285 | 2359.322 | 3095.8628 | 8760 | 2719.108 | 1404.7805 | 1314.3275 | 2719.3731 | 21751.8493 | 5160.5653 | 7562.6642 | 4869.5449 | 0 | 11912.2034 | 8760 | 9113.3884 | 249.575 | 302.65 | 1024.225 | 983450.0649 | 210834.9497 | 2533.325
581 | C | SOK | TOU | FC | ET | WC | R10 | 3.4115 | 38 | 1.9 | 8760 | 183821.5874 | 0 | 158180.9602 | 65533.1035 | 199668.8608 | 32980.5 | 104438.25 | 74206.125 | 65961 | 34229.6828 | 8760 | 1482.4089 | 15147.9186 | 0 | 0 | 1461.7911 | 17226.4813 | 2374.3842 | -1301.0265 | 2589.8388 | 3088.9882 | 8760 | 2718.9267 | 1296.5502 | 1422.3765 | 2719.3731 | 21751.8493 | 5196.8364 | 7560.6154 | 4870.8333 | 0 | 12882.5978 | 8760 | 9114.7379 | 280.375 | 269.3 | 1024.225 | 983380.182 | 210834.9497 | 2442.3
582 | C | SOK | TOU | FC | ET | WC | R10 | 3.4115 | 38 | 2.85 | 8760 | 188274.8457 | 0 | 156297.8358 | 65533.1035 | 199668.8608 | 32836.5 | 103982.25 | 73882.125 | 65673 | 34171.9265 | 8760 | 1482.4089 | 15607.2083 | 0 | 0 | 1457.3924 | 16965.6309 | 2202.6135 | -1314.075 | 2733.1665 | 3082.8532 | 8760 | 2718.7751 | 1233.6505 | 1485.1246 | 2719.3731 | 21751.8493 | 5204.7663 | 7557.3086 | 4867.8902 | 0 | 13346.8087 | 8760 | 9115.3285 | 301.775 | 245.5 | 1024.225 | 983554.6899 | 210834.9497 | 2401.575
583 | C | SOK | TOU | FC | ET | WC | R10 | 3.4115 | 44.5 | 1.1 | 8760 | 180573.1161 | 0 | 158455.4419 | 65533.1035 | 199668.8608 | 32931 | 104281.5 | 74094.75 | 65862 | 34569.2755 | 8760 | 1482.4089 | 15220.844 | 0 | 0 | 1495.2168 | 17053.9663 | 2373.086 | -1286.9313 | 2604.0237 | 3117.5219 | 8760 | 2719.3111 | 1272.5514 | 1446.7597 | 2719.3731 | 21751.8493 | 5183.8735 | 7571.5736 | 4877.6168 | 0 | 12905.6347 | 8760 | 9114.0509 | 274.625 | 274.225 | 1024.225 | 983246.1353 | 210834.9497 | 2638.375
584 | C | SOK | TOU | FC | ET | WC | R10 | 3.4115 | 44.5 | 2.25 | 8760 | 191260.7198 | 0 | 153177.2938 | 65533.1035 | 199668.8608 | 32700 | 103550 | 73575 | 65400 | 33634.2928 | 8760 | 1482.4089 | 16327.309 | 0 | 0 | 1414.54 | 16477.7794 | 2051.4127 | -1333.3469 | 2894.3679 | 3116.7508 | 8760 | 2719.756 | 1143.3498 | 1576.4062 | 2719.3731 | 21751.8493 | 5221.8813 | 7567.5922 | 4877.3722 | 0 | 14011.9716 | 8760 | 9114.9781 | 315.35 | 229.65 | 1024.225 | 983446.5768 | 210834.9497 | 2544.375
585 | C | SOK | TOU | FC | ET | WC | R10 | 3.4115 | 44.5 | 3.35 | 8760 | 195502.5597 | 0 | 151227.4238 | 65533.1035 | 199668.8608 | 32491.5 | 102889.75 | 73105.875 | 64983 | 33729.0724 | 8760 | 1482.4089 | 16774.5964 | 0 | 0 | 1394.2865 | 16220.5856 | 1882.8418 | -1346.7034 | 3039.1575 | 3110.8724 | 8760 | 2720.007 | 1075.2354 | 1644.7716 | 2719.3731 | 21751.8493 | 5226.1073 | 7566.3403 | 4877.9689 | 0 | 14462.3639 | 8760 | 9117.9687 | 333.725 | 207.8 | 1024.225 | 983347.1461 | 210834.9497 | 2508.75
586 | C | SOK | STR | FC | FP | WC | OFF0 | 0.45591 | 18 | 0.45 | 8760 | 105264.548 | 0 | 186790.0528 | 0 | 135001.1402 | 52560 | 166440 | 118260 | 105120 | 55657.9381 | 8760 | 1150.2925 | 5345.2725 | 0 | 0 | 0 | 9037.3005 | 6615.2513 | -1136.0798 | 1740.6005 | 2201.5627 | 8760 | 4832.2466 | 3802.6136 | 1029.633 | 4831.495 | 9572.9904 | 0 | 12918.5544 | 8114.0737 | 0 | 4004.0122 | 8760 | 15538.4406 | 176.025 | 699.975 | 1446.5 | 1700290.6831 | 186766.0544 | 3077.625
587 | C | SOK | STR | FC | FP | WC | OFF0 | 0.45591 | 18 | 0.9 | 8760 | 104350.6046 | 0 | 185478.3903 | 0 | 135001.1402 | 52600.5 | 166568.25 | 118351.125 | 105201 | 55772.2893 | 8760 | 1150.2925 | 5467.2825 | 0 | 0 | 0 | 8912.0109 | 6619.5248 | -1181.2369 | 1729.3487 | 2150.8328 | 8760 | 4831.9246 | 3817.0894 | 1014.8352 | 4831.495 | 9572.9904 | 0 | 12918.8442 | 8115.2209 | 0 | 4171.4902 | 8760 | 15540.1183 | 177.45 | 699.225 | 1446.5 | 1700215.7077 | 186766.0544 | 3105.75
588 | C | SOK | STR | FC | FP | WC | OFF0 | 0.45591 | 18 | 1.35 | 8760 | 104776.8452 | 0 | 184857.4317 | 0 | 135001.1402 | 52731 | 166981.5 | 118644.75 | 105462 | 55452.8417 | 8760 | 1150.2925 | 5537.0692 | 0 | 0 | 0 | 8852.0756 | 6632.3488 | -1196.7255 | 1729.6555 | 2132.5721 | 8760 | 4831.2908 | 3824.8629 | 1006.4279 | 4831.495 | 9572.9904 | 0 | 12926.9166 | 8123.8598 | 0 | 4260.3179 | 8760 | 15551.8106 | 179.475 | 699.375 | 1446.5 | 1700117.8649 | 186766.0544 | 3106.325
589 | C | SOK | STR | FC | FP | WC | OFF0 | 0.45591 | 24.5 | 0.6 | 8760 | 109640.9549 | 0 | 180166.4944 | 0 | 135001.1402 | 52800 | 167200 | 118800 | 105600 | 54892.0593 | 8760 | 1150.2925 | 6552.4342 | 0 | 0 | 0 | 8667.9586 | 6006.1743 | -1191.023 | 2391.0148 | 2215.965 | 8760 | 4831.6231 | 3422.4855 | 1409.1375 | 4831.495 | 9572.9904 | 0 | 12965.7993 | 8161.6269 | 0 | 5172.382 | 8760 | 15585.375 | 240.125 | 639.875 | 1446.5 | 1700175.2827 | 186766.0544 | 3162.175
590 | C | SOK | STR | FC | FP | WC | OFF0 | 0.45591 | 24.5 | 1.25 | 8760 | 109180.1274 | 0 | 178554.1019 | 0 | 135001.1402 | 52792.5 | 167176.25 | 118783.125 | 105585 | 54475.4257 | 8760 | 1150.2925 | 6762.4531 | 0 | 0 | 0 | 8497.9097 | 5965.8989 | -1231.13 | 2433.2303 | 2166.8013 | 8760 | 4831.7354 | 3410.3337 | 1421.4017 | 4831.495 | 9572.9904 | 0 | 12967.3999 | 8164.5307 | 0 | 5428.7331 | 8760 | 15586.4772 | 247.475 | 632.4 | 1446.5 | 1700264.4546 | 186766.0544 | 3184.95
591 | C | SOK | STR | FC | FP | WC | OFF0 | 0.45591 | 24.5 | 1.85 | 8760 | 109671.6031 | 0 | 176975.4572 | 0 | 135001.1402 | 52984.5 | 167784.25 | 119215.125 | 105969 | 54169.5301 | 8760 | 1150.2925 | 6898.1671 | 0 | 0 | 0 | 8377.6513 | 5915.8034 | -1240.484 | 2490.6417 | 2141.092 | 8760 | 4831.7686 | 3390.6707 | 1441.0979 | 4831.495 | 9572.9904 | 0 | 12982.8468 | 8180.5388 | 0 | 5591.8126 | 8760 | 15605.8492 | 256.85 | 626.225 | 1446.5 | 1700245.6904 | 186766.0544 | 3183.4
592 | C | SOK | STR | FC | FP | WC | OFF0 | 0.45591 | 31 | 0.8 | 8760 | 110586.9008 | 0 | 174985.8398 | 0 | 135001.1402 | 52473 | 166164.5 | 118064.25 | 104946 | 56510.4845 | 8760 | 1150.2925 | 7252.7542 | 0 | 0 | 0 | 8320.3503 | 5561.3182 | -1241.001 | 2828.4091 | 2206.0911 | 8760 | 4831.7708 | 3152.0898 | 1679.681 | 4831.495 | 9572.9904 | 0 | 12970.3529 | 8166.7175 | 0 | 5861.1342 | 8760 | 15583.0898 | 278.125 | 596.425 | 1446.5 | 1700383.8175 | 186766.0544 | 3279.05
593 | C | SOK | STR | FC | FP | WC | OFF0 | 0.45591 | 31 | 1.55 | 8760 | 111719.8023 | 0 | 171644.0626 | 0 | 135001.1402 | 52590 | 166535 | 118327.5 | 105180 | 56449.4898 | 8760 | 1150.2925 | 7601.5355 | 0 | 0 | 0 | 8126.3255 | 5428.1868 | -1272.9307 | 2963.3766 | 2165.2531 | 8760 | 4831.4644 | 3094.6737 | 1736.7906 | 4831.495 | 9572.9904 | 0 | 12982.1223 | 8180.2732 | 0 | 6249.7987 | 8760 | 15599.7661 | 297.825 | 578.675 | 1446.5 | 1700070.3847 | 186766.0544 | 3281.125
594 | C | SOK | STR | FC | FP | WC | OFF0 | 0.45591 | 31 | 2.35 | 8760 | 113528.4517 | 0 | 169514.2046 | 0 | 135001.1402 | 52606.5 | 166587.25 | 118364.625 | 105213 | 56185.9345 | 8760 | 1150.2925 | 7857.9156 | 0 | 0 | 0 | 7973.2606 | 5331.2079 | -1277.87 | 3056.4647 | 2146.1549 | 8760 | 4831.6277 | 3060.0278 | 1771.5999 | 4831.495 | 9572.9904 | 0 | 12987.5578 | 8185.3402 | 0 | 6527.2309 | 8760 | 15607.0645 | 312.925 | 563.85 | 1446.5 | 1699993.3996 | 186766.0544 | 3263.625
595 | C | SOK | STR | FC | FP | WC | OFF | 0.45591 | 38 | 0.95 | 8760 | 113855.882 | 0 | 169755.6885 | 0 | 135001.1402 | 52378.5 | 165865.25 | 117851.625 | 104757 | 57990.4519 | 8760 | 1150.2925 | 7977.2075 | 0 | 0 | 0 | 8008.3232 | 5151.5847 | -1267.9615 | 3216.931 | 2191.3472 | 8760 | 4832.4279 | 2921.2905 | 1911.1374 | 4831.495 | 9572.9904 | 0 | 12988.8755 | 8182.811 | 0 | 6581.8704 | 8760 | 15597.2722 | 314.55 | 558.425 | 1446.5 | 1700154.7924 | 186766.0544 | 3371.85
596 | C | SOK | STR | FC | FP | WC | OFF | 0.45591 | 38 | 1.9 | 8760 | 117264.4996 | 0 | 165153.9953 | 0 | 135001.1402 | 52320 | 165680 | 117720 | 104640 | 57479.2556 | 8760 | 1150.2925 | 8570.6644 | 0 | 0 | 0 | 7716.8185 | 4899.7131 | -1297.5658 | 3452.1158 | 2164.8718 | 8760 | 4831.6587 | 2801.4351 | 2030.2236 | 4831.495 | 9572.9904 | 0 | 12986.7301 | 8185.179 | 0 | 7199.7444 | 8760 | 15594.9267 | 344.75 | 527.25 | 1446.5 | 1700127.0923 | 186766.0544 | 3350.125
597 | C | SOK | STR | FC | FP | WC | OFF | 0.45591 | 38 | 2.85 | 8760 | 119811.0159 | 0 | 162731.6568 | 0 | 135001.1402 | 52392 | 165908 | 117882 | 104784 | 56514.866 | 8760 | 1150.2925 | 8951.8815 | 0 | 0 | 0 | 7552.0971 | 4691.3621 | -1301.651 | 3662.2866 | 2139.1983 | 8760 | 4831.6313 | 2709.6 | 2122.0313 | 4831.495 | 9572.9904 | 0 | 12998.7518 | 8198.984 | 0 | 7607.3041 | 8760 | 15610.7283 | 374.925 | 498.275 | 1446.5 | 1700036.4193 | 186766.0544 | 3330.05
598 | C | SOK | STR | FC | FP | WC | OFF | 0.45591 | 44.5 | 1.1 | 8760 | 119481.4876 | 0 | 165010.7549 | 0 | 135001.1402 | 52186.5 | 165257.25 | 117419.625 | 104373 | 57981.3896 | 8760 | 1150.2925 | 8658.3322 | 0 | 0 | 0 | 7748.6692 | 4750.9863 | -1286.1072 | 3597.9039 | 2186.4701 | 8760 | 4832.0093 | 2689.4339 | 2142.5754 | 4831.495 | 9572.9904 | 0 | 12996.7799 | 8192.3908 | 0 | 7254.634 | 8760 | 15595.1214 | 349.125 | 520.65 | 1446.5 | 1700093.4043 | 186766.0544 | 3429.975
599 | C | SOK | STR | FC | FP | WC | OFF | 0.45591 | 44.5 | 2.25 | 8760 | 124145.6894 | 0 | 159700.3589 | 0 | 135001.1402 | 52227 | 165385.5 | 117510.75 | 104454 | 57529.1723 | 8760 | 1150.2925 | 9455.5289 | 0 | 0 | 0 | 7377.0806 | 4376.7027 | -1314.1421 | 3967.7671 | 2153.476 | 8760 | 4831.97 | 2506.722 | 2325.248 | 4831.495 | 9572.9904 | 0 | 13010.6918 | 8208.9098 | 0 | 8079.9177 | 8760 | 15612.5125 | 396.8 | 473.65 | 1446.5 | 1700054.445 | 186766.0544 | 3401.65
600 | C | SOK | STR | FC | FP | WC | OFF | 0.45591 | 44.5 | 3.35 | 8760 | 125684.7381 | 0 | 157628.2471 | 0 | 135001.1402 | 52380 | 165870 | 117855 | 104760 | 56706.2103 | 8760 | 1150.2925 | 9800.086 | 0 | 0 | 0 | 7228.8372 | 4211.379 | -1326.5533 | 4135.4531 | 2127.8925 | 8760 | 4831.988 | 2443.437 | 2388.5509 | 4831.495 | 9572.9904 | 0 | 13029.019 | 8229.9789 | 0 | 8450.1 | 8760 | 15637.9178 | 422.725 | 450.275 | 1446.5 | 1700113.4433 | 186766.0544 | 3395.475
601 | C | SOK | TOU | CC | ET | WC | R100 | 4.6056 | 23 | 0.6 | 8760 | 170024.2969 | 0 | 177117.9477 | 65533.1035 | 238348.6519 | 26653.5 | 84402.75 | 59970.375 | 53307 | 47232.0252 | 8760 | 1482.4089 | 11435.8242 | 0 | 0 | 2418.4413 | 27036.8685 | 3548.3666 | -1118.0289 | 1409.0548 | 2888.6174 | 8760 | 3336.9095 | 2392.2374 | 944.6721 | 3341.6843 | 29365.382 | 6238.5164 | 8153.9886 | 4827.9465 | 0 | 9419.4031 | 8760 | 9884.1064 | 127.825 | 316.4 | 850.5 | 1085646.9521 | 210834.9497 | 2168.35
602 | C | SOK | TOU | CC | ET | WC | R100 | 4.6056 | 23 | 1.15 | 8760 | 177293.718 | 0 | 174814.1013 | 65533.1035 | 238348.6519 | 26772 | 84778 | 60237 | 53544 | 47217.3962 | 8760 | 1482.4089 | 12074.4865 | 0 | 0 | 2280.5024 | 26673.6788 | 3463.1835 | -1155.3971 | 1487.7357 | 2853.2878 | 8760 | 3337.3618 | 2355.6293 | 981.7325 | 3341.6843 | 29365.382 | 6280.5511 | 8164.7148 | 4838.7832 | 0 | 10098.2113 | 8760 | 9899.1186 | 139.925 | 306.275 | 850.5 | 1085623.0039 | 210834.9497 | 2086.5
603 | C | SOK | TOU | CC | ET | WC | R100 | 4.6056 | 23 | 1.75 | 8760 | 180260.2989 | 0 | 173920.9108 | 65533.1035 | 238348.6519 | 26773.5 | 84782.75 | 60240.375 | 53547 | 47494.8827 | 8760 | 1482.4089 | 12332.195 | 0 | 0 | 2267.4064 | 26485.6273 | 3432.9567 | -1167.4034 | 1521.7326 | 2839.6296 | 8760 | 3338.2297 | 2345.3051 | 992.9247 | 3341.6843 | 29365.382 | 6294.5423 | 8170.3698 | 4844.7098 | 0 | 10370.3427 | 8760 | 9907.8335 | 146.075 | 300.15 | 850.5 | 1085689.9566 | 210834.9497 | 2055.625
604 | C | SOK | TOU | CC | ET | WC | R100 | 4.6056 | 32 | 0.8 | 8760 | 175385.4071 | 0 | 169655.1952 | 65533.1035 | 238348.6519 | 26451 | 83761.5 | 59514.75 | 52902 | 47809.4313 | 8760 | 1482.4089 | 13713.9382 | 0 | 0 | 2230.5982 | 25796.6654 | 2979.1364 | -1194.7225 | 1952.8234 | 2990.493 | 8760 | 3334.3181 | 2031.339 | 1302.9791 | 3341.6843 | 29365.382 | 6321.118 | 8168.4918 | 4845.8277 | 0 | 11550.2854 | 8760 | 9895.2602 | 175.75 | 265.1 | 850.5 | 1085541.7598 | 210834.9497 | 2365.75
605 | C | SOK | TOU | CC | ET | WC | R100 | 4.6056 | 32 | 1.6 | 8760 | 183934.0857 | 0 | 166731.1402 | 65533.1035 | 238348.6519 | 26449.5 | 83756.75 | 59511.375 | 52899 | 48405.1595 | 8760 | 1482.4089 | 14580.8902 | 0 | 0 | 2109.6247 | 25303.0522 | 2840.7716 | -1234.7445 | 2092.6669 | 2969.0164 | 8760 | 3335.0175 | 1950.0615 | 1384.956 | 3341.6843 | 29365.382 | 6361.627 | 8171.5481 | 4848.388 | 0 | 12441.1553 | 8760 | 9906.0465 | 192.65 | 248.175 | 850.5 | 1085618.3883 | 210834.9497 | 2280.325
606 | C | SOK | TOU | CC | ET | WC | R100 | 4.6056 | 32 | 2.4 | 8760 | 187850.2306 | 0 | 165141.9961 | 65533.1035 | 238348.6519 | 26470.5 | 83823.25 | 59558.625 | 52941 | 48148.6147 | 8760 | 1482.4089 | 14987.0984 | 0 | 0 | 2077.1189 | 25064.1159 | 2718.2291 | -1241.0656 | 2208.313 | 2950.5944 | 8760 | 3333.3478 | 1880.8726 | 1452.4752 | 3341.6843 | 29365.382 | 6358.3558 | 8173.7243 | 4853.4203 | 0 | 12865.7637 | 8760 | 9909.9576 | 206.325 | 234.85 | 850.5 | 1085546.4938 | 210834.9497 | 2242.575
607 | C | SOK | TOU | CC | ET | WC | R100 | 4.6056 | 40.5 | 1 | 8760 | 183977.2898 | 0 | 164078.567 | 65533.1035 | 238348.6519 | 26242.5 | 83101.25 | 59045.625 | 52485 | 46821.4834 | 8760 | 1482.4089 | 15499.2267 | 0 | 0 | 2084.0719 | 24736.9032 | 2517.1311 | -1243.3797 | 2417.0037 | 3034.4092 | 8760 | 3339.7635 | 1726.5913 | 1613.1722 | 3341.6843 | 29365.382 | 6369.2972 | 8197.4812 | 4870.4589 | 0 | 13260.3126 | 8760 | 9916.0804 | 214.1 | 223.275 | 850.5 | 1085730.1178 | 210834.9497 | 2510.375
608 | C | SOK | TOU | CC | ET | WC | R100 | 4.6056 | 40.5 | 2.05 | 8760 | 194538.3149 | 0 | 159857.8484 | 65533.1035 | 238348.6519 | 26250 | 83125 | 59062.5 | 52500 | 47536.4131 | 8760 | 1482.4089 | 16615.7416 | 0 | 0 | 1969.9852 | 24107.4533 | 2291.0738 | -1283.0351 | 2637.2704 | 3024.6392 | 8760 | 3337.4773 | 1593.8882 | 1743.589 | 3341.6843 | 29365.382 | 6407.6881 | 8199.9042 | 4874.4603 | 0 | 14387.5104 | 8760 | 9930.7026 | 240.325 | 197.175 | 850.5 | 1085657.4285 | 210834.9497 | 2412.95
609 | C | SOK | TOU | CC | ET | WC | R100 | 4.6056 | 40.5 | 3.05 | 8760 | 199081.3472 | 0 | 158495.9392 | 65533.1035 | 238348.6519 | 26301 | 83286.5 | 59177.25 | 52602 | 47738.535 | 8760 | 1482.4089 | 17118.1231 | 0 | 0 | 1930.5229 | 23829.4994 | 2146.9421 | -1293.3109 | 2778.089 | 3010.4317 | 8760 | 3336.8751 | 1510.2194 | 1826.6557 | 3341.6843 | 29365.382 | 6415.1541 | 8204.496 | 4882.4257 | 0 | 14900.9162 | 8760 | 9940.0717 | 257 | 181.35 | 850.5 | 1085642.1564 | 210834.9497 | 2374.025
610 | C | SOK | TOU | CC | ET | WC | R10 | 4.6056 | 49 | 1.25 | 8760 | 195422.5884 | 0 | 158744.1727 | 65533.1035 | 238348.6519 | 26104.5 | 82664.25 | 58735.125 | 52209 | 45236.6111 | 8760 | 1482.4089 | 17071.6653 | 0 | 0 | 1970.73 | 23717.9213 | 2152.6762 | -1281.7878 | 2798.1981 | 3062.9715 | 8760 | 3339.1797 | 1481.5547 | 1857.625 | 3341.6843 | 29365.382 | 6409.5372 | 8218.5242 | 4893.014 | 0 | 14777.1148 | 8760 | 9928.456 | 246.55 | 188.525 | 850.5 | 1085761.3007 | 210834.9497 | 2627.35
611 | C | SOK | TOU | CC | ET | WC | R10 | 4.6056 | 49 | 2.45 | 8760 | 206693.8638 | 0 | 154478.4571 | 65533.1035 | 238348.6519 | 26151 | 82811.5 | 58839.75 | 52302 | 46376.482 | 8760 | 1482.4089 | 18287.4171 | 0 | 0 | 1871.0277 | 23033.0542 | 1860.02 | -1321.9529 | 3076.9411 | 3054.4321 | 8760 | 3340.4448 | 1307.1347 | 2033.3101 | 3341.6843 | 29365.382 | 6453.8174 | 8230.0748 | 4905.243 | 0 | 16001.6104 | 8760 | 9956.1212 | 276.7 | 159.15 | 850.5 | 1085860.9352 | 210834.9497 | 2534.875
612 | C | SOK | TOU | CC | ET | WC | R10 | 4.6056 | 49 | 3.7 | 8760 | 212227.7773 | 0 | 153032.5535 | 65533.1035 | 238348.6519 | 26239.5 | 83091.75 | 59038.875 | 52479 | 46175.5042 | 8760 | 1482.4089 | 18856.6353 | 0 | 0 | 1851.6057 | 22767.2313 | 1666.3502 | -1335.7261 | 3265.2771 | 3052.0672 | 8760 | 3338.9457 | 1193.3647 | 2145.5811 | 3341.6843 | 29365.382 | 6462.965 | 8237.4546 | 4915.9737 | 0 | 16569.3175 | 8760 | 9968.5529 | 298.375 | 138.95 | 850.5 | 1085764.6048 | 210834.9497 | 2490.225
613 | C | SOK | TOU | CC | ET | WC | R10 | 4.6056 | 58 | 1.45 | 8760 | 209501.5169 | 0 | 154474.7073 | 65533.1035 | 238348.6519 | 26073 | 82564.5 | 58664.25 | 52146 | 44342.9699 | 8760 | 1482.4089 | 18463.9481 | 0 | 0 | 1894.3764 | 22801.572 | 1851.1299 | -1308.9929 | 3099.9167 | 3066.4987 | 8760 | 3341.546 | 1293.3489 | 2048.1972 | 3341.6843 | 29365.382 | 6440.0409 | 8245.6135 | 4920.2729 | 0 | 16142.709 | 8760 | 9956.3413 | 273.375 | 161.175 | 850.5 | 1085872.9116 | 210834.9497 | 2738.775
614 | C | SOK | TOU | CC | ET | WC | R10 | 4.6056 | 58 | 2.9 | 8760 | 221865.7825 | 0 | 149877.5138 | 65533.1035 | 238348.6519 | 26223 | 83039.5 | 59001.75 | 52446 | 44632.8958 | 8760 | 1482.4089 | 19801.943 | 0 | 0 | 1804.611 | 22043.3156 | 1527.057 | -1351.0643 | 3428.9981 | 3061.2306 | 8760 | 3340.1661 | 1089.9285 | 2250.2376 | 3341.6843 | 29365.382 | 6483.2954 | 8257.2518 | 4936.9032 | 0 | 17483.0907 | 8760 | 9978.5432 | 309.925 | 127.125 | 850.5 | 1085766.0191 | 210834.9497 | 2648.65
615 | C | SOK | TOU | CC | ET | WC | R10 | 4.6056 | 58 | 4.35 | 8760 | 227778.2306 | 0 | 148004.1388 | 65533.1035 | 238348.6519 | 26236.5 | 83082.25 | 59032.125 | 52473 | 44857.5376 | 8760 | 1482.4089 | 20398.3263 | 0 | 0 | 1786.1633 | 21745.4185 | 1321.6014 | -1365.2946 | 3622.2762 | 3055.5806 | 8760 | 3341.4146 | 963.203 | 2378.2116 | 3341.6843 | 29365.382 | 6491.912 | 8267.8012 | 4944.3307 | 0 | 18082.7409 | 8760 | 9999.0354 | 328.55 | 108.725 | 850.5 | 1085821.4382 | 210834.9497 | 2605
616 | C | SOK | TOU | CC | FP | WC | R100 | 4.6056 | 23 | 0.6 | 8760 | 158947.467 | 0 | 176528.487 | 65533.1035 | 238348.6519 | 26707.5 | 84573.75 | 60091.875 | 53415 | 46542.2897 | 8760 | 1482.4089 | 11136.4621 | 0 | 0 | 2447.1454 | 26744.9381 | 3713.7559 | -1082.6418 | 1246.4898 | 2571.7121 | 8760 | 3337.6386 | 2497.8832 | 839.7554 | 3341.6843 | 29365.382 | 6200.455 | 8158.7843 | 4831.3261 | 0 | 9414.7015 | 8760 | 9885.2574 | 110.325 | 334.8 | 850.5 | 1085733.5097 | 210834.9497 | 2413.875
617 | C | SOK | TOU | CC | FP | WC | R100 | 4.6056 | 23 | 1.15 | 8760 | 164380.1089 | 0 | 173410.1949 | 65533.1035 | 238348.6519 | 26688 | 84512 | 60048 | 53376 | 46711.4798 | 8760 | 1482.4089 | 11975.1563 | 0 | 0 | 2258.8727 | 26201.2925 | 3693.1099 | -1129.8325 | 1263.8976 | 2518.7348 | 8760 | 3337.0653 | 2495.6548 | 841.4105 | 3341.6843 | 29365.382 | 6251.1179 | 8157.0198 | 4830.2431 | 0 | 10306.6922 | 8760 | 9883.8165 | 115.2 | 329.6 | 850.5 | 1085687.7153 | 210834.9497 | 2373.15
618 | C | SOK | TOU | CC | FP | WC | R100 | 4.6056 | 23 | 1.75 | 8760 | 166403.5755 | 0 | 171691.3095 | 65533.1035 | 238348.6519 | 26709 | 84578.5 | 60095.25 | 53418 | 46772.2416 | 8760 | 1482.4089 | 12356.0593 | 0 | 0 | 2232.5388 | 25886.3322 | 3660.1104 | -1142.3633 | 1294.6003 | 2480.0162 | 8760 | 3337.533 | 2486.5469 | 850.9861 | 3341.6843 | 29365.382 | 6266.6126 | 8160.4324 | 4834.6796 | 0 | 10724.6587 | 8760 | 9889.3011 | 121.325 | 323.825 | 850.5 | 1085758.4691 | 210834.9497 | 2364.2
619 | C | SOK | TOU | CC | FP | WC | R100 | 4.6056 | 32 | 0.8 | 8760 | 165624.9991 | 0 | 170063.168 | 65533.1035 | 238348.6519 | 26497.5 | 83908.75 | 59619.375 | 52995 | 47229.7394 | 8760 | 1482.4089 | 13197.5828 | 0 | 0 | 2244.5869 | 25573.6511 | 3318.418 | -1162.6449 | 1646.347 | 2625.255 | 8760 | 3335.4067 | 2226.6473 | 1108.7593 | 3341.6843 | 29365.382 | 6286.1769 | 8162.2882 | 4834.7669 | 0 | 11379.5486 | 8760 | 9883.0655 | 144.325 | 297.3 | 850.5 | 1085716.3899 | 210834.9497 | 2595.8
620 | C | SOK | TOU | CC | FP | WC | R100 | 4.6056 | 32 | 1.6 | 8760 | 171262.0459 | 0 | 165550.7189 | 65533.1035 | 238348.6519 | 26413.5 | 83642.75 | 59430.375 | 52827 | 47341.1839 | 8760 | 1482.4089 | 14357.2388 | 0 | 0 | 2097.9027 | 24767.3279 | 3171.7543 | -1209.6656 | 1765.972 | 2561.9627 | 8760 | 3334.7283 | 2159.2417 | 1175.4866 | 3341.6843 | 29365.382 | 6336.545 | 8161.6523 | 4835.5463 | 0 | 12598.0917 | 8760 | 9886.0787 | 159.65 | 280.575 | 850.5 | 1085568.1388 | 210834.9497 | 2567.075
621 | C | SOK | TOU | CC | FP | WC | R100 | 4.6056 | 32 | 2.4 | 8760 | 173763.339 | 0 | 163516.1045 | 65533.1035 | 238348.6519 | 26445 | 83742.5 | 59501.25 | 52890 | 47459.8348 | 8760 | 1482.4089 | 14851.6745 | 0 | 0 | 2050.7716 | 24426.7356 | 3094.3624 | -1218.2348 | 1856.2804 | 2529.7947 | 8760 | 3335.8763 | 2106.5025 | 1229.3739 | 3341.6843 | 29365.382 | 6336.8636 | 8164.5258 | 4840.1913 | 0 | 13121.7509 | 8760 | 9894.4931 | 170.525 | 270.225 | 850.5 | 1085701.9443 | 210834.9497 | 2552.775
622 | C | SOK | TOU | CC | FP | WC | R100 | 4.6056 | 40.5 | 1 | 8760 | 175335.7822 | 0 | 164448.2924 | 65533.1035 | 238348.6519 | 26280 | 83220 | 59130 | 52560 | 46597.9825 | 8760 | 1482.4089 | 14841.229 | 0 | 0 | 2110.5843 | 24517.9184 | 2955.4648 | -1212.8768 | 1989.3946 | 2648.4719 | 8760 | 3330.3649 | 1995.817 | 1334.5479 | 3341.6843 | 29365.382 | 6339.3533 | 8161.2945 | 4840.7166 | 0 | 12970.3349 | 8760 | 9869.5356 | 173.75 | 264.25 | 850.5 | 1085521.8893 | 210834.9497 | 2721.95
623 | C | SOK | TOU | CC | FP | WC | R100 | 4.6056 | 40.5 | 2.05 | 8760 | 181093.2545 | 0 | 159651.6122 | 65533.1035 | 238348.6519 | 26239.5 | 83091.75 | 59038.875 | 52479 | 47431.7279 | 8760 | 1482.4089 | 16224.2214 | 0 | 0 | 1971.6767 | 23556.3376 | 2766.4628 | -1257.2893 | 2162.8662 | 2578.0499 | 8760 | 3338.6356 | 1902.2937 | 1436.342 | 3341.6843 | 29365.382 | 6382.4762 | 8183.8165 | 4854.4224 | 0 | 14414.5912 | 8760 | 9906.6216 | 194.2 | 243.125 | 850.5 | 1085766.0825 | 210834.9497 | 2701.05
624 | C | SOK | TOU | CC | FP | WC | R100 | 4.6056 | 40.5 | 3.05 | 8760 | 183305.4839 | 0 | 156990.0396 | 65533.1035 | 238348.6519 | 26379 | 83533.5 | 59352.75 | 52758 | 46990.0906 | 8760 | 1482.4089 | 16844.8905 | 0 | 0 | 1914.3921 | 23132.9334 | 2672.5803 | -1267.4069 | 2273.2772 | 2540.3146 | 8760 | 3336.0238 | 1834.0449 | 1501.9789 | 3341.6843 | 29365.382 | 6388.7022 | 8189.4485 | 4866.0815 | 0 | 15066.2242 | 8760 | 9915.3265 | 206.025 | 233.625 | 850.5 | 1085710.2405 | 210834.9497 | 2696.525
625 | C | SOK | TOU | CC | FP | WC | R10 | 4.6056 | 49 | 1.25 | 8760 | 187744.0685 | 0 | 159740.8562 | 65533.1035 | 238348.6519 | 26127 | 82735.5 | 58785.75 | 52254 | 46206.6951 | 8760 | 1482.4089 | 16369.9062 | 0 | 0 | 1998.3796 | 23465.6959 | 2624.3679 | -1252.1196 | 2304.9138 | 2645.3301 | 8760 | 3340.5997 | 1799.5288 | 1541.071 | 3341.6843 | 29365.382 | 6378.1815 | 8200.0965 | 4869.4956 | 0 | 14476.0667 | 8760 | 9910.0274 | 200.15 | 235.3 | 850.5 | 1085793.7463 | 210834.9497 | 2826.625
626 | C | SOK | TOU | CC | FP | WC | R10 | 4.6056 | 49 | 2.45 | 8760 | 193184.5348 | 0 | 153444.276 | 65533.1035 | 238348.6519 | 26122.5 | 82721.25 | 58775.625 | 52245 | 46872.5128 | 8760 | 1482.4089 | 17807.3632 | 0 | 0 | 1860.4179 | 22506.058 | 2389.8307 | -1295.0573 | 2548.2857 | 2580.4738 | 8760 | 3341.1819 | 1653.9291 | 1687.2528 | 3341.6843 | 29365.382 | 6422.3118 | 8210.9977 | 4879.843 | 0 | 15966.3623 | 8760 | 9932.6388 | 227.1 | 208.275 | 850.5 | 1085768.8663 | 210834.9497 | 2816.45
627 | C | SOK | TOU | CC | FP | WC | R10 | 4.6056 | 49 | 3.7 | 8760 | 196015.6367 | 0 | 151529.6537 | 65533.1035 | 238348.6519 | 26313 | 83324.5 | 59204.25 | 52626 | 46231.344 | 8760 | 1482.4089 | 18529.695 | 0 | 0 | 1823.1463 | 22005.306 | 2214.7111 | -1306.9128 | 2711.759 | 2545.4178 | 8760 | 3340.2188 | 1553.7714 | 1786.4474 | 3341.6843 | 29365.382 | 6431.8538 | 8223.8887 | 4898.0736 | 0 | 16718.25 | 8760 | 9950.1818 | 244.825 | 193.725 | 850.5 | 1085805.1125 | 210834.9497 | 2806.225
628 | C | SOK | TOU | CC | FP | WC | R10 | 4.6056 | 58 | 1.45 | 8760 | 202698.7982 | 0 | 155265.9046 | 65533.1035 | 238348.6519 | 26164.5 | 82854.25 | 58870.125 | 52329 | 44820.7771 | 8760 | 1482.4089 | 17681.5664 | 0 | 0 | 1907.7881 | 22578.4985 | 2402.2281 | -1280.5274 | 2546.0712 | 2641.2733 | 8760 | 3339.6024 | 1650.9053 | 1688.6971 | 3341.6843 | 29365.382 | 6406.4567 | 8214.2801 | 4888.1757 | 0 | 15765.4922 | 8760 | 9922.0332 | 223.15 | 212.925 | 850.5 | 1085771.754 | 210834.9497 | 2925.65
629 | C | SOK | TOU | CC | FP | WC | R10 | 4.6056 | 58 | 2.9 | 8760 | 208291.0533 | 0 | 149133.5634 | 65533.1035 | 238348.6519 | 26191.5 | 82939.75 | 58930.875 | 52383 | 44904.5633 | 8760 | 1482.4089 | 19263.2738 | 0 | 0 | 1754.1338 | 21515.7189 | 2115.9294 | -1327.6229 | 2832.0709 | 2567.0609 | 8760 | 3339.1974 | 1474.77 | 1864.4274 | 3341.6843 | 29365.382 | 6455.9625 | 8227.2158 | 4902.5301 | 0 | 17411.4663 | 8760 | 9945.541 | 253.825 | 182.7 | 850.5 | 1085670.1367 | 210834.9497 | 2918.9
630 | C | SOK | TOU | CC | FP | WC | R10 | 4.6056 | 58 | 4.35 | 8760 | 210768.5753 | 0 | 146165.2613 | 65533.1035 | 238348.6519 | 26340 | 83410 | 59265 | 52680 | 45508.9255 | 8760 | 1482.4089 | 20102.7251 | 0 | 0 | 1744.4651 | 20949.6284 | 1885.9884 | -1338.0301 | 3053.8198 | 2525.1378 | 8760 | 3341.1387 | 1336.0952 | 2005.0434 | 3341.6843 | 29365.382 | 6465.255 | 8244.5622 | 4920.9692 | 0 | 18285.4364 | 8760 | 9970.9679 | 276.075 | 162.925 | 850.5 | 1085787.2144 | 210834.9497 | 2918.5
631 | C | SOK | TOU | CC | ET | WC | R600 | 5.4272 | 23 | 0.6 | 8760 | 162782.6911 | 0 | 159518.871 | 65533.1035 | 162408.4576 | 33739.5 | 106841.75 | 75913.875 | 67479 | 58237.3534 | 8760 | 1475.3019 | 12418.5817 | 0 | 0 | 2298.1906 | 16500.8679 | 4452.4076 | -1201.6262 | 1914.1336 | 2960.4269 | 8760 | 4335.1491 | 3041.0754 | 1294.0737 | 4338.0557 | 18236.4195 | 7046.3882 | 10576.4205 | 6241.3547 | 0 | 10241.528 | 8760 | 12706.8498 | 167.875 | 394.45 | 1048.625 | 1390815.143 | 189624.8638 | 2258.05
632 | C | SOK | TOU | CC | ET | WC | R600 | 5.4272 | 23 | 1.15 | 8760 | 170244.6807 | 0 | 157396.5125 | 65533.1035 | 162408.4576 | 33807 | 107055.5 | 76065.75 | 67614 | 57823.5098 | 8760 | 1475.3019 | 13092.5124 | 0 | 0 | 2152.3 | 16237.8189 | 4324.3731 | -1258.5603 | 2034.4461 | 2963.4494 | 8760 | 4333.359 | 2977.9504 | 1355.4087 | 4338.0557 | 18236.4195 | 7143.6523 | 10581.4102 | 6249.6117 | 0 | 10915.9657 | 8760 | 12715.1522 | 184.7 | 378.75 | 1048.625 | 1390744.6855 | 189624.8638 | 2171.175
633 | C | SOK | TOU | CC | ET | WC | R600 | 5.4272 | 23 | 1.75 | 8760 | 173490.0459 | 0 | 156576.0672 | 65533.1035 | 162408.4576 | 33871.5 | 107259.75 | 76210.875 | 67743 | 58064.4776 | 8760 | 1475.3019 | 13379.4393 | 0 | 0 | 2142.7106 | 16087.8781 | 4264.7345 | -1277.0139 | 2100.5699 | 2960.6009 | 8760 | 4334.5956 | 2948.3277 | 1386.2679 | 4338.0557 | 18236.4195 | 7165.9385 | 10589.747 | 6257.4114 | 0 | 11204.8604 | 8760 | 12729.4036 | 195 | 369.525 | 1048.625 | 1390820.3568 | 189624.8638 | 2135.125
634 | C | SOK | TOU | CC | ET | WC | R600 | 5.4272 | 32 | 0.8 | 8760 | 164628.3634 | 0 | 152664.328 | 65533.1035 | 162408.4576 | 33544.5 | 106224.25 | 75475.125 | 67089 | 59109.219 | 8760 | 1475.3019 | 14541.1501 | 0 | 0 | 2090.9251 | 15611.6363 | 3792.1849 | -1283.6449 | 2595.8317 | 3068.7301 | 8760 | 4334.1845 | 2591.4629 | 1742.7215 | 4338.0557 | 18236.4195 | 7155.7923 | 10603.4666 | 6270.0832 | 0 | 12210.46 | 8760 | 12729.6825 | 226.75 | 332.325 | 1048.625 | 1390843.5275 | 189624.8638 | 2481.8
635 | C | SOK | TOU | CC | ET | WC | R600 | 5.4272 | 32 | 1.6 | 8760 | 172738.0703 | 0 | 149209.3084 | 65533.1035 | 162408.4576 | 33550.5 | 106243.25 | 75488.625 | 67101 | 59308.9705 | 8760 | 1475.3019 | 15420.5347 | 0 | 0 | 1991.1277 | 15199.1632 | 3534.0878 | -1333.068 | 2840.7259 | 3065.08 | 8760 | 4334.0533 | 2448.1498 | 1885.9034 | 4338.0557 | 18236.4195 | 7228.39 | 10612.6446 | 6282.1363 | 0 | 13093.6141 | 8760 | 12748.2714 | 255.35 | 303.825 | 1048.625 | 1390774.4863 | 189624.8638 | 2397.575
636 | C | SOK | TOU | CC | ET | WC | R600 | 5.4272 | 32 | 2.4 | 8760 | 176970.0866 | 0 | 147316.4346 | 65533.1035 | 162408.4576 | 33564 | 106286 | 75519 | 67128 | 59331.7896 | 8760 | 1475.3019 | 15870.0388 | 0 | 0 | 1987.4859 | 14975.4383 | 3355.2977 | -1347.3845 | 3008.6809 | 3061.5444 | 8760 | 4335.1339 | 2344.7349 | 1990.399 | 4338.0557 | 18236.4195 | 7243.5661 | 10622.0001 | 6290.0475 | 0 | 13545.7471 | 8760 | 12765.0029 | 273.6 | 285.8 | 1048.625 | 1390775.6561 | 189624.8638 | 2355.15
637 | C | SOK | TOU | CC | ET | WC | R600 | 5.4272 | 40.5 | 1 | 8760 | 169320.1782 | 0 | 146880.7136 | 65533.1035 | 162408.4576 | 33351 | 105611.5 | 75039.75 | 66702 | 57551.9087 | 8760 | 1475.3019 | 16084.6742 | 0 | 0 | 1954.6274 | 14803.5166 | 3263.4836 | -1331.5834 | 3132.5134 | 3109.8465 | 8760 | 4327.8632 | 2238.2004 | 2089.6629 | 4338.0557 | 18236.4195 | 7216.9798 | 10621.2737 | 6296.1594 | 0 | 13681.0073 | 8760 | 12731.659 | 272.075 | 283.775 | 1048.625 | 1390672.7298 | 189624.8638 | 2651.25
638 | C | SOK | TOU | CC | ET | WC | R600 | 5.4272 | 40.5 | 2.05 | 8760 | 178858.6982 | 0 | 142640.4964 | 65533.1035 | 162408.4576 | 33331.5 | 105549.75 | 74995.875 | 66663 | 57456.1894 | 8760 | 1475.3019 | 17217.8398 | 0 | 0 | 1858.7368 | 14256.146 | 2875.5602 | -1375.2778 | 3499.0219 | 3102.9763 | 8760 | 4331.09 | 2015.6374 | 2315.4526 | 4338.0557 | 18236.4195 | 7271.7797 | 10638.4279 | 6313.279 | 0 | 14817.9049 | 8760 | 12763.7414 | 311.925 | 243.6 | 1048.625 | 1390718.879 | 189624.8638 | 2561.65
639 | C | SOK | TOU | CC | ET | WC | R600 | 5.4272 | 40.5 | 3.05 | 8760 | 184113.1527 | 0 | 140467.1413 | 65533.1035 | 162408.4576 | 33312 | 105488 | 74952 | 66624 | 59003.5885 | 8760 | 1475.3019 | 17807.3939 | 0 | 0 | 1860.027 | 13957.2255 | 2652.5307 | -1386.15 | 3729.8883 | 3095.1793 | 8760 | 4337.0018 | 1871.3615 | 2465.6403 | 4338.0557 | 18236.4195 | 7282.9047 | 10655.0448 | 6322.8037 | 0 | 15410.8928 | 8760 | 12798.6501 | 335.475 | 219.725 | 1048.625 | 1390809.8728 | 189624.8638 | 2512.825
640 | C | SOK | TOU | CC | ET | WC | R60 | 5.4272 | 49 | 1.25 | 8760 | 177935.3728 | 0 | 141739.8064 | 65533.1035 | 162408.4576 | 33112.5 | 104856.25 | 74503.125 | 66225 | 57152.4359 | 8760 | 1475.3019 | 17515.8663 | 0 | 0 | 1806.5089 | 14027.9862 | 2801.9093 | -1373.1152 | 3593.3805 | 3130.0639 | 8760 | 4337.3353 | 1947.0749 | 2390.2604 | 4338.0557 | 18236.4195 | 7265.3307 | 10664.6809 | 6330.9253 | 0 | 15067.726 | 8760 | 12778.9398 | 310.1 | 241.775 | 1048.625 | 1390837.5517 | 189624.8638 | 2776.75
641 | C | SOK | TOU | CC | ET | WC | R60 | 5.4272 | 49 | 2.45 | 8760 | 187816.9334 | 0 | 137243.1062 | 65533.1035 | 162408.4576 | 33096 | 104804 | 74466 | 66192 | 57199.7965 | 8760 | 1475.3019 | 18730.3671 | 0 | 0 | 1737.6438 | 13419.4847 | 2366.4008 | -1408.3762 | 4021.1721 | 3113.349 | 8760 | 4336.0324 | 1676.0268 | 2660.0056 | 4338.0557 | 18236.4195 | 7304.7918 | 10673.7231 | 6343.4686 | 0 | 16295.0284 | 8760 | 12800.9464 | 355.025 | 196.575 | 1048.625 | 1390801.5105 | 189624.8638 | 2693.575
642 | C | SOK | TOU | CC | ET | WC | R60 | 5.4272 | 49 | 3.7 | 8760 | 193653.1148 | 0 | 134784.0202 | 65533.1035 | 162408.4576 | 33280.5 | 105388.25 | 74881.125 | 66561 | 57066.2272 | 8760 | 1475.3019 | 19440.0822 | 0 | 0 | 1711.9126 | 13102.8772 | 2089.0934 | -1420.2746 | 4309.8379 | 3109.0737 | 8760 | 4337.4537 | 1488.7874 | 2848.6663 | 4338.0557 | 18236.4195 | 7318.3078 | 10697.3552 | 6364.4351 | 0 | 17003.516 | 8760 | 12840.9576 | 382.925 | 171.75 | 1048.625 | 1390840.2202 | 189624.8638 | 2646.725
643 | C | SOK | TOU | CC | ET | WC | R60 | 5.4272 | 58 | 1.45 | 8760 | 189112.4429 | 0 | 137299.3525 | 65533.1035 | 162408.4576 | 33087 | 104775.5 | 74445.75 | 66174 | 55313.5157 | 8760 | 1475.3019 | 18750.1818 | 0 | 0 | 1709.2106 | 13286.8779 | 2471.3284 | -1402.2498 | 3927.4033 | 3129.0897 | 8760 | 4337.4748 | 1735.9969 | 2601.4779 | 4338.0557 | 18236.4195 | 7299.2539 | 10688.2688 | 6356.1782 | 0 | 16281.444 | 8760 | 12797.7881 | 340 | 211.45 | 1048.625 | 1390929.9878 | 189624.8638 | 2890.725
644 | C | SOK | TOU | CC | ET | WC | R60 | 5.4272 | 58 | 2.9 | 8760 | 201056.7813 | 0 | 132135.9467 | 65533.1035 | 162408.4576 | 33169.5 | 105036.75 | 74631.375 | 66339 | 55229.2673 | 8760 | 1475.3019 | 20239.3614 | 0 | 0 | 1610.2921 | 12582.5057 | 1943.2939 | -1438.2251 | 4461.594 | 3124.2421 | 8760 | 4336.5613 | 1392.8845 | 2943.6767 | 4338.0557 | 18236.4195 | 7338.31 | 10707.725 | 6378.7492 | 0 | 17770.7317 | 8760 | 12837.4918 | 393.775 | 159.05 | 1048.625 | 1390851.5821 | 189624.8638 | 2801.325
645 | C | SOK | TOU | CC | ET | WC | R60 | 5.4272 | 58 | 4.35 | 8760 | 207387.9452 | 0 | 129068.6512 | 65533.1035 | 162408.4576 | 33468 | 105982 | 75303 | 66936 | 54807.3955 | 8760 | 1475.3019 | 21013.5456 | 0 | 0 | 1580.9165 | 12224.6661 | 1664.834 | -1450.2468 | 4757.0383 | 3113.5052 | 8760 | 4337.4714 | 1206.1917 | 3131.2797 | 4338.0557 | 18236.4195 | 7354.8047 | 10736.9126 | 6409.1168 | 0 | 18550.5875 | 8760 | 12881.8334 | 422.925 | 134.875 | 1048.625 | 1390914.6722 | 189624.8638 | 2755.575
646 | C | SOK | TOU | FC | ET | WC | R600 | 3.8882 | 18 | 0.45 | 8760 | 155751.598 | 0 | 164190.3096 | 65533.1035 | 136175.3067 | 41593.5 | 131712.75 | 93585.375 | 83187 | 38837.7912 | 8760 | 1475.3019 | 10162.2068 | 0 | 0 | 1812.3432 | 11935.724 | 4627.6037 | -1162.2483 | 1458.9434 | 2938.6022 | 8760 | 3331.106 | 2530.051 | 801.055 | 3332.6921 | 13065.0481 | 5566.6442 | 9271.5319 | 5942.2403 | 0 | 8050.5764 | 8760 | 11115.5289 | 160.575 | 532.65 | 1166.025 | 1191115.3007 | 189624.8638 | 2192.875
647 | C | SOK | TOU | FC | ET | WC | R600 | 3.8882 | 18 | 0.9 | 8760 | 162983.9812 | 0 | 162067.9511 | 65533.1035 | 136175.3067 | 41604 | 131746 | 93609 | 83208 | 38870.9368 | 8760 | 1475.3019 | 10739.3168 | 0 | 0 | 1639.1687 | 11758.5242 | 4558.0483 | -1228.2057 | 1521.5773 | 2935.6157 | 8760 | 3331.142 | 2499.4444 | 831.6976 | 3332.6921 | 13065.0481 | 5647.5757 | 9271.7733 | 5942.8065 | 0 | 8634.057 | 8760 | 11116.814 | 169.45 | 523.95 | 1166.025 | 1191187.8308 | 189624.8638 | 2104.475
648 | C | SOK | TOU | FC | ET | WC | R600 | 3.8882 | 18 | 1.35 | 8760 | 165904.3224 | 0 | 160985.7732 | 65533.1035 | 136175.3067 | 41629.5 | 131826.75 | 93666.375 | 83259 | 38892.6158 | 8760 | 1475.3019 | 10961.7826 | 0 | 0 | 1620.6558 | 11651.3991 | 4500.0711 | -1246.0641 | 1581.9686 | 2930.3372 | 8760 | 3331.3827 | 2474.8351 | 856.5476 | 3332.6921 | 13065.0481 | 5665.3085 | 9276.1545 | 5946.7537 | 0 | 8863.0515 | 8760 | 11124.8819 | 178.675 | 515.15 | 1166.025 | 1191161.9043 | 189624.8638 | 2070.7
649 | C | SOK | TOU | FC | ET | WC | R600 | 3.8882 | 24.5 | 0.6 | 8760 | 155697.7814 | 0 | 157181.2769 | 65533.1035 | 136175.3067 | 41212.5 | 130506.25 | 92728.125 | 82425 | 39036.5816 | 8760 | 1475.3019 | 12048.0862 | 0 | 0 | 1625.5419 | 11300.8728 | 4044.9877 | -1248.9905 | 2063.228 | 3062.5443 | 8760 | 3332.2821 | 2189.2927 | 1142.9894 | 3332.6921 | 13065.0481 | 5653.1871 | 9284.8394 | 5956.6074 | 0 | 9767.0246 | 8760 | 11122.5904 | 221.85 | 465.025 | 1166.025 | 1191038.515 | 189624.8638 | 2378.45
650 | C | SOK | TOU | FC | ET | WC | R600 | 3.8882 | 24.5 | 1.25 | 8760 | 163423.8148 | 0 | 153730.007 | 65533.1035 | 136175.3067 | 41211 | 130501.5 | 92724.75 | 82422 | 38390.6028 | 8760 | 1475.3019 | 12762.371 | 0 | 0 | 1513.3456 | 11022.4521 | 3864.423 | -1309.6984 | 2232.4504 | 3061.5975 | 8760 | 3331.9706 | 2110.4227 | 1221.5479 | 3332.6921 | 13065.0481 | 5719.314 | 9289.6802 | 5963.6986 | 0 | 10485.5408 | 8760 | 11127.0687 | 244.8 | 442.05 | 1166.025 | 1191318.4178 | 189624.8638 | 2290.325
651 | C | SOK | TOU | FC | ET | WC | R600 | 3.8882 | 24.5 | 1.85 | 8760 | 166944.5575 | 0 | 152040.3696 | 65533.1035 | 136175.3067 | 41112 | 130188 | 92502 | 82224 | 38059.3934 | 8760 | 1475.3019 | 13085.5492 | 0 | 0 | 1501.0046 | 10865.3009 | 3750.5869 | -1321.7409 | 2339.5735 | 3057.1505 | 8760 | 3331.8884 | 2064.3301 | 1267.5583 | 3332.6921 | 13065.0481 | 5730.0043 | 9284.4787 | 5960.2145 | 0 | 10814.6028 | 8760 | 11123.713 | 260.9 | 424.3 | 1166.025 | 1191207.0159 | 189624.8638 | 2249.725
652 | C | SOK | TOU | FC | ET | WC | R600 | 3.8882 | 31 | 0.8 | 8760 | 156410.2763 | 0 | 150730.9569 | 65533.1035 | 136175.3067 | 40179 | 127233.5 | 90402.75 | 80358 | 41603.3546 | 8760 | 1475.3019 | 13393.3729 | 0 | 0 | 1484.212 | 10673.4658 | 3571.5004 | -1311.516 | 2499.0507 | 3126.0038 | 8760 | 3331.497 | 1924.8739 | 1406.6231 | 3332.6921 | 13065.0481 | 5713.3932 | 9246.9382 | 5921.6141 | 0 | 11014.9548 | 8760 | 11071.7605 | 260.825 | 408.825 | 1166.025 | 1191106.1762 | 189624.8638 | 2537.55
653 | C | SOK | TOU | FC | ET | WC | R600 | 3.8882 | 31 | 1.55 | 8760 | 163333.9985 | 0 | 146804.2188 | 65533.1035 | 136175.3067 | 40408.5 | 127960.25 | 90919.125 | 80817 | 40079.5764 | 8760 | 1475.3019 | 14127.5759 | 0 | 0 | 1400.7942 | 10315.7194 | 3313.8601 | -1352.6593 | 2755.1561 | 3118.6153 | 8760 | 3332.8528 | 1816.4307 | 1516.4221 | 3332.6921 | 13065.0481 | 5753.1487 | 9276.7185 | 5953.3778 | 0 | 11758.1083 | 8760 | 11107.6484 | 296.65 | 376.825 | 1166.025 | 1191084.3139 | 189624.8638 | 2463.525
654 | C | SOK | TOU | FC | ET | WC | R600 | 3.8882 | 31 | 2.35 | 8760 | 167793.8926 | 0 | 144838.5998 | 65533.1035 | 136175.3067 | 40168.5 | 127200.25 | 90379.125 | 80337 | 40043.9826 | 8760 | 1475.3019 | 14598.3638 | 0 | 0 | 1393.5054 | 10106.6708 | 3134.3702 | -1364.6664 | 2920.4971 | 3112.1572 | 8760 | 3332.897 | 1732.5834 | 1600.3136 | 3332.6921 | 13065.0481 | 5765.1715 | 9265.5025 | 5942.6582 | 0 | 12234.7384 | 8760 | 11098.8424 | 317.95 | 351.525 | 1166.025 | 1191050.3964 | 189624.8638 | 2417.75
655 | C | SOK | TOU | FC | ET | WC | R60 | 3.8882 | 38 | 0.95 | 8760 | 158381.8232 | 0 | 145447.5592 | 65533.1035 | 136175.3067 | 39697.5 | 125708.75 | 89319.375 | 79395 | 41541.3661 | 8760 | 1475.3019 | 14495.6613 | 0 | 0 | 1372.173 | 10094.3819 | 3133.3198 | -1353.2483 | 2909.1929 | 3161.9165 | 8760 | 3333.393 | 1696.4714 | 1636.9216 | 3332.6921 | 13065.0481 | 5748.7212 | 9258.0509 | 5931.5747 | 0 | 12054.9663 | 8760 | 11067.7457 | 299.9 | 361.725 | 1166.025 | 1191036.0688 | 189624.8638 | 2690.375
656 | C | SOK | TOU | FC | ET | WC | R60 | 3.8882 | 38 | 1.9 | 8760 | 166970.364 | 0 | 140355.3987 | 65533.1035 | 136175.3067 | 39520.5 | 125148.25 | 88921.125 | 79041 | 40706.155 | 8760 | 1475.3019 | 15470.7796 | 0 | 0 | 1295.3333 | 9617.5855 | 2800.2601 | -1390.7738 | 3223.1434 | 3153.3086 | 8760 | 3333.2777 | 1552.3952 | 1780.8825 | 3332.6921 | 13065.0481 | 5782.3188 | 9256.7653 | 5934.8811 | 0 | 13037.6241 | 8760 | 11071.6067 | 342.825 | 315.85 | 1166.025 | 1191039.095 | 189624.8638 | 2605.05
657 | C | SOK | TOU | FC | ET | WC | R60 | 3.8882 | 38 | 2.85 | 8760 | 171828.9609 | 0 | 137960.8084 | 65533.1035 | 136175.3067 | 39573 | 125314.5 | 89039.25 | 79146 | 39891.6529 | 8760 | 1475.3019 | 15997.8349 | 0 | 0 | 1269.341 | 9413.1611 | 2551.6506 | -1405.5572 | 3473.0524 | 3151.2773 | 8760 | 3333.5411 | 1434.4587 | 1899.0824 | 3332.6921 | 13065.0481 | 5794.7868 | 9274.6704 | 5951.7451 | 0 | 13564.891 | 8760 | 11098.9621 | 375.35 | 284.2 | 1166.025 | 1191214.835 | 189624.8638 | 2558.425
658 | C | SOK | TOU | FC | ET | WC | R60 | 3.8882 | 44.5 | 1.1 | 8760 | 162653.742 | 0 | 140893.8628 | 65533.1035 | 136175.3067 | 39414 | 124811 | 88681.5 | 78828 | 41300.0932 | 8760 | 1475.3019 | 15409.846 | 0 | 0 | 1294.4407 | 9565.6835 | 2878.5538 | -1385.3506 | 3151.04 | 3176.8146 | 8760 | 3333.4011 | 1569.301 | 1764.1001 | 3332.6921 | 13065.0481 | 5776.2264 | 9263.4195 | 5937.7513 | 0 | 12933.069 | 8760 | 11069.0603 | 324.8 | 332.1 | 1166.025 | 1191206.4059 | 189624.8638 | 2801.2
659 | C | SOK | TOU | FC | ET | WC | R60 | 3.8882 | 44.5 | 2.25 | 8760 | 172440.4456 | 0 | 135241.4897 | 65533.1035 | 136175.3067 | 39042 | 123633 | 87844.5 | 78084 | 41130.5111 | 8760 | 1475.3019 | 16563.9297 | 0 | 0 | 1198.7085 | 9042.7105 | 2442.9396 | -1422.7675 | 3551.1969 | 3172.7097 | 8760 | 3332.8797 | 1370.4322 | 1962.4474 | 3332.6921 | 13065.0481 | 5809.3516 | 9250.8582 | 5928.8721 | 0 | 14091.0598 | 8760 | 11060.7445 | 376.35 | 274.35 | 1166.025 | 1191094.4352 | 189624.8638 | 2711.05
660 | C | SOK | TOU | FC | ET | WC | R60 | 3.8882 | 44.5 | 3.35 | 8760 | 177391.1829 | 0 | 132109.6985 | 65533.1035 | 136175.3067 | 39064.5 | 123704.25 | 87895.125 | 78129 | 40485.4307 | 8760 | 1475.3019 | 17160.4075 | 0 | 0 | 1171.7135 | 8790.0234 | 2180.7563 | -1436.6206 | 3811.309 | 3167.8754 | 8760 | 3333.1385 | 1247.8823 | 2085.2563 | 3332.6921 | 13065.0481 | 5823.0657 | 9263.9713 | 5944.291 | 0 | 14687.5487 | 8760 | 11083.3343 | 410.325 | 240.75 | 1166.025 | 1191073.7565 | 189624.8638 | 2669.075