## User Parameters
| Country | ηboiler | Cconversion, fossil | Cconversion, elec | CO2conversion,heat,fossil | CO2conversion,conventional, elec | Cost Solar Thermal System(FP) | Cost Solar Thermal System(ET) | Installation CostsSolarSystem | Cost Storage | Cost Chillerthermal | Cost Chillerref | Cost Heat Rejection | Installation CostsChiller;th | Installation CostsChiller;ref | Cfuel | Celectricity | Cwater | Cplanning,ref | Coperating,ref | Cmaintance,ref | Cplanning,SC+ | Coperating,SC+ | Cmaintance,SC+ | i | n | a
|  | [-] | [kWhheat, fossil/kWhPE] | [kWhelec, fossil/kWhPE] | [kgCO2l/kWhheat,useful] | [kgCO2l/kWhheat,useful] | [€/m²] | [€/m²] | [€/m²] | [€/m³] | [€] | [€] | [€] | [€] | [€] | [€/kWh] | [€/kWh] | [€/m³] | [€] | [€] | [€] | [€] | [€] | [€] | [%] | [a] | [-]
1 |  | 0.9 | 0.9 | 0.6 | 0.25 | 0.6 | 350 | 550 | 1 | 1000 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 20 | 8
1 | Italy | 0.9 | 0.9 | 0.6 | 0.25 | 0.6 | 350 | 550 | 1 | 1000 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 20 | 8
2 | Germany | 0.9 | 0.9 | 0.6 | 0.25 | 0.6 | 350 | 550 | 1 | 1000 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 20 | 8
3 | France | 0.9 | 0.9 | 0.6 | 0.25 | 0.6 | 350 | 550 | 1 | 1000 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 20 | 8
4 | Austria | 0.9 | 0.9 | 0.6 | 0.25 | 0.6 | 350 | 550 | 1 | 1000 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 20 | 8
5 | Spain | 0.9 | 0.9 | 0.6 | 0.25 | 0.6 | 350 | 550 | 1 | 1000 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 20 | 8
6 | Greece | 0.9 | 0.9 | 0.6 | 0.25 | 0.6 | 350 | 550 | 1 | 1000 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 20 | 8
7 | Portugal | 0.9 | 0.9 | 0.6 | 0.25 | 0.6 | 350 | 550 | 1 | 1000 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 20 | 8
8 | Sweden | 0.9 | 0.9 | 0.6 | 0.25 | 0.6 | 350 | 550 | 1 | 1000 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 20 | 8
9 | General | 0.9 | 0.9 | 0.6 | 0.25 | 0.6 | 350 | 550 | 1 | 1000 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 20 | 8
10 | User | 0.9 | 0.9 | 0.6 | 0.25 | 0.6 | 350 | 550 | 1 | 1000 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 20 | 8
row containing the integral data in single excel files (8673 in case of hourly data, 8762 in case of UNIBG, 15 in case of monthly data)
15
1 | EURAC | 8763
2 | ISE | 15
3 | AEE | 15
4 | UNIBG | 8762
5 | CRES | 8763
MACRO

## Enviromental & Economic Results
Code | Code | ΔPEfossil | ΔPEelectricity | PEsave | PEref | Relative PEsave | PERSC+ | PERref | COPPE,SC+ | COPPE, ref | CO2save | Isolar system | Ichiller, thermal | Ichiller,compression | Coperating,SC+ | Coperating,ref | Cannual, ref | Cannual, SC+ | CPE
|  | [kWhPE] | [kWhPE] | [kWhPE] | [kWhPE] | [%] | [-] | [-] | [-] | [-] | [kgCO2] | [€] | [€] | [€] | [€/a] | [€/a] | [€/a] | [€/a] | [€/kWh/a]
1 | E-SOR-NAP-CC-ET-HC-R100 | 4000.8598 | 660.6837 | 4661.5435 | 15248.0111 | 0.30571 | 1.3984 | 0.99021 | 2.4717 | 5.14 | 17104.5786 | 19350 | 3 | 4 | 8859.9577 | 12857.1417 | 12898.1417 | 163692.9577 | 32.3487
2 | E-SOR-NAP-CC-ET-HC-R100 | 2072.9321 | 614.1605 | 2687.0926 | 15232.3494 | 0.17641 | 1.1791 | 0.9904 | 2.0165 | 5.1401 | 9315.3292 | 16575 | 3 | 4 | 10608.9113 | 12843.0465 | 12884.0465 | 143241.9113 | 48.5126
3 | E-SOR-NAP-CC-ET-HC-R100 | -624.2501 | 556.0004 | -68.2497 | 15223.6533 | -0.0044831 | 0.96686 | 0.99053 | 1.5861 | 5.1406 | -1570.333 | 13425 | 3 | 4 | 13063.4544 | 12835.2295 | 12876.2295 | 120496.4544 | -1576.8604
4 | E-SOR-NAP-CC-ET-HC-R100 | -2891.2719 | 506.3498 | -2384.9222 | 15212.6152 | -0.15677 | 0.83967 | 0.99067 | 1.3582 | 5.1405 | -10721.1715 | 10650 | 3 | 4 | 15123.6201 | 12825.2852 | 12866.2852 | 100356.6201 | -36.6848
5 | E-SOR-NAP-CC-ET-HC-R100 | -5262.6387 | 453.7355 | -4808.9032 | 15188.9177 | -0.31661 | 0.73794 | 0.99097 | 1.189 | 5.1409 | -20294.3288 | 7825 | 3 | 4 | 17268.0985 | 12803.965 | 12844.965 | 79901.0986 | -13.9442
6 | E-SOR-NAP-CC-ET-HC-R100 | 2732.8263 | 655.6469 | 3388.4733 | 15261.4252 | 0.22203 | 1.2478 | 0.99005 | 2.1948 | 5.14 | 12024.0502 | 18600 | 3 | 4 | 10016.2787 | 12869.2106 | 12910.2106 | 158849.2787 | 43.0693
7 | E-SOR-NAP-CC-ET-HC-R100 | 1240.943 | 615.9838 | 1856.9267 | 15249.4683 | 0.12177 | 1.1055 | 0.99022 | 1.8972 | 5.1405 | 5990.4114 | 15925 | 3 | 4 | 11372.0179 | 12858.4568 | 12899.4568 | 138805.0179 | 67.8032
8 | E-SOR-NAP-CC-ET-HC-R100 | -1052.2003 | 560.4546 | -491.7458 | 15236.0156 | -0.032275 | 0.9407 | 0.99039 | 1.5528 | 5.1407 | -3274.7104 | 12925 | 3 | 4 | 13457.0699 | 12846.3623 | 12887.3623 | 116890.0699 | -211.4969
9 | E-SOR-NAP-CC-ET-HC-R100 | -3458.4622 | 507.4155 | -2951.0467 | 15219.7994 | -0.1939 | 0.8135 | 0.99058 | 1.3152 | 5.1405 | -12988.1564 | 10200 | 3 | 4 | 15639.9275 | 12831.7608 | 12872.7608 | 97272.9276 | -28.6001
10 | E-SOR-NAP-CC-ET-HC-R10 | -5815.9907 | 454.6628 | -5361.3279 | 15192.529 | -0.35289 | 0.71809 | 0.99089 | 1.1604 | 5.1402 | -22506.1913 | 7525 | 3 | 4 | 17768.8154 | 12807.2215 | 12848.2215 | 78001.8155 | -12.1525
11 | E-SOR-NAP-CC-ET-HC-R10 | 1135.7699 | 649.4572 | 1785.2271 | 15263.9742 | 0.11696 | 1.0993 | 0.99005 | 1.916 | 5.1405 | 5625.5081 | 17850 | 3 | 4 | 11459.6322 | 12871.4994 | 12912.4994 | 154292.6322 | 79.1945
12 | E-SOR-NAP-CC-ET-HC-R10 | -253.325 | 613.4863 | 360.1613 | 15250.5997 | 0.023616 | 0.9944 | 0.99021 | 1.7297 | 5.1406 | 9.177 | 15225 | 3 | 4 | 12719.366 | 12859.4652 | 12900.4652 | 134552.366 | 337.7707
13 | E-SOR-NAP-CC-ET-HC-R10 | -2265.565 | 557.0603 | -1708.5047 | 15233.9829 | -0.11215 | 0.87315 | 0.99041 | 1.494 | 5.1405 | -8133.8261 | 12375 | 3 | 4 | 14549.2916 | 12844.5193 | 12885.5193 | 113582.2917 | -58.9385
14 | E-SOR-NAP-CC-ET-HC-R10 | -4627.5415 | 499.8789 | -4127.6625 | 15214.0358 | -0.27131 | 0.76402 | 0.99066 | 1.2716 | 5.1407 | -17677.0343 | 9800 | 3 | 4 | 16691.428 | 12826.568 | 12867.568 | 95124.4281 | -19.9282
15 | E-SOR-NAP-CC-ET-HC-R10 | -7450.4722 | 441.8557 | -7008.6165 | 15172.3087 | -0.46193 | 0.66468 | 0.99114 | 1.1298 | 5.1403 | -29065.4627 | 7175 | 3 | 4 | 19229.3321 | 12789.0206 | 12830.0206 | 76662.3322 | -9.1077
16 | E-SOR-NAP-CC-ET-HC-R600 | 2686.7994 | 780.4033 | 3467.2027 | 12221.4731 | 0.2837 | 1.4531 | 1.0634 | 2.3898 | 5.1781 | 12047.8699 | 19350 | 3 | 4 | 7172.7389 | 10059.1003 | 10100.1003 | 162005.7389 | 43.8122
17 | E-SOR-NAP-CC-ET-HC-R600 | 1146.3278 | 736.7682 | 1883.0961 | 12204.0309 | 0.1543 | 1.2312 | 1.0638 | 2.0202 | 5.1781 | 5813.2584 | 16575 | 3 | 4 | 8569.651 | 10043.407 | 10084.407 | 141202.651 | 69.6291
18 | E-SOR-NAP-CC-ET-HC-R600 | -1387.8989 | 676.3924 | -711.5065 | 12175.5087 | -0.058438 | 0.98425 | 1.0644 | 1.5981 | 5.1783 | -4424.275 | 13425 | 3 | 4 | 10861.0265 | 10017.7529 | 10058.7529 | 118294.0265 | -152.1213
19 | E-SOR-NAP-CC-ET-HC-R600 | -3647.515 | 624.981 | -3022.534 | 12143.1191 | -0.24891 | 0.8346 | 1.065 | 1.3597 | 5.1777 | -13548.4251 | 10650 | 3 | 4 | 12896.3651 | 9988.5902 | 10029.5902 | 98129.3651 | -29.1477
20 | E-SOR-NAP-CC-ET-HC-R600 | -6020.9484 | 567.3381 | -5453.6103 | 12106.6145 | -0.45047 | 0.71916 | 1.0659 | 1.1866 | 5.1786 | -23138.23 | 7825 | 3 | 4 | 15034.1977 | 9955.7471 | 9996.7471 | 77667.1979 | -12.4084
21 | E-SOR-NAP-CC-ET-HC-R600 | 1527.3254 | 775.8052 | 2303.1306 | 12220.8586 | 0.18846 | 1.2826 | 1.0634 | 2.1317 | 5.1781 | 7402.3104 | 18600 | 3 | 4 | 8218.4614 | 10058.5374 | 10099.5374 | 157051.4614 | 63.8053
22 | E-SOR-NAP-CC-ET-HC-R600 | 146.2606 | 735.9355 | 882.1961 | 12209.6546 | 0.072254 | 1.1222 | 1.0636 | 1.8713 | 5.1781 | 1811.6016 | 15925 | 3 | 4 | 9475.2737 | 10048.4696 | 10089.4696 | 136908.2737 | 143.7535
23 | E-SOR-NAP-CC-ET-HC-R600 | -1923.3602 | 680.0764 | -1243.2838 | 12188.5633 | -0.102 | 0.94513 | 1.0641 | 1.563 | 5.1785 | -6559.9802 | 12925 | 3 | 4 | 11352.4716 | 10029.4933 | 10070.4933 | 114785.4716 | -84.2245
24 | E-SOR-NAP-CC-ET-HC-R600 | -4199.4117 | 624.7781 | -3574.6337 | 12157.0461 | -0.29404 | 0.80532 | 1.0648 | 1.3262 | 5.1781 | -15756.3502 | 10200 | 3 | 4 | 13405.7321 | 10001.1284 | 10042.1284 | 95038.7322 | -23.7777
25 | E-SOR-NAP-CC-ET-HC-R60 | -6513.3453 | 568.6188 | -5944.7264 | 12112.7009 | -0.49078 | 0.69962 | 1.0657 | 1.1584 | 5.1785 | -25105.683 | 7525 | 3 | 4 | 15482.0604 | 9961.2209 | 10002.2209 | 75715.0604 | -11.054
26 | E-SOR-NAP-CC-ET-HC-R60 | -199.4449 | 765.4764 | 566.0314 | 12220.9746 | 0.046316 | 1.0914 | 1.0634 | 1.8467 | 5.1777 | 478.0143 | 17850 | 3 | 4 | 9778.8607 | 10058.6461 | 10099.6461 | 152611.8608 | 251.7744
27 | E-SOR-NAP-CC-ET-HC-R60 | -1388.3257 | 732.0592 | -656.2665 | 12199.3403 | -0.053795 | 0.98815 | 1.0638 | 1.6918 | 5.1781 | -4333.2042 | 15225 | 3 | 4 | 10849.4325 | 10039.1749 | 10080.1749 | 132682.4326 | -186.8178
28 | E-SOR-NAP-CC-ET-HC-R60 | -3156.2356 | 679.3364 | -2476.8991 | 12172.9892 | -0.20348 | 0.86569 | 1.0644 | 1.4759 | 5.1784 | -11492.7148 | 12375 | 3 | 4 | 12448.4815 | 10015.4714 | 10056.4714 | 111481.4816 | -40.9484
29 | E-SOR-NAP-CC-ET-HC-R60 | -5357.8024 | 618.6175 | -4739.1848 | 12140.0556 | -0.39038 | 0.74974 | 1.0651 | 1.2648 | 5.1779 | -20400.1802 | 9800 | 3 | 4 | 14436.6946 | 9985.843 | 10026.843 | 92869.6946 | -17.4804
30 | E-SOR-NAP-CC-ET-HC-R60 | -8208.0392 | 561.5859 | -7646.4533 | 12071.0823 | -0.63345 | 0.63899 | 1.0666 | 1.1113 | 5.1781 | -31896.1804 | 7175 | 3 | 4 | 16974.0587 | 9923.7749 | 9964.7749 | 74407.0587 | -8.4277
31 | E-SOR-NAP-CC-ET-WC-R100 | 6900.7455 | 2316.8628 | 9217.6083 | 21007.8475 | 0.43877 | 1.7405 | 0.99086 | 3.6798 | 5.0795 | 31464.4201 | 27175 | 3 | 4 | 10139.5512 | 17714.6889 | 17755.6889 | 227572.5512 | 22.7626
32 | E-SOR-NAP-CC-ET-WC-R100 | 4533.2958 | 2285.8027 | 6819.0985 | 20974.3533 | 0.32512 | 1.4478 | 0.99116 | 2.8916 | 5.0796 | 21942.8543 | 23150 | 3 | 4 | 12258.7585 | 17684.5682 | 17725.5682 | 197491.7585 | 26.3622
33 | E-SOR-NAP-CC-ET-WC-R100 | 1235.338 | 2242.0884 | 3477.4265 | 20955.7749 | 0.16594 | 1.1716 | 0.99123 | 2.1667 | 5.0783 | 8678.1662 | 19075 | 3 | 4 | 15236.4677 | 17667.8851 | 17708.8851 | 167869.4677 | 43.1815
34 | E-SOR-NAP-CC-ET-WC-R100 | -2508.0737 | 2193.6767 | -314.3969 | 20936.4105 | -0.015017 | 0.96284 | 0.99138 | 1.6733 | 5.078 | -6376.1668 | 15000 | 3 | 4 | 18617.1729 | 17650.4629 | 17691.4629 | 138650.1729 | -384.7325
35 | E-SOR-NAP-CC-ET-WC-R100 | -5669.5781 | 2147.7283 | -3521.8498 | 20894.6623 | -0.16855 | 0.83661 | 0.99174 | 1.4444 | 5.0779 | -19098.7652 | 10925 | 3 | 4 | 21452.5551 | 17612.9154 | 17653.9154 | 108885.5551 | -25.9045
36 | E-SOR-NAP-CC-ET-WC-R100 | 5108.8282 | 2307.2171 | 7416.0454 | 21029.0898 | 0.35266 | 1.5088 | 0.99072 | 3.0577 | 5.0802 | 24280.6748 | 26125 | 3 | 4 | 11777.2209 | 17733.8019 | 17774.8019 | 220810.2209 | 27.3779
37 | E-SOR-NAP-CC-ET-WC-R100 | 3089.7496 | 2282.7433 | 5372.493 | 21002.4174 | 0.2558 | 1.3127 | 0.99093 | 2.5712 | 5.0798 | 16163.5708 | 22200 | 3 | 4 | 13585.0722 | 17709.7993 | 17750.7993 | 191218.0722 | 32.288
38 | E-SOR-NAP-CC-ET-WC-R100 | 384.569 | 2244.8214 | 2629.3904 | 20979.1175 | 0.12533 | 1.117 | 0.99108 | 2.0554 | 5.0791 | 5279.6448 | 18325 | 3 | 4 | 16021.5358 | 17688.8681 | 17729.8681 | 162654.5358 | 55.1172
39 | E-SOR-NAP-CC-ET-WC-R100 | -3128.0714 | 2196.7608 | -931.3106 | 20947.6311 | -0.044459 | 0.93566 | 0.99133 | 1.6292 | 5.0787 | -8851.0174 | 14400 | 3 | 4 | 19183.4199 | 17660.5489 | 17701.5489 | 134416.4199 | -125.3233
40 | E-SOR-NAP-CC-ET-WC-R10 | -6239.256 | 2150.6992 | -4088.5568 | 20897.7036 | -0.19565 | 0.81767 | 0.99175 | 1.4119 | 5.0785 | -21372.5253 | 10525 | 3 | 4 | 21966.2147 | 17615.6397 | 17656.6397 | 106199.2149 | -21.6562
41 | E-SOR-NAP-CC-ET-WC-R10 | 2631.1138 | 2298.3885 | 4929.5024 | 21024.3014 | 0.23447 | 1.2759 | 0.99076 | 2.4639 | 5.0801 | 14355.1029 | 25025 | 3 | 4 | 14008.1938 | 17729.473 | 17770.473 | 214241.1938 | 39.8561
42 | E-SOR-NAP-CC-ET-WC-R10 | 1156.0822 | 2276.0755 | 3432.1577 | 21001.0092 | 0.16343 | 1.1678 | 0.99096 | 2.2464 | 5.0801 | 8417.7881 | 21300 | 3 | 4 | 15328.1486 | 17708.5244 | 17749.5244 | 185761.1487 | 48.9522
43 | E-SOR-NAP-CC-ET-WC-R10 | -1182.4048 | 2241.1017 | 1058.6969 | 20968.4324 | 0.05049 | 1.029 | 0.99114 | 1.9422 | 5.0786 | -994.4498 | 17525 | 3 | 4 | 17424.4688 | 17679.2542 | 17720.2542 | 157657.4688 | 132.1787
44 | E-SOR-NAP-CC-ET-WC-R10 | -4515.082 | 2188.6362 | -2326.4458 | 20927.728 | -0.11117 | 0.87962 | 0.99149 | 1.5891 | 5.0785 | -14412.601 | 13800 | 3 | 4 | 20418.7145 | 17642.6285 | 17683.6285 | 130851.7146 | -48.6442
45 | E-SOR-NAP-CC-ET-WC-R10 | -7809.3432 | 2141.6536 | -5667.6897 | 20868.5809 | -0.27159 | 0.76898 | 0.99196 | 1.3531 | 5.0778 | -27667.9503 | 10075 | 3 | 4 | 23358.5274 | 17589.4327 | 17630.4327 | 103991.5275 | -15.2374
46 | E-SOR-NAP-CC-ET-WC-R600 | 4947.5487 | 2618.5424 | 7566.0911 | 16644.971 | 0.45456 | 1.9265 | 1.0674 | 3.4866 | 5.1201 | 24154.4321 | 27175 | 3 | 4 | 7683.3421 | 13678.3534 | 13719.3534 | 225116.3421 | 27.9401
47 | E-SOR-NAP-CC-ET-WC-R600 | 2917.2407 | 2587.9767 | 5505.2174 | 16604.3509 | 0.33155 | 1.5728 | 1.068 | 2.8122 | 5.1198 | 15982.2572 | 23150 | 3 | 4 | 9492.421 | 13641.8154 | 13682.8154 | 194725.421 | 32.8856
48 | E-SOR-NAP-CC-ET-WC-R600 | -29.5424 | 2545.2311 | 2515.6887 | 16566.8789 | 0.15185 | 1.2401 | 1.0684 | 2.1541 | 5.1183 | 4123.8823 | 19075 | 3 | 4 | 12136.4809 | 13608.1222 | 13649.1222 | 164769.4809 | 60.0712
49 | E-SOR-NAP-CC-ET-WC-R600 | -3388.1369 | 2493.6503 | -894.4866 | 16511.9763 | -0.054172 | 0.99856 | 1.0694 | 1.7136 | 5.1192 | -9396.4637 | 15000 | 3 | 4 | 15140.7821 | 13558.7166 | 13599.7166 | 135173.7821 | -135.9149
50 | E-SOR-NAP-CC-ET-WC-R600 | -6734.6473 | 2442.4515 | -4292.1958 | 16452.2982 | -0.26089 | 0.83554 | 1.0703 | 1.445 | 5.1191 | -22867.8368 | 10925 | 3 | 4 | 18129.6839 | 13505.0206 | 13546.0206 | 105562.6839 | -21.4381
51 | E-SOR-NAP-CC-ET-WC-R600 | 3266.1389 | 2608.6346 | 5874.7735 | 16631.5843 | 0.35323 | 1.625 | 1.0676 | 2.9131 | 5.1203 | 17412.2798 | 26125 | 3 | 4 | 9190.5626 | 13666.3001 | 13707.3001 | 218223.5626 | 34.8126
52 | E-SOR-NAP-CC-ET-WC-R600 | 1391.8041 | 2582.6699 | 3974.474 | 16608.99 | 0.2393 | 1.3821 | 1.068 | 2.4821 | 5.1205 | 9871.6662 | 22200 | 3 | 4 | 10872.7308 | 13645.9885 | 13686.9885 | 188505.7308 | 43.9854
53 | E-SOR-NAP-CC-ET-WC-R600 | -944.8287 | 2544.0675 | 1599.2388 | 16583.4144 | 0.096436 | 1.1638 | 1.0682 | 2.0669 | 5.1187 | 460.7978 | 18325 | 3 | 4 | 12975.858 | 13623.0059 | 13664.0059 | 159608.858 | 91.2589
54 | E-SOR-NAP-CC-ET-WC-R600 | -4211.6691 | 2491.6255 | -1720.0436 | 16532.7061 | -0.10404 | 0.95319 | 1.0691 | 1.6575 | 5.1194 | -12693.9674 | 14400 | 3 | 4 | 15901.8539 | 13577.3737 | 13618.3737 | 131134.8539 | -68.3218
55 | E-SOR-NAP-CC-ET-WC-R60 | -7211.5683 | 2442.4373 | -4769.1309 | 16461.4456 | -0.28972 | 0.8167 | 1.0701 | 1.4186 | 5.1184 | -24775.5442 | 10525 | 3 | 4 | 18567.1774 | 13513.2751 | 13554.2751 | 102800.1775 | -18.7132
56 | E-SOR-NAP-CC-ET-WC-R60 | 723.7107 | 2594.8872 | 3318.5978 | 16631.9679 | 0.19953 | 1.313 | 1.0676 | 2.3726 | 5.1207 | 7219.6547 | 25025 | 3 | 4 | 11487.422 | 13666.6497 | 13707.6497 | 211720.422 | 59.6676
57 | E-SOR-NAP-CC-ET-WC-R60 | -528.2484 | 2574.679 | 2046.4306 | 16602.2986 | 0.12326 | 1.1993 | 1.0681 | 2.1882 | 5.1202 | 2178.138 | 21300 | 3 | 4 | 12599.5919 | 13639.9466 | 13680.9466 | 183032.592 | 82.7546
58 | E-SOR-NAP-CC-ET-WC-R60 | -2498.4685 | 2540.5984 | 42.1299 | 16557.279 | 0.0025445 | 1.0548 | 1.0688 | 1.9188 | 5.12 | -5759.5434 | 17525 | 3 | 4 | 14352.7293 | 13599.4608 | 13640.4608 | 154585.7294 | 3345.495
59 | E-SOR-NAP-CC-ET-WC-R60 | -5403.3965 | 2487.4642 | -2915.9323 | 16501.5457 | -0.17671 | 0.89466 | 1.0695 | 1.6011 | 5.1186 | -17467.8124 | 13800 | 3 | 4 | 16948.886 | 13549.3345 | 13590.3345 | 127381.8861 | -39.0241
60 | E-SOR-NAP-CC-ET-WC-R60 | -8699.6503 | 2436.3449 | -6263.3055 | 16412.1061 | -0.38163 | 0.76291 | 1.0709 | 1.3554 | 5.1185 | -30738.0265 | 10075 | 3 | 4 | 19865.6956 | 13468.8534 | 13509.8534 | 100498.6956 | -13.8886
61 | E-SOR-NAP-CC-FP-HC-R100 | 2425.9276 | 637.5825 | 3063.5101 | 15255.2247 | 0.20082 | 1.2136 | 0.98913 | 2.0382 | 5.1032 | 10766.3478 | 13150 | 3 | 4 | 10292.0768 | 12857.9611 | 12898.9611 | 115525.0768 | 33.4995
62 | E-SOR-NAP-CC-FP-HC-R100 | 614.9994 | 602.3041 | 1217.3036 | 15246.3397 | 0.079842 | 1.0541 | 0.98923 | 1.7255 | 5.1032 | 3463.838 | 11275 | 3 | 4 | 11935.0885 | 12849.9705 | 12890.9705 | 102168.0885 | 73.3401
63 | E-SOR-NAP-CC-FP-HC-R100 | -1801.0567 | 555.0737 | -1245.983 | 15236.0303 | -0.081779 | 0.89672 | 0.98936 | 1.427 | 5.1033 | -6279.1041 | 9125 | 3 | 4 | 14128.5941 | 12840.6872 | 12881.6872 | 87161.5941 | -59.6155
64 | E-SOR-NAP-CC-FP-HC-R100 | -3848.8348 | 514.5801 | -3334.2547 | 15219.7068 | -0.21907 | 0.79586 | 0.98955 | 1.2611 | 5.1032 | -14537.7056 | 7250 | 3 | 4 | 15981.2191 | 12826.0159 | 12867.0159 | 74014.2191 | -18.3391
65 | E-SOR-NAP-CC-FP-HC-R100 | -5863.9792 | 471.3815 | -5392.5977 | 15194.9187 | -0.35489 | 0.71628 | 0.98985 | 1.1422 | 5.1033 | -22670.2808 | 5325 | 3 | 4 | 17798.4598 | 12803.7075 | 12844.7075 | 60431.46 | -8.8245
66 | E-SOR-NAP-CC-FP-HC-R100 | 1181.7879 | 629.3366 | 1811.1245 | 15267.5824 | 0.11863 | 1.1002 | 0.98898 | 1.8463 | 5.1033 | 5776.0458 | 12400 | 3 | 4 | 11427.8816 | 12869.0926 | 12910.0926 | 110660.8816 | 53.9724
67 | E-SOR-NAP-CC-FP-HC-R100 | -195.5863 | 599.1521 | 403.5658 | 15258.5703 | 0.026448 | 0.99617 | 0.98909 | 1.6485 | 5.1033 | 216.2415 | 10625 | 3 | 4 | 12677.4988 | 12860.9623 | 12901.9623 | 97710.4988 | 210.148
68 | E-SOR-NAP-CC-FP-HC-R100 | -2369.3106 | 555.3546 | -1813.956 | 15241.8043 | -0.11901 | 0.86683 | 0.98929 | 1.3946 | 5.1032 | -8551.6514 | 8625 | 3 | 4 | 14645.0631 | 12845.8964 | 12886.8964 | 83678.0631 | -39.0258
69 | E-SOR-NAP-CC-FP-HC-R100 | -4455.4393 | 512.084 | -3943.3553 | 15223.5469 | -0.25903 | 0.77058 | 0.98951 | 1.2307 | 5.1033 | -16968.2839 | 6800 | 3 | 4 | 16532.1088 | 12829.4638 | 12870.4638 | 70965.1089 | -14.7323
70 | E-SOR-NAP-CC-FP-HC-R10 | -6542.0056 | 469.2463 | -6072.7593 | 15198.9259 | -0.39955 | 0.69338 | 0.98979 | 1.1148 | 5.103 | -25385.9451 | 5025 | 3 | 4 | 18413.5671 | 12807.3098 | 12848.3098 | 58646.5671 | -7.5416
71 | E-SOR-NAP-CC-FP-HC-R10 | -589.1064 | 614.2893 | 25.183 | 15266.3416 | 0.0016496 | 0.97134 | 0.98899 | 1.6519 | 5.1032 | -1332.6099 | 11650 | 3 | 4 | 13029.5768 | 12867.9547 | 12908.9547 | 106262.5769 | 3707.0145
72 | E-SOR-NAP-CC-FP-HC-R10 | -1959.2662 | 586.1099 | -1373.1563 | 15250.0443 | -0.090043 | 0.88978 | 0.98918 | 1.5203 | 5.1031 | -6860.2149 | 9925 | 3 | 4 | 14264.9682 | 12853.2945 | 12894.2945 | 93697.9682 | -58.8452
73 | E-SOR-NAP-CC-FP-HC-R10 | -3788.4715 | 545.3361 | -3243.1354 | 15233.3902 | -0.2129 | 0.79982 | 0.98941 | 1.3495 | 5.1035 | -14244.9925 | 8075 | 3 | 4 | 15920.7285 | 12838.3059 | 12879.3059 | 80553.7286 | -20.867
74 | E-SOR-NAP-CC-FP-HC-R10 | -5778.7004 | 499.5942 | -5279.1062 | 15216.393 | -0.34694 | 0.72036 | 0.98961 | 1.183 | 5.1037 | -22282.1446 | 6400 | 3 | 4 | 17724.1127 | 12823.0388 | 12864.0388 | 68957.1127 | -10.6255
75 | E-SOR-NAP-CC-FP-HC-R10 | -8526.7904 | 453.4267 | -8073.3637 | 15172.1745 | -0.53212 | 0.63359 | 0.99014 | 1.0689 | 5.1035 | -33351.4504 | 4675 | 3 | 4 | 20185.2831 | 12783.2278 | 12824.2278 | 57618.2832 | -5.5484
76 | E-SOR-NAP-CC-FP-HC-R600 | 2686.7994 | 800.7636 | 3487.563 | 12241.8334 | 0.28489 | 1.4531 | 1.0616 | 2.3898 | 5.1416 | 12081.8037 | 13150 | 3 | 4 | 7172.7389 | 10071.3165 | 10112.3165 | 112405.7389 | 29.3309
77 | E-SOR-NAP-CC-FP-HC-R600 | 1146.3278 | 757.119 | 1903.4469 | 12224.3817 | 0.15571 | 1.2312 | 1.0619 | 2.0202 | 5.1417 | 5847.1764 | 11275 | 3 | 4 | 8569.651 | 10055.6175 | 10096.6175 | 98802.651 | 46.6028
78 | E-SOR-NAP-CC-FP-HC-R600 | -1387.8989 | 696.7247 | -691.1742 | 12195.841 | -0.056673 | 0.98425 | 1.0626 | 1.5981 | 5.1419 | -4390.3878 | 9125 | 3 | 4 | 10861.0265 | 10029.9523 | 10070.9523 | 83894.0265 | -106.8082
79 | E-SOR-NAP-CC-FP-HC-R600 | -3647.515 | 645.3202 | -3002.1948 | 12163.4583 | -0.24682 | 0.8346 | 1.0632 | 1.3597 | 5.1414 | -13514.5264 | 7250 | 3 | 4 | 12896.3651 | 10000.7937 | 10041.7937 | 70929.3651 | -20.281
80 | E-SOR-NAP-CC-FP-HC-R600 | -6020.9484 | 587.6641 | -5433.2843 | 12126.9404 | -0.44803 | 0.71916 | 1.0641 | 1.1866 | 5.1423 | -23104.3534 | 5325 | 3 | 4 | 15034.1977 | 9967.9426 | 10008.9426 | 57667.1979 | -8.7715
81 | E-SOR-NAP-CC-FP-HC-R600 | 1527.3254 | 796.1764 | 2323.5018 | 12241.2298 | 0.18981 | 1.2826 | 1.0616 | 2.1317 | 5.1416 | 7436.2623 | 12400 | 3 | 4 | 8218.4614 | 10070.7601 | 10111.7601 | 107451.4614 | 41.8935
82 | E-SOR-NAP-CC-FP-HC-R600 | 146.2606 | 756.2875 | 902.5481 | 12230.0066 | 0.073798 | 1.1222 | 1.0618 | 1.8713 | 5.1417 | 1845.5216 | 10625 | 3 | 4 | 9475.2737 | 10060.6808 | 10101.6808 | 94508.2737 | 93.5203
83 | E-SOR-NAP-CC-FP-HC-R600 | -1923.3602 | 700.4177 | -1222.9425 | 12208.9046 | -0.10017 | 0.94513 | 1.0623 | 1.563 | 5.1421 | -6526.0781 | 8625 | 3 | 4 | 11352.4716 | 10041.6981 | 10082.6981 | 80385.4716 | -57.4866
84 | E-SOR-NAP-CC-FP-HC-R600 | -4199.4117 | 645.115 | -3554.2968 | 12177.383 | -0.29188 | 0.80532 | 1.0629 | 1.3262 | 5.1418 | -15722.4553 | 6800 | 3 | 4 | 13405.7321 | 10013.3306 | 10054.3306 | 67838.7322 | -16.2576
85 | E-SOR-NAP-CC-FP-HC-R60 | -6513.3453 | 588.9488 | -5924.3965 | 12133.0309 | -0.48829 | 0.69962 | 1.0639 | 1.1584 | 5.1421 | -25071.7997 | 5025 | 3 | 4 | 15482.0604 | 9973.4189 | 10014.4189 | 55715.0604 | -7.714
86 | E-SOR-NAP-CC-FP-HC-R60 | -199.4449 | 785.8476 | 586.4027 | 12241.3459 | 0.047903 | 1.0914 | 1.0616 | 1.8467 | 5.1413 | 511.9663 | 11650 | 3 | 4 | 9778.8607 | 10070.8688 | 10111.8688 | 103011.8608 | 158.4235
87 | E-SOR-NAP-CC-FP-HC-R60 | -1388.3257 | 752.4263 | -635.8994 | 12219.7075 | -0.052039 | 0.98815 | 1.062 | 1.6918 | 5.1416 | -4299.2589 | 9925 | 3 | 4 | 10849.4325 | 10051.3952 | 10092.3952 | 90282.4326 | -126.1049
88 | E-SOR-NAP-CC-FP-HC-R60 | -3156.2356 | 699.6858 | -2456.5498 | 12193.3385 | -0.20147 | 0.86569 | 1.0626 | 1.4759 | 5.142 | -11458.7992 | 8075 | 3 | 4 | 12448.4815 | 10027.681 | 10068.681 | 77081.4816 | -27.2792
89 | E-SOR-NAP-CC-FP-HC-R60 | -5357.8024 | 638.9519 | -4718.8504 | 12160.39 | -0.38805 | 0.74974 | 1.0633 | 1.2648 | 5.1416 | -20366.2896 | 6400 | 3 | 4 | 14436.6946 | 9998.0436 | 10039.0436 | 65669.6946 | -11.789
90 | E-SOR-NAP-CC-FP-HC-R60 | -8208.0392 | 581.9097 | -7626.1295 | 12091.4061 | -0.63071 | 0.63899 | 1.0648 | 1.1113 | 5.1418 | -31862.3074 | 4675 | 3 | 4 | 16974.0587 | 9935.9692 | 9976.9692 | 54407.0587 | -5.826
91 | E-SOR-NAP-CC-FP-WC-R100 | 5200.3793 | 2274.8738 | 7475.2532 | 20982.4524 | 0.35626 | 1.5178 | 0.99113 | 3.0184 | 5.0802 | 24592.9738 | 18475 | 3 | 4 | 11672.2103 | 17691.8295 | 17732.8295 | 159505.2103 | 18.9656
92 | E-SOR-NAP-CC-FP-WC-R100 | 2868.5836 | 2251.9307 | 5120.5143 | 20958.0457 | 0.24432 | 1.2931 | 0.99126 | 2.4393 | 5.079 | 15227.5524 | 15750 | 3 | 4 | 13762.6581 | 17669.8941 | 17710.8941 | 139795.6581 | 23.8423
93 | E-SOR-NAP-CC-FP-WC-R100 | -121.8884 | 2218.2997 | 2096.4114 | 20941.6878 | 0.10011 | 1.0861 | 0.99141 | 1.9421 | 5.0791 | 3209.6128 | 12975 | 3 | 4 | 16459.5561 | 17655.1805 | 17696.1805 | 120292.5561 | 48.939
94 | E-SOR-NAP-CC-FP-WC-R100 | -3600.6478 | 2178.8548 | -1421.793 | 20915.2475 | -0.067979 | 0.91529 | 0.99161 | 1.5635 | 5.0786 | -10771.1665 | 10200 | 3 | 4 | 19590.3471 | 17631.4165 | 17672.4165 | 101223.3471 | -58.7645
95 | E-SOR-NAP-CC-FP-WC-R100 | -6386.3761 | 2141.8073 | -4244.5688 | 20868.9969 | -0.20339 | 0.81256 | 0.99196 | 1.3904 | 5.0778 | -21975.8255 | 7425 | 3 | 4 | 22078.127 | 17589.8152 | 17630.8152 | 81511.127 | -15.0499
96 | E-SOR-NAP-CC-FP-WC-R100 | 3471.6993 | 2264.2897 | 5735.9891 | 20999.1745 | 0.27315 | 1.3441 | 0.99097 | 2.6071 | 5.0801 | 17660.6136 | 17425 | 3 | 4 | 13249.4685 | 17706.8869 | 17747.8869 | 152682.4685 | 23.5242
97 | E-SOR-NAP-CC-FP-WC-R100 | 1520.1029 | 2245.4545 | 3765.5574 | 20982.0125 | 0.17947 | 1.1908 | 0.9911 | 2.229 | 5.0797 | 9822.8356 | 14800 | 3 | 4 | 15001.7841 | 17691.462 | 17732.462 | 133434.7841 | 30.7265
98 | E-SOR-NAP-CC-FP-WC-R100 | -994.6806 | 2217.7485 | 1223.0679 | 20953.1397 | 0.058372 | 1.0378 | 0.99132 | 1.8673 | 5.0792 | -282.4749 | 12225 | 3 | 4 | 17255.7262 | 17665.4901 | 17706.4901 | 115088.7262 | 79.6213
99 | E-SOR-NAP-CC-FP-WC-R100 | -4195.9246 | 2178.6912 | -2017.2334 | 20918.8937 | -0.096431 | 0.89149 | 0.99155 | 1.5371 | 5.0782 | -13152.5462 | 9600 | 3 | 4 | 20129.4796 | 17634.6952 | 17675.6952 | 96962.4796 | -39.3047
100 | E-SOR-NAP-CC-FP-WC-R10 | -7113.5458 | 2142.1901 | -4971.3557 | 20871.469 | -0.23819 | 0.78969 | 0.99192 | 1.3575 | 5.0774 | -24883.8663 | 7025 | 3 | 4 | 22734.5678 | 17592.0285 | 17633.0285 | 78967.5679 | -12.3376
101 | E-SOR-NAP-CC-FP-WC-R10 | 720.9056 | 2247.1194 | 2968.025 | 20992.8534 | 0.14138 | 1.1379 | 0.99104 | 2.1552 | 5.0801 | 6628.8214 | 16325 | 3 | 4 | 15729.8442 | 17701.1892 | 17742.1892 | 146362.8442 | 43.3354
102 | E-SOR-NAP-CC-FP-WC-R10 | -729.7044 | 2230.8387 | 1501.1343 | 20968.5825 | 0.07159 | 1.0525 | 0.99125 | 1.9764 | 5.0802 | 799.2469 | 13900 | 3 | 4 | 17023.3271 | 17679.3621 | 17720.3621 | 128256.3272 | 73.635
103 | E-SOR-NAP-CC-FP-WC-R10 | -2985.1157 | 2204.7174 | -780.3982 | 20930.8802 | -0.037285 | 0.94232 | 0.99153 | 1.7434 | 5.0795 | -8265.9336 | 11425 | 3 | 4 | 19034.9337 | 17645.446 | 17686.446 | 110467.9338 | -118.8899
104 | E-SOR-NAP-CC-FP-WC-R10 | -5842.9037 | 2167.5214 | -3675.3823 | 20892.6248 | -0.17592 | 0.83144 | 0.99182 | 1.4939 | 5.0788 | -19759.079 | 9000 | 3 | 4 | 21594.8354 | 17611.0438 | 17652.0438 | 93627.8355 | -20.6715
105 | E-SOR-NAP-CC-FP-WC-R10 | -9104.5662 | 2130.434 | -6974.1323 | 20835.7868 | -0.33472 | 0.73281 | 0.99225 | 1.2762 | 5.0778 | -32867.5417 | 6575 | 3 | 4 | 24501.439 | 17559.917 | 17600.917 | 77134.4391 | -8.5363
106 | E-SOR-NAP-CC-FP-WC-R600 | 3195.474 | 2572.4959 | 5767.9699 | 16594.7944 | 0.34758 | 1.6118 | 1.0682 | 2.8686 | 5.1205 | 17069.389 | 18475 | 3 | 4 | 9242.6986 | 13633.204 | 13674.204 | 157075.6986 | 24.8617
107 | E-SOR-NAP-CC-FP-WC-R600 | 1072.2051 | 2550.0689 | 3622.274 | 16557.6817 | 0.21877 | 1.3467 | 1.0688 | 2.3615 | 5.1202 | 8538.9351 | 15750 | 3 | 4 | 11133.7159 | 13599.8174 | 13640.8174 | 137166.7159 | 34.1018
108 | E-SOR-NAP-CC-FP-WC-R600 | -1691.6508 | 2516.1837 | 824.5328 | 16520.6512 | 0.049909 | 1.1079 | 1.0693 | 1.9071 | 5.1198 | -2572.9639 | 12975 | 3 | 4 | 13608.2155 | 13566.5078 | 13607.5078 | 117441.2155 | 125.9303
109 | E-SOR-NAP-CC-FP-WC-R600 | -4879.9379 | 2475.0398 | -2404.8981 | 16475.811 | -0.14597 | 0.91906 | 1.07 | 1.5666 | 5.1196 | -15394.6851 | 10200 | 3 | 4 | 16462.0322 | 13526.1656 | 13567.1656 | 98095.0322 | -35.1482
110 | E-SOR-NAP-CC-FP-WC-R600 | -7721.5822 | 2434.9175 | -5286.6647 | 16414.5645 | -0.32207 | 0.7973 | 1.071 | 1.3743 | 5.1193 | -26828.133 | 7425 | 3 | 4 | 18988.4981 | 13471.0654 | 13512.0654 | 78421.4981 | -12.278
111 | E-SOR-NAP-CC-FP-WC-R600 | 1525.6047 | 2559.4624 | 4085.0671 | 16595.2406 | 0.24616 | 1.3949 | 1.0682 | 2.4813 | 5.12 | 10368.1895 | 17425 | 3 | 4 | 10753.8371 | 13633.5948 | 13674.5948 | 150186.8371 | 33.4174
112 | E-SOR-NAP-CC-FP-WC-R600 | -348.4281 | 2540.6 | 2192.1719 | 16570.695 | 0.13229 | 1.2123 | 1.0686 | 2.156 | 5.1206 | 2840.621 | 14800 | 3 | 4 | 12429.7154 | 13611.5217 | 13652.5217 | 130862.7154 | 53.4676
113 | E-SOR-NAP-CC-FP-WC-R600 | -2622.9313 | 2512.5436 | -110.3877 | 16534.6804 | -0.0066761 | 1.0453 | 1.069 | 1.8426 | 5.1192 | -6304.1526 | 12225 | 3 | 4 | 14461.201 | 13579.1324 | 13620.1324 | 112294.201 | -893.8862
114 | E-SOR-NAP-CC-FP-WC-R600 | -5587.1007 | 2471.8398 | -3115.261 | 16489.3086 | -0.18893 | 0.88568 | 1.0698 | 1.5334 | 5.1194 | -18228.67 | 9600 | 3 | 4 | 17112.5681 | 13538.3186 | 13579.3186 | 93945.5681 | -25.7976
115 | E-SOR-NAP-CC-FP-WC-R60 | -8368.3818 | 2433.0952 | -5935.2866 | 16416.8697 | -0.36154 | 0.77416 | 1.0709 | 1.342 | 5.1191 | -29418.3685 | 7025 | 3 | 4 | 19573.7759 | 13473.1255 | 13514.1255 | 75806.776 | -10.4953
116 | E-SOR-NAP-CC-FP-WC-R60 | -1222.5818 | 2540.2808 | 1317.699 | 16582.2296 | 0.079465 | 1.1425 | 1.0684 | 2.0738 | 5.1202 | -656.5259 | 16325 | 3 | 4 | 13227.0711 | 13621.8827 | 13662.8827 | 143860.0711 | 98.8065
117 | E-SOR-NAP-CC-FP-WC-R60 | -2479.1476 | 2526.0774 | 46.9298 | 16550.7846 | 0.0028355 | 1.0551 | 1.0688 | 1.915 | 5.1199 | -5706.4614 | 13900 | 3 | 4 | 14338.1974 | 13593.5912 | 13634.5912 | 125571.1975 | 2385.1938
118 | E-SOR-NAP-CC-FP-WC-R60 | -4403.8644 | 2500.3476 | -1903.5167 | 16501.0788 | -0.11536 | 0.94395 | 1.0696 | 1.7063 | 5.1195 | -13448.2114 | 11425 | 3 | 4 | 16041.1444 | 13548.8752 | 13589.8752 | 107474.1445 | -49.3215
119 | E-SOR-NAP-CC-FP-WC-R60 | -7006.4558 | 2463.5831 | -4542.8727 | 16442.8876 | -0.27628 | 0.82562 | 1.0706 | 1.4764 | 5.1198 | -23919.8514 | 9000 | 3 | 4 | 18353.1714 | 13496.5287 | 13537.5287 | 90386.1715 | -16.9163
120 | E-SOR-NAP-CC-FP-WC-R60 | -10054.7802 | 2426.9876 | -7627.7926 | 16357.3664 | -0.46632 | 0.71943 | 1.0718 | 1.2774 | 5.1188 | -36174.1416 | 6575 | 3 | 4 | 21041.6559 | 13419.5775 | 13460.5775 | 73674.656 | -7.894
121 | E-SOR-NAP-FC-ET-WC-OFF0 | -1777.4188 | 1121.1525 | -656.2663 | 4145.9618 | -0.15829 | 1.2039 | 1.4594 | 3.1156 | 4.4528 | -5241.0878 | 15925 | 3 | 4 | 3675.4013 | 2702.7367 | 2743.7367 | 131108.4013 | -195.5984
122 | E-SOR-NAP-FC-ET-WC-OFF0 | -3577.418 | 1063.513 | -2513.9051 | 4145.9712 | -0.60635 | 0.86813 | 1.4594 | 2.2271 | 4.4528 | -12537.1505 | 13425 | 3 | 4 | 5330.3529 | 2702.7424 | 2743.7424 | 112763.3529 | -43.7644
123 | E-SOR-NAP-FC-ET-WC-OFF0 | -5776.129 | 1003.8593 | -4772.2698 | 4146.2602 | -1.151 | 0.64828 | 1.4594 | 1.659 | 4.4525 | -21431.4174 | 11250 | 3 | 4 | 7345.5319 | 2702.9158 | 2743.9158 | 97378.5319 | -19.8301
124 | E-SOR-NAP-FC-ET-WC-OFF0 | -7912.2251 | 943.7147 | -6968.5105 | 4147.035 | -1.6804 | 0.52014 | 1.459 | 1.3358 | 4.4513 | -30076.0428 | 8750 | 3 | 4 | 9304.9875 | 2703.3807 | 2744.3807 | 79337.9875 | -10.9914
125 | E-SOR-NAP-FC-ET-WC-OFF0 | -10475.1343 | 881.5393 | -9593.595 | 4146.7159 | -2.3135 | 0.42079 | 1.4592 | 1.087 | 4.4518 | -40431.3051 | 6250 | 3 | 4 | 11649.0976 | 2703.1892 | 2744.1892 | 61682.0977 | -6.1435
126 | E-SOR-NAP-FC-ET-WC-OFF0 | -2160.8506 | 1115.8644 | -1044.9862 | 4145.4792 | -0.25208 | 1.1139 | 1.4596 | 2.8805 | 4.4535 | -6783.6285 | 15325 | 3 | 4 | 4023.4426 | 2702.4472 | 2743.4472 | 126656.4426 | -118.5786
127 | E-SOR-NAP-FC-ET-WC-OFF0 | -3769.7964 | 1065.5465 | -2704.2499 | 4146.0778 | -0.65224 | 0.84401 | 1.4594 | 2.1724 | 4.4527 | -13303.2746 | 12925 | 3 | 4 | 5502.3448 | 2702.8064 | 2743.8064 | 108935.3448 | -39.2684
128 | E-SOR-NAP-FC-ET-WC-OFF0 | -5826.4776 | 1010.2073 | -4816.2703 | 4146.2814 | -1.1616 | 0.6451 | 1.4593 | 1.6604 | 4.4524 | -21622.2316 | 10800 | 3 | 4 | 7386.9926 | 2702.9285 | 2743.9285 | 93819.9927 | -18.9101
129 | E-SOR-NAP-FC-ET-WC-OFF0 | -8063.7976 | 946.9725 | -7116.8251 | 4146.5218 | -1.7163 | 0.51332 | 1.4592 | 1.3255 | 4.4521 | -30676.903 | 8400 | 3 | 4 | 9439.0429 | 2703.0727 | 2744.0727 | 76672.043 | -10.3878
130 | E-SOR-NAP-FC-ET-WC-OFF | -10579.9644 | 881.8662 | -9698.0981 | 4146.9038 | -2.3386 | 0.41762 | 1.4592 | 1.0858 | 4.4517 | -40850.0803 | 6000 | 3 | 4 | 11743.2782 | 2703.302 | 2744.302 | 59776.2783 | -5.8807
131 | E-SOR-NAP-FC-ET-WC-OFF | -2966.5153 | 1114.9187 | -1851.5966 | 4145.7763 | -0.44662 | 0.96403 | 1.4595 | 2.5163 | 4.4531 | -10007.8635 | 14675 | 3 | 4 | 4749.3112 | 2702.6254 | 2743.6254 | 122182.3113 | -64.5058
132 | E-SOR-NAP-FC-ET-WC-OFF | -4306.0488 | 1068.676 | -3237.3728 | 4145.8099 | -0.78088 | 0.78309 | 1.4595 | 2.0434 | 4.4531 | -15443.0684 | 12375 | 3 | 4 | 5982.8666 | 2702.6456 | 2743.6456 | 105015.8667 | -31.5911
133 | E-SOR-NAP-FC-ET-WC-OFF | -6035.1208 | 1018.0612 | -5017.0596 | 4146.0324 | -1.2101 | 0.63097 | 1.4594 | 1.6483 | 4.4527 | -22443.7145 | 10350 | 3 | 4 | 7569.7506 | 2702.7791 | 2743.7791 | 90402.7507 | -17.4722
134 | E-SOR-NAP-FC-ET-WC-OFF | -8272.9168 | 947.7322 | -7325.1846 | 4146.2769 | -1.7667 | 0.504 | 1.4593 | 1.3241 | 4.4524 | -31512.1135 | 8050 | 3 | 4 | 9626.4964 | 2702.9258 | 2743.9258 | 74059.4964 | -9.7357
135 | E-SOR-NAP-FC-ET-WC-OFF | -11208.4374 | 879.3807 | -10329.0567 | 4146.7668 | -2.4909 | 0.3994 | 1.4592 | 1.0754 | 4.4517 | -43368.1151 | 5750 | 3 | 4 | 12310.0468 | 2703.2197 | 2744.2197 | 58343.0469 | -5.3828
136 | E-SOR-NAP-FC-ET-WC-R100 | 697.4379 | 1106.1418 | 1803.5796 | 10920.1803 | 0.16516 | 1.1583 | 0.99403 | 1.7856 | 4.5826 | 4633.321 | 15925 | 3 | 4 | 7769.1588 | 9040.5837 | 9081.5837 | 135202.1588 | 69.9279
137 | E-SOR-NAP-FC-ET-WC-R100 | -1059.9961 | 1059.1975 | -0.79861 | 10914.7734 | -7.3168e-05 | 0.96686 | 0.994 | 1.4874 | 4.5812 | -2474.6552 | 13425 | 3 | 4 | 9374.207 | 9035.7421 | 9076.7421 | 116807.207 | -134897.4465
138 | E-SOR-NAP-FC-ET-WC-R100 | -2865.8413 | 1015.359 | -1850.4822 | 10910.3208 | -0.16961 | 0.82678 | 0.99409 | 1.2744 | 4.5815 | -9771.1001 | 11250 | 3 | 4 | 11021.8209 | 9031.7536 | 9072.7536 | 101054.8209 | -49.7071
139 | E-SOR-NAP-FC-ET-WC-R100 | -4746.2374 | 962.3441 | -3783.8934 | 10908.3112 | -0.34688 | 0.71796 | 0.9941 | 1.1177 | 4.5808 | -17381.0429 | 8750 | 3 | 4 | 12744.11 | 9029.8357 | 9070.8357 | 82777.11 | -19.479
140 | E-SOR-NAP-FC-ET-WC-R100 | -6880.5981 | 905.6195 | -5974.9786 | 10903.8431 | -0.54797 | 0.62469 | 0.99411 | 0.9858 | 4.58 | -26013.0265 | 6250 | 3 | 4 | 14695.1293 | 9025.8589 | 9066.8589 | 64728.1294 | -9.3157
141 | E-SOR-NAP-FC-ET-WC-R100 | -265.8473 | 1097.446 | 831.5987 | 10922.2924 | 0.076138 | 1.0466 | 0.99398 | 1.637 | 4.5826 | 765.6874 | 15325 | 3 | 4 | 8643.3189 | 9042.5436 | 9083.5436 | 131276.3189 | 146.9372
142 | E-SOR-NAP-FC-ET-WC-R100 | -1806.8406 | 1056.2865 | -750.5541 | 10917.9917 | -0.068745 | 0.90473 | 0.99399 | 1.4131 | 4.582 | -5466.8848 | 12925 | 3 | 4 | 10051.077 | 9038.6902 | 9079.6902 | 113484.077 | -139.1031
143 | E-SOR-NAP-FC-ET-WC-R100 | -3375.7005 | 1013.1992 | -2362.5014 | 10914.9732 | -0.21645 | 0.79489 | 0.99402 | 1.2376 | 4.5814 | -11814.1368 | 10800 | 3 | 4 | 11486.1542 | 9035.9123 | 9076.9123 | 97919.1544 | -37.6052
144 | E-SOR-NAP-FC-ET-WC-R100 | -5249.113 | 962.6623 | -4286.4507 | 10912.0442 | -0.39282 | 0.69419 | 0.99396 | 1.0876 | 4.5798 | -19392.0148 | 8400 | 3 | 4 | 13199.8763 | 9033.2098 | 9074.2098 | 80432.8764 | -16.6475
145 | E-SOR-NAP-FC-ET-WC-R10 | -7463.0474 | 901.4182 | -6561.6292 | 10907.7637 | -0.60156 | 0.60367 | 0.99391 | 0.9496 | 4.5782 | -28349.826 | 6000 | 3 | 4 | 15225.3415 | 9029.361 | 9070.361 | 63258.3415 | -8.2583
146 | E-SOR-NAP-FC-ET-WC-R10 | -1687.3844 | 1084.7432 | -602.6413 | 10920.913 | -0.055182 | 0.91634 | 0.99397 | 1.4769 | 4.5823 | -4941.6324 | 14675 | 3 | 4 | 9929.1294 | 9041.319 | 9082.319 | 127362.1294 | -196.269
147 | E-SOR-NAP-FC-ET-WC-R10 | -3070.5687 | 1043.6775 | -2026.8912 | 10919.1209 | -0.18563 | 0.81554 | 0.99399 | 1.3163 | 4.5818 | -10542.8123 | 12375 | 3 | 4 | 11196.9374 | 9039.614 | 9080.614 | 110229.9374 | -49.9037
148 | E-SOR-NAP-FC-ET-WC-R10 | -4678.4557 | 999.3833 | -3679.0724 | 10917.1 | -0.337 | 0.72317 | 0.99395 | 1.1583 | 4.5812 | -17048.1841 | 10350 | 3 | 4 | 12668.8871 | 9037.8784 | 9078.8784 | 95501.8871 | -23.4904
149 | E-SOR-NAP-FC-ET-WC-R10 | -6710.8258 | 945.5119 | -5765.3138 | 10913.3403 | -0.52828 | 0.63266 | 0.99395 | 1.0234 | 4.58 | -25267.4499 | 8050 | 3 | 4 | 14526.8764 | 9034.3791 | 9075.3791 | 78959.8764 | -12.1215
150 | E-SOR-NAP-FC-ET-WC-R10 | -9590.1695 | 874.0299 | -8716.1396 | 10907.8466 | -0.79907 | 0.5375 | 0.9941 | 0.89094 | 4.5806 | -36903.9616 | 5750 | 3 | 4 | 17156.2432 | 9029.4367 | 9070.4367 | 63189.2432 | -6.209
151 | E-SOR-NAP-FC-ET-WC-R600 | -475.0227 | 1223.1203 | 748.0976 | 8809.5643 | 0.084919 | 1.1237 | 1.0593 | 1.7615 | 4.6024 | 138.443 | 15925 | 3 | 4 | 6811.2978 | 7095.8209 | 7136.8209 | 134244.2978 | 169.9076
152 | E-SOR-NAP-FC-ET-WC-R600 | -1993.9567 | 1181.9426 | -812.0141 | 8799.9156 | -0.092275 | 0.94166 | 1.0597 | 1.4883 | 4.6033 | -6005.9225 | 13425 | 3 | 4 | 8194.4246 | 7087.1481 | 7128.1481 | 115627.4246 | -133.6175
153 | E-SOR-NAP-FC-ET-WC-R600 | -3644.5174 | 1142.2804 | -2502.2371 | 8793.135 | -0.28457 | 0.80071 | 1.0597 | 1.2734 | 4.6015 | -12674.2691 | 11250 | 3 | 4 | 9697.5983 | 7080.9795 | 7121.9795 | 99730.5983 | -37.0103
154 | E-SOR-NAP-FC-ET-WC-R600 | -5549.1964 | 1092.5215 | -4456.6749 | 8782.5003 | -0.50745 | 0.68246 | 1.06 | 1.1039 | 4.6008 | -20375.9165 | 8750 | 3 | 4 | 11432.0845 | 7071.3362 | 7112.3362 | 81465.0845 | -16.6835
155 | E-SOR-NAP-FC-ET-WC-R600 | -7668.4718 | 1035.5954 | -6632.8764 | 8771.3647 | -0.7562 | 0.58601 | 1.0604 | 0.96906 | 4.6017 | -28947.8949 | 6250 | 3 | 4 | 13363.6644 | 7061.3635 | 7102.3635 | 63396.6645 | -8.4872
156 | E-SOR-NAP-FC-ET-WC-R600 | -1279.0289 | 1216.9538 | -62.0752 | 8805.9119 | -0.0070493 | 1.0212 | 1.0595 | 1.6287 | 4.6027 | -3087.8594 | 15325 | 3 | 4 | 7535.3546 | 7092.5333 | 7133.5333 | 130168.3546 | -1982.0299
157 | E-SOR-NAP-FC-ET-WC-R600 | -2693.4477 | 1177.6786 | -1515.7691 | 8800.8527 | -0.17223 | 0.87731 | 1.0595 | 1.4137 | 4.6021 | -8810.9931 | 12925 | 3 | 4 | 8827.4053 | 7088.009 | 7129.009 | 112260.4053 | -69.3585
158 | E-SOR-NAP-FC-ET-WC-R600 | -4259.8015 | 1137.1369 | -3122.6646 | 8797.9608 | -0.35493 | 0.75908 | 1.0596 | 1.231 | 4.602 | -15143.9777 | 10800 | 3 | 4 | 10258.7794 | 7085.2991 | 7126.2991 | 96691.7795 | -28.6824
159 | E-SOR-NAP-FC-ET-WC-R600 | -6015.6899 | 1089.043 | -4926.6469 | 8788.6916 | -0.56057 | 0.65919 | 1.0599 | 1.0828 | 4.6018 | -22247.6879 | 8400 | 3 | 4 | 11859.6661 | 7076.9848 | 7117.9848 | 79092.6662 | -14.6093
160 | E-SOR-NAP-FC-ET-WC-R60 | -8258.1181 | 1028.2435 | -7229.8747 | 8779.1547 | -0.82353 | 0.56426 | 1.0602 | 0.93376 | 4.6017 | -31318.7334 | 6000 | 3 | 4 | 13905.7535 | 7068.3644 | 7109.3644 | 61938.7536 | -7.5837
161 | E-SOR-NAP-FC-ET-WC-R60 | -2721.1472 | 1205.0143 | -1516.1329 | 8805.4609 | -0.17218 | 0.87736 | 1.0595 | 1.4488 | 4.6034 | -8876.2316 | 14675 | 3 | 4 | 8840.0989 | 7092.1673 | 7133.1673 | 126273.099 | -78.5815
162 | E-SOR-NAP-FC-ET-WC-R60 | -3931.7431 | 1168.1158 | -2763.6274 | 8800.8948 | -0.31402 | 0.78269 | 1.0596 | 1.3021 | 4.6027 | -13780.1129 | 12375 | 3 | 4 | 9947.6751 | 7088.068 | 7129.068 | 108980.6752 | -36.8543
163 | E-SOR-NAP-FC-ET-WC-R60 | -5449.0008 | 1128.8289 | -4320.1719 | 8795.6493 | -0.49117 | 0.68984 | 1.0598 | 1.1499 | 4.6029 | -19914.6217 | 10350 | 3 | 4 | 11331.9442 | 7083.1923 | 7124.1923 | 94164.9442 | -20.1475
164 | E-SOR-NAP-FC-ET-WC-R60 | -7321.6933 | 1076.3474 | -6245.3459 | 8787.4105 | -0.71072 | 0.60138 | 1.06 | 1.0154 | 4.6021 | -27492.861 | 8050 | 3 | 4 | 13041.4768 | 7075.7866 | 7116.7866 | 77474.4768 | -11.2656
165 | E-SOR-NAP-FC-ET-WC-R60 | -10092.6784 | 1006.9731 | -9085.7054 | 8773.1241 | -1.0356 | 0.50554 | 1.0603 | 0.88319 | 4.6018 | -38692.4253 | 5750 | 3 | 4 | 15564.2456 | 7063.0268 | 7104.0268 | 61597.2456 | -5.9977
166 | E-SOR-NAP-FC-FP-WC-OFF0 | -4982.1097 | 1019.7079 | -3962.4018 | 4146.5657 | -0.95559 | 0.713 | 1.4592 | 1.8232 | 4.452 | -18228.9258 | 10825 | 3 | 4 | 6621.663 | 2703.0991 | 2744.0991 | 93254.663 | -22.8423
167 | E-SOR-NAP-FC-FP-WC-OFF0 | -7134.9325 | 977.1952 | -6157.7373 | 4146.4927 | -1.485 | 0.5611 | 1.4593 | 1.435 | 4.4521 | -26911.0714 | 9125 | 3 | 4 | 8584.9621 | 2703.0553 | 2744.0553 | 81617.9621 | -12.8089
168 | E-SOR-NAP-FC-FP-WC-OFF0 | -8532.4193 | 944.2975 | -7588.1218 | 4146.7112 | -1.8299 | 0.49269 | 1.4592 | 1.2634 | 4.4518 | -32555.8481 | 7650 | 3 | 4 | 9862.8356 | 2703.1864 | 2744.1864 | 71095.8356 | -9.0077
169 | E-SOR-NAP-FC-FP-WC-OFF0 | -10248.1967 | 906.9432 | -9341.2535 | 4147.1507 | -2.2525 | 0.42864 | 1.459 | 1.1032 | 4.4512 | -39481.2149 | 5950 | 3 | 4 | 11429.9231 | 2703.4501 | 2744.4501 | 59062.9231 | -6.029
170 | E-SOR-NAP-FC-FP-WC-OFF0 | -12321.5314 | 869.9431 | -11451.5882 | 4147.0622 | -2.7614 | 0.37065 | 1.459 | 0.96146 | 4.4512 | -47836.2202 | 4250 | 3 | 4 | 13318.2332 | 2703.397 | 2744.397 | 47351.2333 | -3.8953
171 | E-SOR-NAP-FC-FP-WC-OFF0 | -5312.0286 | 1021.1169 | -4290.9118 | 4146.3501 | -1.0349 | 0.68525 | 1.4593 | 1.7601 | 4.4522 | -19546.2531 | 10225 | 3 | 4 | 6917.6069 | 2702.9697 | 2743.9697 | 88750.6069 | -20.0439
172 | E-SOR-NAP-FC-FP-WC-OFF0 | -7120.7492 | 981.7872 | -6138.9621 | 4146.5888 | -1.4805 | 0.56211 | 1.4592 | 1.4457 | 4.452 | -26846.685 | 8625 | 3 | 4 | 8569.438 | 2703.1129 | 2744.1129 | 77602.438 | -12.194
173 | E-SOR-NAP-FC-FP-WC-OFF0 | -8930.7611 | 944.4804 | -7986.2806 | 4146.8854 | -1.9259 | 0.47656 | 1.4592 | 1.2278 | 4.452 | -34148.9101 | 7200 | 3 | 4 | 10221.2263 | 2703.2909 | 2744.2909 | 67854.2264 | -8.1527
174 | E-SOR-NAP-FC-FP-WC-OFF0 | -10684.7091 | 908.3791 | -9776.33 | 4146.7502 | -2.3576 | 0.41526 | 1.4592 | 1.0751 | 4.4518 | -41224.8714 | 5600 | 3 | 4 | 11821.5952 | 2703.2098 | 2744.2098 | 56654.5953 | -5.5144
175 | E-SOR-NAP-FC-FP-WC-OFF | -12585.3376 | 868.4163 | -11716.9213 | 4147.1719 | -2.8253 | 0.36445 | 1.459 | 0.95071 | 4.4511 | -48893.9899 | 4000 | 3 | 4 | 13556.5762 | 2703.4628 | 2744.4628 | 45589.5762 | -3.6567
176 | E-SOR-NAP-FC-FP-WC-OFF | -6211.8778 | 1017.1193 | -5194.7585 | 4145.9159 | -1.253 | 0.61898 | 1.4595 | 1.6093 | 4.4529 | -23152.3123 | 9575 | 3 | 4 | 7729.5292 | 2702.7092 | 2743.7092 | 84362.5293 | -15.7118
177 | E-SOR-NAP-FC-FP-WC-OFF | -7654.4833 | 985.0402 | -6669.4431 | 4146.2532 | -1.6085 | 0.53456 | 1.4593 | 1.3935 | 4.4524 | -28976.1994 | 8075 | 3 | 4 | 9047.5056 | 2702.9116 | 2743.9116 | 73680.5056 | -10.6361
178 | E-SOR-NAP-FC-FP-WC-OFF | -9398.8864 | 944.4559 | -8454.4305 | 4146.0508 | -2.0392 | 0.45887 | 1.4595 | 1.1984 | 4.4529 | -36021.4524 | 6750 | 3 | 4 | 10641.8917 | 2702.7901 | 2743.7901 | 64674.8917 | -7.3253
179 | E-SOR-NAP-FC-FP-WC-OFF | -11017.4334 | 904.1065 | -10113.3269 | 4146.8748 | -2.4388 | 0.40547 | 1.4592 | 1.0679 | 4.4519 | -42562.8893 | 5250 | 3 | 4 | 12123.5167 | 2703.2845 | 2744.2845 | 54156.5168 | -5.0836
180 | E-SOR-NAP-FC-FP-WC-OFF | -13421.7822 | 866.4712 | -12555.311 | 4146.6323 | -3.0278 | 0.34621 | 1.4594 | 0.93423 | 4.4524 | -52243.01 | 3750 | 3 | 4 | 14310.038 | 2703.1391 | 2744.1391 | 44343.038 | -3.3133
181 | E-SOR-NAP-FC-FP-WC-R100 | -631.8539 | 1073.365 | 441.5112 | 10916.2471 | 0.040445 | 1.0078 | 0.99408 | 1.5317 | 4.5826 | -738.4738 | 10825 | 3 | 4 | 8981.7556 | 9037.1109 | 9078.1109 | 95614.7556 | 196.001
182 | E-SOR-NAP-FC-FP-WC-R100 | -2214.3187 | 1035.3442 | -1178.9744 | 10911.6225 | -0.10805 | 0.87275 | 0.99413 | 1.327 | 4.5821 | -7131.701 | 9125 | 3 | 4 | 10424.5944 | 9032.8826 | 9073.8826 | 83457.5944 | -63.0919
183 | E-SOR-NAP-FC-FP-WC-R100 | -3838.3551 | 1000.1372 | -2838.2179 | 10909.5186 | -0.26016 | 0.76737 | 0.9941 | 1.1707 | 4.5811 | -13686.525 | 7650 | 3 | 4 | 11905.4742 | 9030.9831 | 9071.9831 | 73138.4742 | -22.5728
184 | E-SOR-NAP-FC-FP-WC-R100 | -5542.8973 | 958.023 | -4584.8743 | 10907.1047 | -0.42036 | 0.68075 | 0.994 | 1.0485 | 4.5791 | -20574.8843 | 5950 | 3 | 4 | 13462.5911 | 9028.7177 | 9069.7177 | 61095.5911 | -11.3473
185 | E-SOR-NAP-FC-FP-WC-R100 | -7408.0995 | 910.4786 | -6497.6209 | 10902.2476 | -0.59599 | 0.60593 | 0.99417 | 0.95045 | 4.5804 | -28114.9338 | 4250 | 3 | 4 | 15165.5186 | 9024.4 | 9065.4 | 49198.5187 | -6.1766
186 | E-SOR-NAP-FC-FP-WC-R100 | -1502.1941 | 1064.7242 | -437.4699 | 10917.8814 | -0.040069 | 0.92968 | 0.994 | 1.4398 | 4.5821 | -4234.2361 | 10225 | 3 | 4 | 9771.7582 | 9038.5971 | 9079.5971 | 91604.7582 | -188.6419
187 | E-SOR-NAP-FC-FP-WC-R100 | -3020.2505 | 1028.8334 | -1991.4171 | 10914.758 | -0.18245 | 0.81772 | 0.99399 | 1.2611 | 4.5809 | -10366.2798 | 8625 | 3 | 4 | 11156.6477 | 9035.6851 | 9076.6851 | 80189.6477 | -35.7097
188 | E-SOR-NAP-FC-FP-WC-R100 | -4449.2415 | 994.593 | -3454.6486 | 10913.1229 | -0.31656 | 0.73451 | 0.99411 | 1.1361 | 4.582 | -16139.3112 | 7200 | 3 | 4 | 12461.8274 | 9034.202 | 9075.202 | 70094.8275 | -17.663
189 | E-SOR-NAP-FC-FP-WC-R100 | -6063.6994 | 952.5906 | -5111.1088 | 10909.2565 | -0.46851 | 0.65849 | 0.9941 | 1.0292 | 4.581 | -22667.1468 | 5600 | 3 | 4 | 13936.5898 | 9030.7313 | 9071.7313 | 58769.5898 | -9.7235
190 | E-SOR-NAP-FC-FP-WC-R10 | -8114.8246 | 904.1372 | -7210.6874 | 10905.2854 | -0.66121 | 0.58212 | 0.99413 | 0.91003 | 4.5806 | -30952.4029 | 4000 | 3 | 4 | 15808.1285 | 9027.1661 | 9068.1661 | 47841.1285 | -5.3772
191 | E-SOR-NAP-FC-FP-WC-R10 | -3216.5583 | 1041.3662 | -2175.1921 | 10918.1156 | -0.19923 | 0.8063 | 0.99401 | 1.292 | 4.5823 | -11130.6228 | 9575 | 3 | 4 | 11328.9815 | 9038.8487 | 9079.8487 | 87961.9816 | -36.2644
192 | E-SOR-NAP-FC-FP-WC-R10 | -4478.3273 | 1010.2998 | -3468.0275 | 10915.6841 | -0.31771 | 0.73383 | 0.99404 | 1.1818 | 4.5821 | -16229.4761 | 8075 | 3 | 4 | 12480.9818 | 9036.619 | 9077.619 | 77113.9818 | -19.6182
193 | E-SOR-NAP-FC-FP-WC-R10 | -5995.2598 | 975.9444 | -5019.3154 | 10913.3352 | -0.45992 | 0.66241 | 0.99415 | 1.0533 | 4.5828 | -22354.4652 | 6750 | 3 | 4 | 13864.675 | 9034.4405 | 9075.4405 | 67897.675 | -11.7192
194 | E-SOR-NAP-FC-FP-WC-R10 | -7809.2219 | 933.3091 | -6875.9128 | 10909.321 | -0.63028 | 0.59318 | 0.99413 | 0.9545 | 4.5815 | -29681.3724 | 5250 | 3 | 4 | 15519.1747 | 9030.7746 | 9071.7746 | 57552.1748 | -7.0508
195 | E-SOR-NAP-FC-FP-WC-R10 | -10618.7794 | 892.3164 | -9726.463 | 10903.1049 | -0.89208 | 0.51105 | 0.99406 | 0.84568 | 4.579 | -40987.9237 | 3750 | 3 | 4 | 18066.7332 | 9025.1299 | 9066.1299 | 48099.7332 | -4.0131
196 | E-SOR-NAP-FC-FP-WC-R600 | -1749.7835 | 1197.1995 | -552.584 | 8801.3727 | -0.062784 | 0.9678 | 1.0597 | 1.5184 | 4.6036 | -5003.8016 | 10825 | 3 | 4 | 7966.8384 | 7088.4531 | 7129.4531 | 94599.8384 | -158.2934
197 | E-SOR-NAP-FC-FP-WC-R600 | -3200.1421 | 1164.7462 | -2035.3959 | 8793.9156 | -0.23146 | 0.83533 | 1.0598 | 1.3219 | 4.6027 | -10859.3247 | 9125 | 3 | 4 | 9284.8677 | 7081.6621 | 7122.6621 | 82317.8677 | -36.9438
198 | E-SOR-NAP-FC-FP-WC-R600 | -4633.7365 | 1131.7619 | -3501.9746 | 8787.4012 | -0.39852 | 0.73561 | 1.06 | 1.1762 | 4.602 | -16648.6762 | 7650 | 3 | 4 | 10589.0604 | 7075.7871 | 7116.7871 | 71822.0604 | -18.4768
199 | E-SOR-NAP-FC-FP-WC-R600 | -6307.001 | 1090.4818 | -5216.5192 | 8778.2395 | -0.59426 | 0.64546 | 1.0603 | 1.0459 | 4.6021 | -23410.5343 | 5950 | 3 | 4 | 12111.4752 | 7067.4544 | 7108.4544 | 59744.4752 | -10.0903
200 | E-SOR-NAP-FC-FP-WC-R600 | -8097.2232 | 1043.6456 | -7053.5776 | 8766.7081 | -0.80459 | 0.5704 | 1.0606 | 0.94435 | 4.6025 | -30649.4833 | 4250 | 3 | 4 | 13740.5362 | 7057.1753 | 7098.1753 | 47773.5363 | -5.7666
201 | E-SOR-NAP-FC-FP-WC-R600 | -2627.2914 | 1188.8302 | -1438.4612 | 8800.305 | -0.16346 | 0.88399 | 1.0596 | 1.4139 | 4.6025 | -8527.7821 | 10225 | 3 | 4 | 8760.6537 | 7087.4686 | 7128.4686 | 90593.6537 | -58.0239
202 | E-SOR-NAP-FC-FP-WC-R600 | -3877.564 | 1157.4759 | -2720.0881 | 8797.3322 | -0.30919 | 0.78567 | 1.0597 | 1.271 | 4.6026 | -13581.1296 | 8625 | 3 | 4 | 9901.9843 | 7084.7183 | 7125.7183 | 78934.9843 | -26.3996
203 | E-SOR-NAP-FC-FP-WC-R600 | -5273.4975 | 1124.8638 | -4148.6337 | 8791.5357 | -0.47189 | 0.69889 | 1.0599 | 1.1381 | 4.6022 | -19219.2168 | 7200 | 3 | 4 | 11172.7368 | 7079.5286 | 7120.5286 | 68805.7369 | -14.8688
204 | E-SOR-NAP-FC-FP-WC-R600 | -6879.9005 | 1085.1943 | -5794.7061 | 8782.2761 | -0.65982 | 0.61995 | 1.0602 | 1.0217 | 4.6031 | -25710.9447 | 5600 | 3 | 4 | 12634.0203 | 7071.2159 | 7112.2159 | 57467.0204 | -8.6898
205 | E-SOR-NAP-FC-FP-WC-R60 | -8775.2876 | 1036.3639 | -7738.9237 | 8771.9885 | -0.88223 | 0.54676 | 1.0604 | 0.9059 | 4.6016 | -33373.8772 | 4000 | 3 | 4 | 14359.8509 | 7061.869 | 7102.869 | 46392.8509 | -5.0769
206 | E-SOR-NAP-FC-FP-WC-R60 | -4193.9762 | 1168.7927 | -3025.1834 | 8798.5093 | -0.34383 | 0.76543 | 1.0597 | 1.2741 | 4.6034 | -14827.9168 | 9575 | 3 | 4 | 10181.1708 | 7085.9096 | 7126.9096 | 86814.1709 | -26.3413
207 | E-SOR-NAP-FC-FP-WC-R60 | -5284.929 | 1141.2305 | -4143.6986 | 8793.4361 | -0.47123 | 0.69918 | 1.0598 | 1.1731 | 4.6026 | -19237.6654 | 8075 | 3 | 4 | 11174.9651 | 7081.3106 | 7122.3106 | 75807.9652 | -16.5759
208 | E-SOR-NAP-FC-FP-WC-R60 | -6650.8282 | 1111.0342 | -5539.7941 | 8788.1599 | -0.63037 | 0.631 | 1.0599 | 1.0528 | 4.6022 | -24751.5893 | 6750 | 3 | 4 | 12417.5875 | 7076.4892 | 7117.4892 | 66450.5876 | -10.7103
209 | E-SOR-NAP-FC-FP-WC-R60 | -8355.8831 | 1069.2573 | -7286.6258 | 8777.7604 | -0.83012 | 0.56227 | 1.0603 | 0.95209 | 4.6024 | -31641.437 | 5250 | 3 | 4 | 13967.932 | 7067.1957 | 7108.1957 | 56000.932 | -6.7099
210 | E-SOR-NAP-FC-FP-WC-R60 | -11061.0849 | 1030.8948 | -10030.1901 | 8761.5581 | -1.1448 | 0.47994 | 1.0607 | 0.84355 | 4.6016 | -42526.1817 | 3750 | 3 | 4 | 16410.9993 | 7052.5439 | 7093.5439 | 46443.9993 | -3.9232
211 | E-SOR-STR-FC-ET-HC-OFF0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 8150 | 3 | 4 | 0 | 0 | 41 | 65233 | #DIV/0!
212 | E-SOR-STR-FC-ET-HC-OFF0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 6900 | 3 | 4 | 0 | 0 | 41 | 55233.0001 | #DIV/0!
213 | E-SOR-STR-FC-ET-HC-OFF0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 5650 | 3 | 4 | 0 | 0 | 41 | 45233.0001 | #DIV/0!
214 | E-SOR-STR-FC-ET-HC-OFF0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 4400 | 3 | 4 | 0 | 0 | 41 | 35233.0001 | #DIV/0!
215 | E-SOR-STR-FC-ET-HC-OFF0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 3150 | 3 | 4 | 0 | 0 | 41 | 25233 | #DIV/0!
216 | E-SOR-STR-FC-ET-HC-OFF0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 7800 | 3 | 4 | 0 | 0 | 41 | 62433.0001 | #DIV/0!
217 | E-SOR-STR-FC-ET-HC-OFF0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 6600 | 3 | 4 | 0 | 0 | 41 | 52833.0001 | #DIV/0!
218 | E-SOR-STR-FC-ET-HC-OFF0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 5400 | 3 | 4 | 0 | 0 | 41 | 43233.0001 | #DIV/0!
219 | E-SOR-STR-FC-ET-HC-OFF0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 4200 | 3 | 4 | 0 | 0 | 41 | 33633 | #DIV/0!
220 | E-SOR-STR-FC-ET-HC-OFF | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 3000 | 3 | 4 | 0 | 0 | 41 | 24033 | #DIV/0!
221 | E-SOR-STR-FC-ET-HC-OFF | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 7500 | 3 | 4 | 0 | 0 | 41 | 60033 | #DIV/0!
222 | E-SOR-STR-FC-ET-HC-OFF | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 6350 | 3 | 4 | 0 | 0 | 41 | 50833 | #DIV/0!
223 | E-SOR-STR-FC-ET-HC-OFF | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 4050 | 3 | 4 | 0 | 0 | 41 | 32433 | #DIV/0!
224 | E-SOR-STR-FC-ET-WC-OFF0 | -547.9629 | 620.8367 | 72.8738 | 8685.0831 | 0.0083907 | 0.94582 | 0.97274 | 1.6669 | 4.5935 | -1157.1239 | 15925 | 3 | 4 | 7371.6421 | 7238.5856 | 7279.5856 | 134804.6421 | 1749.9447
225 | E-SOR-STR-FC-ET-WC-OFF0 | -1664.8607 | 593.6489 | -1071.2118 | 8685.1862 | -0.12334 | 0.83498 | 0.97283 | 1.3865 | 4.5946 | -5670.0279 | 13425 | 3 | 4 | 8393.1904 | 7238.6475 | 7279.6475 | 115826.1904 | -101.3306
226 | E-SOR-STR-FC-ET-WC-OFF0 | -2665.7653 | 567.8367 | -2097.9286 | 8685.1492 | -0.24155 | 0.75509 | 0.97234 | 1.2057 | 4.5876 | -9716.6667 | 11250 | 3 | 4 | 9309.4116 | 7238.6253 | 7279.6253 | 99342.4116 | -43.8827
227 | E-SOR-STR-FC-ET-WC-OFF0 | -3934.6454 | 533.7475 | -3400.8979 | 8685.1818 | -0.39157 | 0.67374 | 0.97241 | 1.0366 | 4.5885 | -14849.0024 | 8750 | 3 | 4 | 10471.8342 | 7238.6448 | 7279.6448 | 80504.8342 | -21.5311
228 | E-SOR-STR-FC-ET-WC-OFF0 | -5203.5628 | 497.3151 | -4706.2477 | 8684.9549 | -0.54189 | 0.60774 | 0.9719 | 0.90696 | 4.5814 | -19985.3927 | 6250 | 3 | 4 | 11635.5196 | 7238.5087 | 7279.5087 | 61668.5197 | -11.5568
229 | E-SOR-STR-FC-ET-WC-OFF0 | -811.9545 | 617.0268 | -194.9277 | 8685.2562 | -0.022444 | 0.91732 | 0.97277 | 1.582 | 4.5936 | -2219.4401 | 15325 | 3 | 4 | 7611.6443 | 7238.6895 | 7279.6895 | 130244.6443 | -630.8234
230 | E-SOR-STR-FC-ET-WC-OFF0 | -1937.0287 | 588.9217 | -1348.107 | 8684.9851 | -0.15522 | 0.81191 | 0.9728 | 1.3379 | 4.5944 | -6766.5787 | 12925 | 3 | 4 | 8640.8729 | 7238.5268 | 7279.5268 | 112073.8729 | -77.7344
231 | E-SOR-STR-FC-ET-WC-OFF0 | -2931.6685 | 563.8031 | -2367.8653 | 8685.3356 | -0.27263 | 0.73669 | 0.97239 | 1.1755 | 4.588 | -10787.002 | 10800 | 3 | 4 | 9551.2768 | 7238.7371 | 7279.7371 | 95984.2769 | -37.4618
232 | E-SOR-STR-FC-ET-WC-OFF0 | -4169.0051 | 528.386 | -3640.6191 | 8685.1891 | -0.41918 | 0.66049 | 0.9722 | 1.0233 | 4.5855 | -15795.3771 | 8400 | 3 | 4 | 10685.984 | 7238.6492 | 7279.6492 | 77918.9841 | -19.4031
233 | E-SOR-STR-FC-ET-WC-OFF | -5273.4024 | 494.4392 | -4778.9632 | 8684.8863 | -0.55026 | 0.60444 | 0.97188 | 0.89506 | 4.5812 | -20269.5444 | 6000 | 3 | 4 | 11700.0675 | 7238.4675 | 7279.4675 | 59733.0676 | -10.9759
234 | E-SOR-STR-FC-ET-WC-OFF | -1552.7293 | 604.0683 | -948.661 | 8685.4655 | -0.10922 | 0.8459 | 0.97317 | 1.443 | 4.5991 | -5204.1368 | 14675 | 3 | 4 | 8286.2989 | 7238.8151 | 7279.8151 | 125719.299 | -124.8491
235 | E-SOR-STR-FC-ET-WC-OFF | -2639.2174 | 576.8668 | -2062.3506 | 8685.3831 | -0.23745 | 0.75801 | 0.97287 | 1.2615 | 4.5949 | -9595.4249 | 12375 | 3 | 4 | 9280.3579 | 7238.7656 | 7279.7656 | 108313.3579 | -48.9895
236 | E-SOR-STR-FC-ET-WC-OFF | -3129.3898 | 549.4896 | -2579.9002 | 8685.1098 | -0.29705 | 0.72298 | 0.9726 | 1.1285 | 4.5913 | -11601.7433 | 10350 | 3 | 4 | 9737.7199 | 7238.6016 | 7279.6016 | 92570.7199 | -33.0599
237 | E-SOR-STR-FC-ET-WC-OFF | -4270.6705 | 514.2063 | -3756.4642 | 8685.2475 | -0.43251 | 0.6543 | 0.97213 | 1.0031 | 4.5844 | -16225.6716 | 8050 | 3 | 4 | 10786.0567 | 7238.6843 | 7279.6843 | 75219.0567 | -18.086
238 | E-SOR-STR-FC-ET-WC-OFF | -7006.9973 | 469.2468 | -6537.7506 | 8685.2554 | -0.75274 | 0.53454 | 0.97174 | 0.85416 | 4.5788 | -27245.9114 | 5750 | 3 | 4 | 13275.6797 | 7238.689 | 7279.689 | 59308.6797 | -7.9582
239 | E-SOR-STR-FC-FP-HC-OFF0 | -2739.3795 | -242.0614 | -2981.4409 | 4554.1477 | -0.65466 | 0.55643 | 0.98825 | 0.98195 | 4.8654 | -11360.9537 | 5550 | 3 | 4 | 6375.0557 | 3764.3773 | 3805.3773 | 50808.0557 | -15.7651
240 | E-SOR-STR-FC-FP-HC-OFF0 | -3288.1154 | -261.4593 | -3549.5747 | 4554.2729 | -0.77939 | 0.51744 | 0.98828 | 0.89575 | 4.8655 | -13588.2272 | 4700 | 3 | 4 | 6880.6319 | 3764.4524 | 3805.4524 | 44513.632 | -11.4685
241 | E-SOR-STR-FC-FP-HC-OFF0 | -3948.0761 | -284.4984 | -4232.5745 | 4554.2213 | -0.92937 | 0.47716 | 0.98816 | 0.81806 | 4.8639 | -16266.4685 | 3850 | 3 | 4 | 7488.389 | 3764.4214 | 3805.4214 | 38321.3891 | -8.1548
242 | E-SOR-STR-FC-FP-HC-OFF0 | -4670.8364 | -308.6004 | -4979.4368 | 4554.4205 | -1.0933 | 0.43977 | 0.98811 | 0.74454 | 4.8627 | -19197.6795 | 3000 | 3 | 4 | 8153.4539 | 3764.5409 | 3805.5409 | 32186.454 | -5.6996
243 | E-SOR-STR-FC-FP-HC-OFF0 | -5377.4776 | -329.6519 | -5707.1295 | 4554.2908 | -1.2531 | 0.40855 | 0.98805 | 0.67705 | 4.8621 | -22059.3304 | 2150 | 3 | 4 | 8801.9841 | 3764.4631 | 3805.4631 | 26034.9842 | -3.895
244 | E-SOR-STR-FC-FP-HC-OFF0 | -3099.9504 | -249.8978 | -3349.8482 | 4554.0069 | -0.73558 | 0.53041 | 0.98812 | 0.94334 | 4.8638 | -12816.2979 | 5200 | 3 | 4 | 6704.1868 | 3764.2928 | 3805.2928 | 48337.1869 | -13.2937
245 | E-SOR-STR-FC-FP-HC-OFF0 | -3668.2027 | -272.5387 | -3940.7414 | 4554.291 | -0.86528 | 0.4935 | 0.98805 | 0.86723 | 4.8621 | -15127.042 | 4400 | 3 | 4 | 7229.3689 | 3764.4633 | 3805.4633 | 42462.369 | -9.8096
246 | E-SOR-STR-FC-FP-HC-OFF0 | -4164.1196 | -291.0781 | -4455.1977 | 4554.3922 | -0.97822 | 0.46538 | 0.98816 | 0.79198 | 4.8634 | -17141.6087 | 3600 | 3 | 4 | 7686.8785 | 3764.524 | 3805.524 | 36519.8785 | -7.343
247 | E-SOR-STR-FC-FP-HC-OFF0 | -4982.029 | -316.3945 | -5298.4235 | 4554.0959 | -1.1634 | 0.42559 | 0.98829 | 0.72014 | 4.8661 | -20455.4403 | 2800 | 3 | 4 | 8438.009 | 3764.3462 | 3805.3462 | 30871.009 | -5.1082
248 | E-SOR-STR-FC-FP-HC-OFF | -6298.3982 | -332.4964 | -6630.8946 | 4554.0733 | -1.456 | 0.37489 | 0.9883 | 0.64966 | 4.8663 | -25747.7536 | 2000 | 3 | 4 | 9632.3888 | 3764.3326 | 3805.3326 | 25665.3889 | -3.2967
249 | E-SOR-STR-FC-FP-HC-OFF | -3775.5439 | -266.9756 | -4042.5195 | 4554.232 | -0.88764 | 0.48775 | 0.98824 | 0.86793 | 4.8651 | -15547.135 | 4900 | 3 | 4 | 7322.6027 | 3764.4279 | 3805.4279 | 46555.6028 | -10.5751
250 | E-SOR-STR-FC-FP-HC-OFF | -4393.7825 | -290.1471 | -4683.9296 | 4554.0838 | -1.0285 | 0.45388 | 0.98824 | 0.80681 | 4.8654 | -18058.7086 | 4150 | 3 | 4 | 7892.8315 | 3764.3389 | 3805.3389 | 41125.8315 | -7.9678
251 | E-SOR-STR-FC-FP-HC-OFF | -5372.2499 | -304.6089 | -5676.8588 | 4554.2985 | -1.2465 | 0.40983 | 0.98822 | 0.73657 | 4.8645 | -21996.6811 | 2650 | 3 | 4 | 8782.258 | 3764.4677 | 3805.4677 | 30015.258 | -4.617
252 | E-SOR-STR-FC-FP-WC-OFF0 | -1608.0824 | 647.523 | -960.5594 | 8687.4228 | -0.11057 | 0.85382 | 0.98347 | 1.4657 | 4.7449 | -5353.1246 | 10825 | 3 | 4 | 8317.6729 | 7239.9894 | 7280.9894 | 94950.6729 | -91.2694
253 | E-SOR-STR-FC-FP-WC-OFF0 | -2502.1145 | 626.0055 | -1876.109 | 8687.3821 | -0.21596 | 0.77983 | 0.98348 | 1.2927 | 4.7453 | -8965.1155 | 9125 | 3 | 4 | 9135.2666 | 7239.965 | 7280.965 | 82168.2666 | -39.9163
254 | E-SOR-STR-FC-FP-WC-OFF0 | -3198.7184 | 604.5181 | -2594.2002 | 8687.3112 | -0.29862 | 0.7302 | 0.98349 | 1.1792 | 4.7455 | -11787.3432 | 7650 | 3 | 4 | 9775.1274 | 7239.9225 | 7280.9225 | 71008.1274 | -24.5653
255 | E-SOR-STR-FC-FP-WC-OFF0 | -4167.9326 | 577.6284 | -3590.3042 | 8687.3314 | -0.41328 | 0.67096 | 0.9835 | 1.0638 | 4.7455 | -15709.0165 | 5950 | 3 | 4 | 10663.6215 | 7239.9346 | 7280.9346 | 58296.6215 | -14.2093
256 | E-SOR-STR-FC-FP-WC-OFF0 | -5119.863 | 548.2518 | -4571.6112 | 8687.4413 | -0.52623 | 0.6213 | 0.98349 | 0.96835 | 4.7452 | -19565.699 | 4250 | 3 | 4 | 11538.0967 | 7240.0005 | 7281.0005 | 45571.0968 | -8.3756
257 | E-SOR-STR-FC-FP-WC-OFF0 | -1974.2536 | 641.7222 | -1332.5314 | 8687.3079 | -0.15339 | 0.82215 | 0.98349 | 1.4006 | 4.7455 | -6827.4775 | 10225 | 3 | 4 | 8650.6069 | 7239.9205 | 7280.9205 | 90483.6069 | -62.4396
258 | E-SOR-STR-FC-FP-WC-OFF0 | -2795.2499 | 620.342 | -2174.908 | 8687.3762 | -0.25035 | 0.75837 | 0.98347 | 1.2588 | 4.745 | -10147.0964 | 8625 | 3 | 4 | 9402.4444 | 7239.9615 | 7280.9615 | 78435.4444 | -32.7161
259 | E-SOR-STR-FC-FP-WC-OFF0 | -3538.6585 | 599.6351 | -2939.0233 | 8687.5104 | -0.3383 | 0.70851 | 0.98344 | 1.1573 | 4.7445 | -13155.2419 | 7200 | 3 | 4 | 10084.0783 | 7240.042 | 7281.042 | 67717.0784 | -20.5633
260 | E-SOR-STR-FC-FP-WC-OFF0 | -4487.9559 | 571.1278 | -3916.8282 | 8687.5057 | -0.45086 | 0.65359 | 0.9835 | 1.0438 | 4.7454 | -16999.9442 | 5600 | 3 | 4 | 10955.6207 | 7240.0392 | 7281.0392 | 55788.6208 | -12.3844
261 | E-SOR-STR-FC-FP-WC-OFF | -5249.7884 | 542.7152 | -4707.0732 | 8687.4467 | -0.54182 | 0.61502 | 0.98349 | 0.95001 | 4.7452 | -20094.6284 | 4000 | 3 | 4 | 11658.327 | 7240.0038 | 7281.0038 | 43691.327 | -7.7352
262 | E-SOR-STR-FC-FP-WC-OFF | -2783.048 | 623.5922 | -2159.4558 | 8687.2179 | -0.24858 | 0.75948 | 0.98351 | 1.2936 | 4.7458 | -10092.8715 | 9575 | 3 | 4 | 9389.2919 | 7239.8665 | 7280.8665 | 86022.2919 | -36.4636
263 | E-SOR-STR-FC-FP-WC-OFF | -3926.0455 | 602.6511 | -3323.3944 | 8687.3023 | -0.38256 | 0.68587 | 0.98349 | 1.192 | 4.7455 | -14699.7636 | 8075 | 3 | 4 | 10430.6623 | 7239.9171 | 7280.9171 | 75063.6623 | -20.3956
264 | E-SOR-STR-FC-FP-WC-OFF | -3859.5547 | 583.1375 | -3276.4172 | 8687.4816 | -0.37714 | 0.68856 | 0.98348 | 1.1015 | 4.745 | -14466.323 | 6750 | 3 | 4 | 10382.7047 | 7240.0247 | 7281.0247 | 64415.7047 | -17.4382
265 | E-SOR-STR-FC-FP-WC-OFF | -4895.8485 | 556.41 | -4339.4385 | 8687.6775 | -0.49949 | 0.63236 | 0.98346 | 1.0002 | 4.7446 | -18656.0439 | 5250 | 3 | 4 | 11331.5941 | 7240.1423 | 7281.1423 | 53364.5941 | -10.6197
266 | E-SOR-STR-FC-FP-WC-OFF | -6646.5702 | 533.7099 | -6112.8603 | 8687.3754 | -0.70365 | 0.55661 | 0.9835 | 0.91717 | 4.7455 | -25696.7643 | 3750 | 3 | 4 | 12920.7398 | 7239.961 | 7280.961 | 42953.7398 | -5.8357
267 | E-SOR-TOU-CC-ET-HC-R100 | 7372.8136 | -31.462 | 7341.3516 | 25737.6228 | 0.28524 | 1.1726 | 0.84976 | 2.5881 | 5.1619 | 29438.8176 | 19350 | 3 | 4 | 16152.9068 | 22769.5618 | 22810.5618 | 170985.9068 | 20.1837
268 | E-SOR-TOU-CC-ET-HC-R100 | 6046.668 | -55.1406 | 5991.5273 | 25727.0254 | 0.23289 | 1.0926 | 0.84976 | 2.245 | 5.1606 | 24094.7709 | 16575 | 3 | 4 | 17351.1067 | 22760.0236 | 22801.0236 | 149984.1067 | 21.2272
269 | E-SOR-TOU-CC-ET-HC-R100 | 4397.7864 | -85.3374 | 4312.449 | 25701.769 | 0.16779 | 1.0072 | 0.84981 | 1.86 | 5.1616 | 17448.9167 | 13425 | 3 | 4 | 18830.4925 | 22737.2979 | 22778.2979 | 126263.4925 | 23.9969
270 | E-SOR-TOU-CC-ET-HC-R100 | 2601.0014 | -121.8624 | 2479.139 | 25669.2588 | 0.09658 | 0.92786 | 0.84988 | 1.5292 | 5.1627 | 10200.9017 | 10650 | 3 | 4 | 20440.2546 | 22708.0385 | 22749.0385 | 105673.2546 | 33.4488
271 | E-SOR-TOU-CC-ET-HC-R100 | 530.5844 | -162.9505 | 367.6339 | 25638.6497 | 0.014339 | 0.85042 | 0.84987 | 1.2585 | 5.1583 | 1850.7535 | 7825 | 3 | 4 | 22300.7348 | 22680.4904 | 22721.4904 | 84933.7349 | 169.2233
272 | E-SOR-TOU-CC-ET-HC-R100 | 6672.0651 | -25.0787 | 6646.9864 | 25742.4602 | 0.25821 | 1.1299 | 0.84975 | 2.4092 | 5.1617 | 26646.4626 | 18600 | 3 | 4 | 16784.0938 | 22773.9052 | 22814.9052 | 165617.0938 | 21.4837
273 | E-SOR-TOU-CC-ET-HC-R100 | 5537.1546 | -49.7357 | 5487.4189 | 25728.1733 | 0.21328 | 1.0654 | 0.84975 | 2.1171 | 5.1598 | 22065.7256 | 15925 | 3 | 4 | 17807.4524 | 22761.0501 | 22802.0501 | 145240.4524 | 22.3126
274 | E-SOR-TOU-CC-ET-HC-R100 | 3967.7003 | -83.7007 | 3883.9996 | 25702.2824 | 0.15111 | 0.98739 | 0.8498 | 1.7843 | 5.1606 | 15731.3002 | 12925 | 3 | 4 | 19217.0453 | 22737.7552 | 22778.7552 | 122650.0453 | 25.7135
275 | E-SOR-TOU-CC-ET-HC-R100 | 2162.1482 | -119.6895 | 2042.4587 | 25676.9599 | 0.079544 | 0.91067 | 0.84986 | 1.4691 | 5.1621 | 8449.1101 | 10200 | 3 | 4 | 20840.8469 | 22714.9665 | 22755.9665 | 102473.847 | 39.0304
276 | E-SOR-TOU-CC-ET-HC-R10 | 31.4936 | -161.6453 | -130.1516 | 25639.4402 | -0.0050762 | 0.83399 | 0.84987 | 1.2125 | 5.1589 | -143.4342 | 7525 | 3 | 4 | 22749.8497 | 22681.2068 | 22722.2068 | 82982.8498 | -463.0034
277 | E-SOR-TOU-CC-ET-HC-R10 | 5314.8393 | -29.9381 | 5284.9012 | 25726.7877 | 0.20542 | 1.0549 | 0.84977 | 2.0894 | 5.1612 | 21209.4604 | 17850 | 3 | 4 | 17994.4146 | 22759.8071 | 22800.8071 | 160827.4147 | 26.1172
278 | E-SOR-TOU-CC-ET-HC-R10 | 3902.4262 | -54.3662 | 3848.06 | 25705.9624 | 0.1497 | 0.98573 | 0.84979 | 1.8299 | 5.1603 | 15519.0946 | 15225 | 3 | 4 | 19261.5095 | 22741.0734 | 22782.0734 | 141094.5096 | 30.746
279 | E-SOR-TOU-CC-ET-HC-R10 | 2308.0122 | -89.1359 | 2218.8763 | 25684.8149 | 0.086389 | 0.91746 | 0.84983 | 1.5884 | 5.1607 | 9083.489 | 12375 | 3 | 4 | 20698.3104 | 22722.0399 | 22763.0399 | 119731.3105 | 43.7015
280 | E-SOR-TOU-CC-ET-HC-R10 | 643.7257 | -125.8984 | 517.8273 | 25662.4858 | 0.020178 | 0.85547 | 0.84985 | 1.338 | 5.1596 | 2365.0722 | 9800 | 3 | 4 | 22198.1281 | 22701.9422 | 22742.9422 | 100631.1282 | 150.4134
281 | E-SOR-TOU-CC-ET-HC-R10 | -2272.5122 | -172.4903 | -2445.0025 | 25618.0905 | -0.09544 | 0.76525 | 0.84994 | 1.0813 | 5.1614 | -9377.5327 | 7175 | 3 | 4 | 24810.7514 | 22661.9962 | 22702.9962 | 82243.7514 | -24.352
282 | E-SOR-TOU-CC-ET-HC-R600 | 6106.196 | 102.2441 | 6208.4401 | 19353.8773 | 0.32079 | 1.2738 | 0.87953 | 2.4962 | 5.2328 | 24595.191 | 19350 | 3 | 4 | 11396.9618 | 16953.8847 | 16994.8847 | 166229.9618 | 24.0375
283 | E-SOR-TOU-CC-ET-HC-R600 | 4923.6399 | 77.9698 | 5001.6097 | 19334.2993 | 0.25869 | 1.1671 | 0.87958 | 2.1422 | 5.2322 | 19824.5092 | 16575 | 3 | 4 | 12458.2137 | 16936.2715 | 16977.2715 | 145091.2137 | 25.6145
284 | E-SOR-TOU-CC-ET-HC-R600 | 3249.3587 | 43.2999 | 3292.6586 | 19312.6233 | 0.17049 | 1.0431 | 0.87962 | 1.7513 | 5.2306 | 13069.6012 | 13425 | 3 | 4 | 13966.3616 | 16916.7644 | 16957.7644 | 121399.3616 | 31.7195
285 | E-SOR-TOU-CC-ET-HC-R600 | 1619.5571 | 7.2213 | 1626.7783 | 19283.6235 | 0.084361 | 0.94506 | 0.87975 | 1.456 | 5.2314 | 6490.2637 | 10650 | 3 | 4 | 15428.7345 | 16890.6687 | 16931.6687 | 100661.7345 | 51.4699
286 | E-SOR-TOU-CC-ET-HC-R600 | -299.8421 | -35.3925 | -335.2346 | 19218.8292 | -0.017443 | 0.85066 | 0.87997 | 1.201 | 5.2307 | -1258.356 | 7825 | 3 | 4 | 17123.4467 | 16832.3533 | 16873.3533 | 79756.4469 | -187.5794
287 | E-SOR-TOU-CC-ET-HC-R600 | 5337.177 | 104.4067 | 5441.5837 | 19354.458 | 0.28115 | 1.2035 | 0.8795 | 2.2857 | 5.232 | 21522.7193 | 18600 | 3 | 4 | 12088.3086 | 16954.4119 | 16995.4119 | 160921.3086 | 26.4493
288 | E-SOR-TOU-CC-ET-HC-R600 | 4246.2497 | 79.1979 | 4325.4475 | 19335.8461 | 0.2237 | 1.1145 | 0.87957 | 2.0111 | 5.2317 | 17116.995 | 15925 | 3 | 4 | 13068.5181 | 16937.6615 | 16978.6615 | 140501.5181 | 28.5572
289 | E-SOR-TOU-CC-ET-HC-R600 | 2757.3964 | 46.7677 | 2804.1641 | 19312.8349 | 0.1452 | 1.0122 | 0.87959 | 1.6735 | 5.2292 | 11107.5318 | 12925 | 3 | 4 | 14407.2434 | 16916.9607 | 16957.9607 | 117840.2434 | 35.9759
290 | E-SOR-TOU-CC-ET-HC-R600 | 1190.9933 | 9.6107 | 1200.604 | 19280.7799 | 0.062269 | 0.92279 | 0.87975 | 1.4002 | 5.2309 | 4779.991 | 10200 | 3 | 4 | 15810.4463 | 16888.1067 | 16929.1067 | 97443.4464 | 67.0615
291 | E-SOR-TOU-CC-ET-HC-R60 | -733.6555 | -32.8893 | -766.5447 | 19212.1966 | -0.039899 | 0.8323 | 0.87998 | 1.1691 | 5.2303 | -2989.4373 | 7525 | 3 | 4 | 17506.4194 | 16826.3959 | 16867.3959 | 77739.4195 | -79.4109
292 | E-SOR-TOU-CC-ET-HC-R60 | 4012.3556 | 103.3409 | 4115.6965 | 19343.3881 | 0.21277 | 1.099 | 0.87951 | 1.9318 | 5.2304 | 16221.6572 | 17850 | 3 | 4 | 13271.3197 | 16944.4442 | 16985.4442 | 156104.3198 | 33.802
293 | E-SOR-TOU-CC-ET-HC-R60 | 2839.0688 | 78.7798 | 2917.8486 | 19316.0395 | 0.15106 | 1.0192 | 0.87966 | 1.7198 | 5.2326 | 11487.575 | 15225 | 3 | 4 | 14317.4026 | 16919.8325 | 16960.8325 | 136150.4027 | 40.8484
294 | E-SOR-TOU-CC-ET-HC-R60 | 1433.2407 | 43.0632 | 1476.3039 | 19283.1341 | 0.076559 | 0.93707 | 0.87975 | 1.4955 | 5.2312 | 5804.735 | 12375 | 3 | 4 | 15574.4736 | 16890.2282 | 16931.2282 | 114607.4737 | 66.1627
295 | E-SOR-TOU-CC-ET-HC-R60 | 15.1586 | 5.8652 | 21.0238 | 19240.1847 | 0.0010927 | 0.86642 | 0.87993 | 1.2877 | 5.2322 | 70.4098 | 9800 | 3 | 4 | 16834.4104 | 16851.5723 | 16892.5723 | 95267.4104 | 3727.9043
296 | E-SOR-TOU-CC-ET-HC-R60 | -2879.4811 | -39.131 | -2918.6121 | 19163.9186 | -0.1523 | 0.75122 | 0.88015 | 1.0599 | 5.2296 | -11583.1428 | 7175 | 3 | 4 | 19397.9565 | 16782.9448 | 16823.9448 | 76830.9565 | -20.5601
297 | E-SOR-TOU-CC-ET-WC-R100 | 11218.1614 | 563.1129 | 11781.2744 | 35497.0813 | 0.33189 | 1.2596 | 0.84998 | 3.9795 | 5.1078 | 45811.1673 | 27175 | 3 | 4 | 21008.6467 | 31432.1837 | 31473.1837 | 238441.6467 | 17.5676
298 | E-SOR-TOU-CC-ET-WC-R100 | 9375.7871 | 548.9627 | 9924.7498 | 35478.6408 | 0.27974 | 1.1684 | 0.84995 | 3.3056 | 5.1039 | 38418.0863 | 23150 | 3 | 4 | 22658.7016 | 31415.6025 | 31456.6025 | 207891.7016 | 17.7773
299 | E-SOR-TOU-CC-ET-WC-R100 | 7347.4462 | 530.2329 | 7877.6791 | 35445.1604 | 0.22225 | 1.082 | 0.84999 | 2.6454 | 5.1041 | 30273.5065 | 19075 | 3 | 4 | 24465.3456 | 31385.4828 | 31426.4828 | 177098.3456 | 18.4917
300 | E-SOR-TOU-CC-ET-WC-R100 | 5000.2794 | 502.5241 | 5502.8035 | 35389.3916 | 0.15549 | 0.99657 | 0.85005 | 2.1313 | 5.1042 | 20838.6577 | 15000 | 3 | 4 | 26544.2776 | 31335.294 | 31376.294 | 146577.2776 | 20.935
301 | E-SOR-TOU-CC-ET-WC-R100 | 2184.4966 | 464.4022 | 2648.8988 | 35338.7552 | 0.074957 | 0.90985 | 0.8501 | 1.6662 | 5.1038 | 9511.9901 | 10925 | 3 | 4 | 29055.8339 | 31289.7382 | 31330.7382 | 116488.8339 | 32.1485
302 | E-SOR-TOU-CC-ET-WC-R100 | 10159.5549 | 569.7302 | 10729.2851 | 35502.7247 | 0.30221 | 1.206 | 0.84998 | 3.6405 | 5.1081 | 41587.77 | 26125 | 3 | 4 | 21962.5109 | 31437.2604 | 31478.2604 | 230995.5109 | 18.5956
303 | E-SOR-TOU-CC-ET-WC-R100 | 8557.636 | 556.9223 | 9114.5582 | 35479.7526 | 0.25689 | 1.1325 | 0.84997 | 3.0421 | 5.1055 | 35158.7476 | 22200 | 3 | 4 | 23391.2761 | 31416.6063 | 31457.6063 | 201024.2761 | 18.6039
304 | E-SOR-TOU-CC-ET-WC-R100 | 6737.5574 | 534.6708 | 7272.2282 | 35441.5275 | 0.20519 | 1.0588 | 0.84999 | 2.52 | 5.1042 | 27841.3476 | 18325 | 3 | 4 | 25008.3294 | 31382.2148 | 31423.2148 | 171641.3294 | 19.2813
305 | E-SOR-TOU-CC-ET-WC-R100 | 4477.1613 | 504.4927 | 4981.654 | 35397.7705 | 0.14073 | 0.97945 | 0.85005 | 2.0168 | 5.1043 | 18749.4663 | 14400 | 3 | 4 | 27021.4401 | 31342.8291 | 31383.8291 | 142254.4401 | 22.2558
306 | E-SOR-TOU-CC-ET-WC-R10 | 1661.4194 | 466.8454 | 2128.2647 | 35342.0842 | 0.060219 | 0.89561 | 0.85013 | 1.6081 | 5.1058 | 7423.7531 | 10525 | 3 | 4 | 29528.1421 | 31292.7331 | 31333.7331 | 113761.1422 | 38.7299
307 | E-SOR-TOU-CC-ET-WC-R10 | 8265.6076 | 570.1768 | 8835.7844 | 35478.1326 | 0.24905 | 1.1207 | 0.84998 | 2.9754 | 5.1063 | 34012.725 | 25025 | 3 | 4 | 23644.6709 | 31415.125 | 31456.125 | 223877.6709 | 21.7775
308 | E-SOR-TOU-CC-ET-WC-R10 | 6769.7622 | 556.4503 | 7326.2125 | 35450.7117 | 0.20666 | 1.0608 | 0.84999 | 2.5898 | 5.1046 | 28006.466 | 21300 | 3 | 4 | 24974.5181 | 31390.4635 | 31431.4635 | 195407.5182 | 22.3821
309 | E-SOR-TOU-CC-ET-WC-R10 | 4774.9118 | 534.5263 | 5309.4382 | 35411.737 | 0.14993 | 0.99005 | 0.85004 | 2.1922 | 5.105 | 19990.5246 | 17525 | 3 | 4 | 26747.9897 | 31355.4051 | 31396.4051 | 166980.9898 | 25.5365
310 | E-SOR-TOU-CC-ET-WC-R10 | 2323.6158 | 501.845 | 2825.4608 | 35369.8482 | 0.079883 | 0.91473 | 0.85011 | 1.809 | 5.1063 | 10130.8717 | 13800 | 3 | 4 | 28936.0927 | 31317.7018 | 31358.7018 | 139369.0928 | 38.2275
311 | E-SOR-TOU-CC-ET-WC-R10 | -272.5958 | 463.9623 | 191.3664 | 35312.8987 | 0.0054192 | 0.84626 | 0.85013 | 1.4352 | 5.1037 | -317.1129 | 10075 | 3 | 4 | 31244.1924 | 31266.4582 | 31307.4582 | 111877.1925 | 421.0233
312 | E-SOR-TOU-CC-ET-WC-R600 | 9248.3985 | 869.6423 | 10118.0408 | 26393.9453 | 0.38335 | 1.411 | 0.88062 | 3.7365 | 5.1759 | 38442.9979 | 27175 | 3 | 4 | 14303.881 | 23135.2278 | 23176.2278 | 231736.881 | 20.6128
313 | E-SOR-TOU-CC-ET-WC-R600 | 7632.8461 | 854.2834 | 8487.1295 | 26359.9286 | 0.32197 | 1.2834 | 0.88072 | 3.0931 | 5.1762 | 31955.19 | 23150 | 3 | 4 | 15736.5295 | 23104.6312 | 23145.6312 | 200969.5295 | 20.9522
314 | E-SOR-TOU-CC-ET-WC-R600 | 5667.2609 | 830.2519 | 6497.5128 | 26327.6633 | 0.24679 | 1.1553 | 0.88075 | 2.4659 | 5.1741 | 24052.7968 | 19075 | 3 | 4 | 17491.0055 | 23075.6178 | 23116.6178 | 170124.0055 | 22.6252
315 | E-SOR-TOU-CC-ET-WC-R600 | 3369.8459 | 797.7022 | 4167.5481 | 26288.1091 | 0.15853 | 1.0343 | 0.8809 | 1.946 | 5.1759 | 14808.8872 | 15000 | 3 | 4 | 19542.6655 | 23040.0204 | 23081.0204 | 139575.6655 | 27.9528
316 | E-SOR-TOU-CC-ET-WC-R600 | 805.8749 | 759.2113 | 1565.0863 | 26222.7223 | 0.059684 | 0.92569 | 0.88106 | 1.5485 | 5.1749 | 4488.852 | 10925 | 3 | 4 | 21814.5457 | 22981.1793 | 23022.1793 | 109247.5457 | 55.093
317 | E-SOR-TOU-CC-ET-WC-R600 | 8275.3233 | 873.8679 | 9149.1913 | 26392.1033 | 0.34666 | 1.3318 | 0.88066 | 3.3703 | 5.1773 | 34557.74 | 26125 | 3 | 4 | 15175.4856 | 23133.5699 | 23174.5699 | 224208.4856 | 21.9729
318 | E-SOR-TOU-CC-ET-WC-R600 | 6665.1853 | 856.6229 | 7521.8082 | 26363.4509 | 0.28531 | 1.2175 | 0.88072 | 2.81 | 5.1766 | 28088.446 | 22200 | 3 | 4 | 16609.205 | 23107.7949 | 23148.7949 | 194242.205 | 22.7463
319 | E-SOR-TOU-CC-ET-WC-R600 | 4899.4557 | 834.0026 | 5733.4584 | 26331.2719 | 0.21774 | 1.1124 | 0.88074 | 2.306 | 5.174 | 20987.8273 | 18325 | 3 | 4 | 18183.0237 | 23078.8591 | 23119.8591 | 164816.0237 | 24.7139
320 | E-SOR-TOU-CC-ET-WC-R600 | 2800.603 | 803.4199 | 3604.0228 | 26288.7623 | 0.13709 | 1.0086 | 0.88092 | 1.8612 | 5.1767 | 12541.445 | 14400 | 3 | 4 | 20052.1322 | 23040.5967 | 23081.5967 | 135285.1322 | 31.1329
321 | E-SOR-TOU-CC-ET-WC-R60 | 441.3723 | 763.8541 | 1205.2264 | 26214.6387 | 0.045975 | 0.9124 | 0.88108 | 1.5026 | 5.1749 | 3038.5794 | 10525 | 3 | 4 | 22132.5321 | 22973.9077 | 23014.9077 | 106365.5322 | 69.1576
322 | E-SOR-TOU-CC-ET-WC-R60 | 6376.06 | 872.9516 | 7249.0116 | 26375.3873 | 0.27484 | 1.1999 | 0.88067 | 2.6628 | 5.1758 | 26959.1593 | 25025 | 3 | 4 | 16870.3389 | 23118.5253 | 23159.5253 | 217103.3389 | 26.7545
323 | E-SOR-TOU-CC-ET-WC-R60 | 5089.9174 | 856.1789 | 5946.0963 | 26345.5814 | 0.2257 | 1.1239 | 0.88077 | 2.3543 | 5.1769 | 21786.6345 | 21300 | 3 | 4 | 18011.1387 | 23091.7109 | 23132.7109 | 188444.1388 | 27.8017
324 | E-SOR-TOU-CC-ET-WC-R60 | 3346.9619 | 833.8197 | 4180.7816 | 26298.2825 | 0.15898 | 1.0348 | 0.8809 | 2.0191 | 5.1768 | 14777.5473 | 17525 | 3 | 4 | 19550.6919 | 23049.1647 | 23090.1647 | 159783.692 | 32.6957
325 | E-SOR-TOU-CC-ET-WC-R60 | 1257.3183 | 803.353 | 2060.6713 | 26236.4579 | 0.078542 | 0.94458 | 0.881 | 1.6866 | 5.1743 | 6368.1948 | 13800 | 3 | 4 | 21394.0524 | 22993.54 | 23034.54 | 131827.0524 | 52.7947
326 | E-SOR-TOU-CC-ET-WC-R60 | -1106.4329 | 763.2133 | -343.2197 | 26141.9103 | -0.013129 | 0.85934 | 0.88128 | 1.3783 | 5.175 | -3153.7096 | 10075 | 3 | 4 | 23460.4743 | 22908.4558 | 22949.4558 | 104093.4744 | -236.4201
327 | E-SOR-TOU-CC-FP-HC-R100 | 6214.4789 | -63.815 | 6150.6639 | 25718.2596 | 0.23916 | 1.1016 | 0.84978 | 2.0444 | 5.1607 | 24751.5573 | 13150 | 3 | 4 | 17197.39 | 22752.1321 | 22793.1321 | 122430.39 | 16.1994
328 | E-SOR-TOU-CC-FP-HC-R100 | 4984.8953 | -80.0156 | 4904.8796 | 25700.9101 | 0.19084 | 1.0359 | 0.84982 | 1.8019 | 5.1619 | 19806.2217 | 11275 | 3 | 4 | 18298.1264 | 22736.5228 | 22777.5228 | 108531.1264 | 17.4833
329 | E-SOR-TOU-CC-FP-HC-R100 | 3349.8976 | -105.5999 | 3244.2977 | 25673.8602 | 0.12637 | 0.9595 | 0.84988 | 1.5471 | 5.1634 | 13223.5907 | 9125 | 3 | 4 | 19760.6239 | 22712.1718 | 22753.1718 | 92793.6239 | 21.5888
330 | E-SOR-TOU-CC-FP-HC-R100 | 1792.4647 | -132.5881 | 1659.8766 | 25646.3692 | 0.064722 | 0.89624 | 0.84988 | 1.3403 | 5.1602 | 6948.8786 | 7250 | 3 | 4 | 21153.7796 | 22687.445 | 22728.445 | 79186.7796 | 34.0136
331 | E-SOR-TOU-CC-FP-HC-R100 | -94.7386 | -165.7967 | -260.5353 | 25610.988 | -0.010173 | 0.82982 | 0.84992 | 1.1522 | 5.1589 | -655.2823 | 5325 | 3 | 4 | 22840.3337 | 22655.5909 | 22696.5909 | 65473.3338 | -164.1879
332 | E-SOR-TOU-CC-FP-HC-R100 | 5381.2285 | -62.97 | 5318.2585 | 25717.6076 | 0.20679 | 1.0567 | 0.84978 | 1.9192 | 5.1611 | 21419.964 | 12400 | 3 | 4 | 17946.2213 | 22751.545 | 22792.545 | 117179.2213 | 17.7477
333 | E-SOR-TOU-CC-FP-HC-R100 | 4311.3006 | -81.8542 | 4229.4465 | 25699.909 | 0.16457 | 1.0033 | 0.84983 | 1.7208 | 5.1627 | 17108.7789 | 10625 | 3 | 4 | 18904.5699 | 22735.6279 | 22776.6279 | 103937.5699 | 19.1895
334 | E-SOR-TOU-CC-FP-HC-R100 | 2874.3866 | -107.5729 | 2766.8137 | 25675.4828 | 0.10776 | 0.93946 | 0.84986 | 1.5014 | 5.1616 | 11318.2582 | 8625 | 3 | 4 | 20191.2402 | 22713.6444 | 22754.6444 | 89224.2402 | 24.0239
335 | E-SOR-TOU-CC-FP-HC-R100 | 1216.1558 | -134.7784 | 1081.3774 | 25650.6087 | 0.042158 | 0.87512 | 0.84987 | 1.2975 | 5.1596 | 4639.9926 | 6800 | 3 | 4 | 21677.5788 | 22691.252 | 22732.252 | 76110.5789 | 49.3614
336 | E-SOR-TOU-CC-FP-HC-R10 | -768.4276 | -167.3372 | -935.7648 | 25610.8623 | -0.036538 | 0.80877 | 0.84998 | 1.1098 | 5.1633 | -3352.6058 | 5025 | 3 | 4 | 23447.4771 | 22655.4899 | 22696.4899 | 63680.4772 | -43.7973
337 | E-SOR-TOU-CC-FP-HC-R10 | 3750.0862 | -75.5639 | 3674.5224 | 25698.5764 | 0.14299 | 0.97807 | 0.84984 | 1.678 | 5.1634 | 14874.4051 | 11650 | 3 | 4 | 19404.6811 | 22734.4203 | 22775.4203 | 112637.6812 | 24.4555
338 | E-SOR-TOU-CC-FP-HC-R10 | 2379.9944 | -92.8864 | 2287.108 | 25678.7212 | 0.089066 | 0.92019 | 0.84986 | 1.5146 | 5.1621 | 9365.167 | 9925 | 3 | 4 | 20630.2928 | 22716.5559 | 22757.5559 | 100063.2929 | 33.8006
339 | E-SOR-TOU-CC-FP-HC-R10 | 881.5409 | -117.4588 | 764.0821 | 25658.1344 | 0.029779 | 0.86399 | 0.8499 | 1.348 | 5.1626 | 3330.3988 | 8075 | 3 | 4 | 21975.1149 | 22698.0264 | 22739.0264 | 86608.115 | 83.5893
340 | E-SOR-TOU-CC-FP-HC-R10 | -474.6637 | -144.9807 | -619.6443 | 25634.8563 | -0.024172 | 0.81849 | 0.84992 | 1.1775 | 5.1619 | -2140.2891 | 6400 | 3 | 4 | 23191.2681 | 22677.0824 | 22718.0824 | 74424.2682 | -83.4449
341 | E-SOR-TOU-CC-FP-HC-R10 | -3375.7763 | -182.107 | -3557.8833 | 25590.1381 | -0.13903 | 0.73597 | 0.84997 | 0.97104 | 5.1601 | -13806.6169 | 4675 | 3 | 4 | 25784.2938 | 22636.8309 | 22677.8309 | 63217.2938 | -11.3943
342 | E-SOR-TOU-CC-FP-HC-R600 | 4813.4718 | 66.644 | 4880.1159 | 19328.2198 | 0.25249 | 1.1574 | 0.87958 | 1.9567 | 5.2311 | 19364.9607 | 13150 | 3 | 4 | 12558.6899 | 16930.801 | 16971.801 | 117791.6899 | 20.6593
343 | E-SOR-TOU-CC-FP-HC-R600 | 3668.1996 | 48.3656 | 3716.5652 | 19309.4962 | 0.19247 | 1.0715 | 0.87962 | 1.7234 | 5.23 | 14753.4077 | 11275 | 3 | 4 | 13583.5551 | 16913.9541 | 16954.9541 | 103816.5551 | 23.3715
344 | E-SOR-TOU-CC-FP-HC-R600 | 2172.8823 | 23.5426 | 2196.4249 | 19280.5619 | 0.11392 | 0.9766 | 0.87976 | 1.4802 | 5.2317 | 8730.7668 | 9125 | 3 | 4 | 14918.201 | 16887.9206 | 16928.9206 | 87951.201 | 32.3354
345 | E-SOR-TOU-CC-FP-HC-R600 | 746.6062 | -3.1326 | 743.4736 | 19237.0331 | 0.038648 | 0.90021 | 0.87987 | 1.2884 | 5.2293 | 2981.2038 | 7250 | 3 | 4 | 16178.6756 | 16848.7416 | 16889.7416 | 74211.6756 | 77.1002
346 | E-SOR-TOU-CC-FP-HC-R600 | -998.0584 | -34.8598 | -1032.9182 | 19166.3872 | -0.053892 | 0.82139 | 0.88017 | 1.1136 | 5.2308 | -4050.3332 | 5325 | 3 | 4 | 17704.3318 | 16785.1634 | 16826.1634 | 60337.332 | -42.1245
347 | E-SOR-TOU-CC-FP-HC-R600 | 3947.2489 | 64.5856 | 4011.8345 | 19324.4973 | 0.2076 | 1.0919 | 0.87963 | 1.8207 | 5.2325 | 15896.6383 | 12400 | 3 | 4 | 13336.1739 | 16927.4493 | 16968.4493 | 112569.1739 | 23.8297
348 | E-SOR-TOU-CC-FP-HC-R600 | 2907.0872 | 47.5857 | 2954.6729 | 19305.6203 | 0.15305 | 1.0216 | 0.87965 | 1.6315 | 5.2305 | 11707.6583 | 10625 | 3 | 4 | 14265.5455 | 16910.4754 | 16951.4754 | 99298.5455 | 27.8701
349 | E-SOR-TOU-CC-FP-HC-R600 | 1589.431 | 23.4765 | 1612.9076 | 19274.7553 | 0.08368 | 0.94441 | 0.87981 | 1.4207 | 5.2327 | 6396.8517 | 8625 | 3 | 4 | 15438.1151 | 16882.689 | 16923.689 | 84471.1151 | 41.8793
350 | E-SOR-TOU-CC-FP-HC-R600 | 189.57 | -2.6301 | 186.9398 | 19227.4737 | 0.0097225 | 0.87398 | 0.87994 | 1.2472 | 5.2308 | 753.8963 | 6800 | 3 | 4 | 16671.0941 | 16840.129 | 16881.129 | 71104.0942 | 290.0557
351 | E-SOR-TOU-CC-FP-HC-R60 | -1572.6511 | -34.6482 | -1607.2993 | 19161.2807 | -0.083883 | 0.79864 | 0.88015 | 1.0796 | 5.2292 | -6348.3515 | 5025 | 3 | 4 | 18216.7479 | 16780.573 | 16821.573 | 58449.748 | -25.8995
352 | E-SOR-TOU-CC-FP-HC-R60 | 2393.5077 | 57.2939 | 2450.8016 | 19298.2496 | 0.127 | 0.99115 | 0.87968 | 1.5753 | 5.2309 | 9669.5206 | 11650 | 3 | 4 | 14715.2971 | 16903.8304 | 16944.8304 | 107948.2972 | 37.1321
353 | E-SOR-TOU-CC-FP-HC-R60 | 1321.9932 | 41.1759 | 1363.1691 | 19265.0278 | 0.070759 | 0.93128 | 0.87982 | 1.438 | 5.2314 | 5356.5992 | 9925 | 3 | 4 | 15659.4432 | 16873.9426 | 16914.9426 | 95092.4433 | 57.3498
354 | E-SOR-TOU-CC-FP-HC-R60 | -16.9162 | 18.91 | 1.9938 | 19231.8797 | 0.00010367 | 0.86554 | 0.87991 | 1.2833 | 5.2301 | -36.148 | 8075 | 3 | 4 | 16847.9932 | 16844.1146 | 16885.1146 | 81480.9933 | 32397.9708
355 | E-SOR-TOU-CC-FP-HC-R60 | -1172.6104 | -10.7753 | -1183.3857 | 19190.1339 | -0.061666 | 0.81533 | 0.8801 | 1.1413 | 5.2319 | -4708.4005 | 6400 | 3 | 4 | 17868.3537 | 16806.5392 | 16847.5392 | 69101.3538 | -44.1562
356 | E-SOR-TOU-CC-FP-HC-R60 | -4025.7651 | -46.0031 | -4071.7682 | 19120.0227 | -0.21296 | 0.71375 | 0.8803 | 0.96644 | 5.2293 | -16179.7321 | 4675 | 3 | 4 | 20394.2353 | 16743.4449 | 16784.4449 | 57827.2353 | -10.0798
357 | E-SOR-TOU-CC-FP-WC-R100 | 9650.1937 | 525.3278 | 10175.5215 | 35464.8343 | 0.28692 | 1.1802 | 0.85 | 2.9115 | 5.1067 | 39476.3212 | 18475 | 3 | 4 | 22413.5064 | 31403.1771 | 31444.1771 | 170246.5064 | 13.6408
358 | E-SOR-TOU-CC-FP-WC-R100 | 8017.6073 | 518.4407 | 8536.0479 | 35436.3515 | 0.24088 | 1.1087 | 0.85002 | 2.5506 | 5.1059 | 32934.4969 | 15750 | 3 | 4 | 23861.3637 | 31377.5508 | 31418.5508 | 149894.3637 | 13.8795
359 | E-SOR-TOU-CC-FP-WC-R100 | 6056.2471 | 506.3588 | 6562.6059 | 35394.8195 | 0.18541 | 1.0332 | 0.85007 | 2.1703 | 5.1055 | 25068.9196 | 12975 | 3 | 4 | 25596.4814 | 31340.1729 | 31381.1729 | 129429.4814 | 14.9405
360 | E-SOR-TOU-CC-FP-WC-R100 | 3842.9726 | 484.6698 | 4327.6424 | 35346.7034 | 0.12243 | 0.95911 | 0.85013 | 1.7909 | 5.1063 | 16179.6734 | 10200 | 3 | 4 | 27558.1746 | 31296.8698 | 31337.8698 | 109191.1746 | 17.9898
361 | E-SOR-TOU-CC-FP-WC-R100 | 1322.9884 | 456.2865 | 1779.2749 | 35296.4196 | 0.050409 | 0.88638 | 0.85016 | 1.4958 | 5.1042 | 6052.431 | 7425 | 3 | 4 | 29797.9737 | 31251.633 | 31292.633 | 89230.9737 | 32.5629
362 | E-SOR-TOU-CC-FP-WC-R100 | 8549.6457 | 527.2017 | 9076.8473 | 35464.0737 | 0.25594 | 1.131 | 0.84999 | 2.7055 | 5.1053 | 35077.2522 | 17425 | 3 | 4 | 23402.1979 | 31402.4901 | 31443.4901 | 162835.1979 | 14.4755
363 | E-SOR-TOU-CC-FP-WC-R100 | 7041.2169 | 518.4201 | 7559.6369 | 35432.4062 | 0.21335 | 1.0698 | 0.85002 | 2.3736 | 5.105 | 29028.9009 | 14800 | 3 | 4 | 24736.5749 | 31373.9938 | 31414.9938 | 143169.5749 | 14.7831
364 | E-SOR-TOU-CC-FP-WC-R100 | 5273.6058 | 504.4453 | 5778.0511 | 35396.4698 | 0.16324 | 1.0058 | 0.85007 | 2.0259 | 5.106 | 21935.1654 | 12225 | 3 | 4 | 26303.4929 | 31341.6523 | 31382.6523 | 124136.4929 | 16.0528
365 | E-SOR-TOU-CC-FP-WC-R100 | 3175.6527 | 484.3118 | 3659.9645 | 35353.9731 | 0.10352 | 0.93886 | 0.85012 | 1.7105 | 5.106 | 13509.797 | 9600 | 3 | 4 | 28165.5222 | 31303.422 | 31344.422 | 104998.5222 | 20.1243
366 | E-SOR-TOU-CC-FP-WC-R10 | 631.0279 | 458.0567 | 1089.0845 | 35292.0071 | 0.030859 | 0.8685 | 0.85016 | 1.4383 | 5.1039 | 3287.5392 | 7025 | 3 | 4 | 30415.7016 | 31247.6544 | 31288.6544 | 86648.7017 | 50.8317
367 | E-SOR-TOU-CC-FP-WC-R10 | 6305.1067 | 520.2798 | 6825.3865 | 35429.3752 | 0.19265 | 1.0425 | 0.85006 | 2.2778 | 5.1076 | 26087.5598 | 16325 | 3 | 4 | 25395.2149 | 31371.2425 | 31412.2425 | 156028.2149 | 18.2577
368 | E-SOR-TOU-CC-FP-WC-R10 | 4922.7669 | 512.175 | 5434.9419 | 35403.1154 | 0.15352 | 0.99425 | 0.85005 | 2.0426 | 5.1053 | 20544.6927 | 13900 | 3 | 4 | 26620.5814 | 31347.6329 | 31388.6329 | 137853.5815 | 19.589
369 | E-SOR-TOU-CC-FP-WC-R10 | 2973.3718 | 499.516 | 3472.8878 | 35366.6416 | 0.098197 | 0.93327 | 0.85007 | 1.7996 | 5.1036 | 12726.0138 | 11425 | 3 | 4 | 28349.8241 | 31314.8199 | 31355.8199 | 119782.8242 | 25.4621
370 | E-SOR-TOU-CC-FP-WC-R10 | 689.4727 | 478.6332 | 1168.1059 | 35321.8559 | 0.03307 | 0.87047 | 0.85014 | 1.5515 | 5.1048 | 3555.6127 | 9000 | 3 | 4 | 30377.5837 | 31274.5172 | 31315.5172 | 102410.5837 | 60.8635
371 | E-SOR-TOU-CC-FP-WC-R10 | -1442.2691 | 451.2122 | -991.0569 | 35261.8335 | -0.028106 | 0.81872 | 0.8502 | 1.2957 | 5.1045 | -5017.0561 | 6575 | 3 | 4 | 32258.6096 | 31220.5022 | 31261.5022 | 84891.6097 | -54.1141
372 | E-SOR-TOU-CC-FP-WC-R600 | 7508.8012 | 830.7301 | 8339.5312 | 26347.4121 | 0.31652 | 1.2732 | 0.88077 | 2.7581 | 5.1771 | 31419.7548 | 18475 | 3 | 4 | 15851.0753 | 23093.3677 | 23134.3677 | 163684.0753 | 16.8534
373 | E-SOR-TOU-CC-FP-WC-R600 | 6006.3317 | 817.996 | 6824.3277 | 26323.8644 | 0.25924 | 1.1747 | 0.88077 | 2.3744 | 5.1745 | 25388.6533 | 15750 | 3 | 4 | 17189.7905 | 23072.1983 | 23113.1983 | 143222.7905 | 17.6002
374 | E-SOR-TOU-CC-FP-WC-R600 | 4174.1427 | 801.4959 | 4975.6386 | 26288.4055 | 0.18927 | 1.0734 | 0.88086 | 1.9926 | 5.1743 | 18032.3974 | 12975 | 3 | 4 | 18816.7861 | 23040.2932 | 23081.2932 | 122649.7861 | 20.0112
375 | E-SOR-TOU-CC-FP-WC-R600 | 2169.4616 | 781.4054 | 2950.867 | 26233.8126 | 0.11248 | 0.98072 | 0.88102 | 1.6758 | 5.1748 | 9980.1887 | 10200 | 3 | 4 | 20583.9501 | 22991.1562 | 23032.1562 | 102216.9501 | 26.8344
376 | E-SOR-TOU-CC-FP-WC-R600 | -121.8558 | 754.2076 | 632.3519 | 26137.5259 | 0.024193 | 0.89221 | 0.88129 | 1.4089 | 5.1748 | 769.5897 | 7425 | 3 | 4 | 22575.8468 | 22904.509 | 22945.509 | 82008.8468 | 93.4026
377 | E-SOR-TOU-CC-FP-WC-R600 | 6442.1543 | 827.89 | 7270.0443 | 26346.374 | 0.27594 | 1.2018 | 0.88077 | 2.5379 | 5.1769 | 27148.4337 | 17425 | 3 | 4 | 16811.8282 | 23092.4266 | 23133.4266 | 156244.8282 | 18.3096
378 | E-SOR-TOU-CC-FP-WC-R600 | 4928.2756 | 818.3991 | 5746.6747 | 26316.8644 | 0.21836 | 1.1134 | 0.88083 | 2.1903 | 5.1762 | 21077.1009 | 14800 | 3 | 4 | 18153.5045 | 23065.8927 | 23106.8927 | 136586.5045 | 19.747
379 | E-SOR-TOU-CC-FP-WC-R600 | 3328.4279 | 805.26 | 4133.6879 | 26284.7293 | 0.15727 | 1.0327 | 0.8809 | 1.8868 | 5.1754 | 14655.8116 | 12225 | 3 | 4 | 19572.3541 | 23036.9752 | 23077.9752 | 117405.3541 | 22.8192
380 | E-SOR-TOU-CC-FP-WC-R600 | 1493.7946 | 784.1888 | 2277.9834 | 26222.3833 | 0.086872 | 0.95326 | 0.88107 | 1.6021 | 5.1754 | 7282.1597 | 9600 | 3 | 4 | 21180.088 | 22980.8624 | 23021.8624 | 98013.088 | 32.92
381 | E-SOR-TOU-CC-FP-WC-R60 | -605.5273 | 756.3311 | 150.8038 | 26128.49 | 0.0057716 | 0.87571 | 0.88132 | 1.375 | 5.175 | -1161.5574 | 7025 | 3 | 4 | 23001.7419 | 22896.3753 | 22937.3753 | 79234.742 | 373.3153
382 | E-SOR-TOU-CC-FP-WC-R60 | 4333.8582 | 820.5238 | 5154.382 | 26315.8838 | 0.19587 | 1.0822 | 0.88084 | 2.0917 | 5.1763 | 18702.9726 | 16325 | 3 | 4 | 18686.2843 | 23064.9826 | 23105.9826 | 149319.2843 | 24.4866
383 | E-SOR-TOU-CC-FP-WC-R60 | 3159.4776 | 814.0424 | 3973.52 | 26278.0185 | 0.15121 | 1.0254 | 0.88093 | 1.8964 | 5.1758 | 13994.6478 | 13900 | 3 | 4 | 19713.0641 | 23030.917 | 23071.917 | 130946.0642 | 27.1483
384 | E-SOR-TOU-CC-FP-WC-R60 | 1602.0391 | 799.8834 | 2401.9225 | 26222.7326 | 0.091597 | 0.9582 | 0.88105 | 1.6808 | 5.1746 | 7741.2955 | 11425 | 3 | 4 | 21073.532 | 22981.1824 | 23022.1824 | 112506.5321 | 37.2553
385 | E-SOR-TOU-CC-FP-WC-R60 | -362.0785 | 780.6939 | 418.6153 | 26158.9722 | 0.016003 | 0.88474 | 0.88123 | 1.471 | 5.1749 | -147.1576 | 9000 | 3 | 4 | 22795.3887 | 22923.7929 | 22964.7929 | 94828.3888 | 171.6698
386 | E-SOR-TOU-CC-FP-WC-R60 | -2465.4379 | 751.715 | -1713.7229 | 26069.1775 | -0.065738 | 0.81709 | 0.88149 | 1.2478 | 5.1754 | -8608.8933 | 6575 | 3 | 4 | 24625.0226 | 22842.9839 | 22883.9839 | 77258.0226 | -31.7286
387 | E-SOR-TOU-FC-ET-HC-OFF0 | -1796.2329 | -188.2197 | -1984.4526 | 2779.572 | -0.71394 | 0.62374 | 1.1789 | 1.3352 | 4.7134 | -7498.631 | 8150 | 3 | 4 | 3838.8909 | 2109.3495 | 2150.3495 | 69071.8909 | -33.7229
388 | E-SOR-TOU-FC-ET-HC-OFF0 | -2616.9521 | -221.1999 | -2838.1521 | 2779.8943 | -1.021 | 0.52898 | 1.1789 | 1.1343 | 4.7129 | -10836.4751 | 6900 | 3 | 4 | 4597.5197 | 2109.5428 | 2150.5428 | 59830.5198 | -20.3231
389 | E-SOR-TOU-FC-ET-HC-OFF0 | -3599.9433 | -257.8674 | -3857.8107 | 2779.816 | -1.3878 | 0.44765 | 1.1787 | 0.96661 | 4.7118 | -14829.5522 | 5650 | 3 | 4 | 5504.1653 | 2109.4959 | 2150.4959 | 50737.1653 | -12.5944
390 | E-SOR-TOU-FC-ET-HC-OFF0 | -4806.9999 | -293.441 | -5100.4409 | 2779.923 | -1.8347 | 0.37677 | 1.1778 | 0.82093 | 4.7054 | -19717.0679 | 4400 | 3 | 4 | 6611.9246 | 2109.5601 | 2150.5601 | 41844.9247 | -7.7825
391 | E-SOR-TOU-FC-ET-HC-OFF0 | -6014.4865 | -326.1815 | -6340.668 | 2780.0176 | -2.2808 | 0.32547 | 1.1775 | 0.71477 | 4.7034 | -24601.582 | 3150 | 3 | 4 | 7718.3636 | 2109.6169 | 2150.6169 | 32951.3637 | -4.8577
392 | E-SOR-TOU-FC-ET-HC-OFF0 | -2108.3782 | -190.8517 | -2299.2299 | 2779.6608 | -0.82716 | 0.58517 | 1.1791 | 1.2757 | 4.7144 | -8751.5989 | 7800 | 3 | 4 | 4121.4542 | 2109.4028 | 2150.4028 | 66554.4542 | -28.0111
393 | E-SOR-TOU-FC-ET-HC-OFF0 | -2956.3916 | -224.4069 | -3180.7986 | 2779.874 | -1.1442 | 0.49837 | 1.1784 | 1.0948 | 4.7098 | -12199.5781 | 6600 | 3 | 4 | 4904.9273 | 2109.5307 | 2150.5307 | 57737.9274 | -17.4759
394 | E-SOR-TOU-FC-ET-HC-OFF0 | -3904.157 | -259.0812 | -4163.2382 | 2779.6452 | -1.4978 | 0.42784 | 1.1785 | 0.9371 | 4.7103 | -16048.4301 | 5400 | 3 | 4 | 5778.5835 | 2109.3934 | 2150.3934 | 49011.5835 | -11.2559
395 | E-SOR-TOU-FC-ET-HC-OFF0 | -5105.0192 | -297.9735 | -5402.9928 | 2779.9653 | -1.9435 | 0.36288 | 1.1779 | 0.80521 | 4.7061 | -20916.6995 | 4200 | 3 | 4 | 6882.8869 | 2109.5855 | 2150.5855 | 40515.887 | -7.1008
396 | E-SOR-TOU-FC-ET-HC-OFF | -6885.01 | -345.5323 | -7230.5423 | 2779.9268 | -2.601 | 0.2968 | 1.1786 | 0.68542 | 4.7108 | -28115.927 | 3000 | 3 | 4 | 8513.3907 | 2109.5624 | 2150.5624 | 32546.3907 | -4.2038
397 | E-SOR-TOU-FC-ET-HC-OFF | -2829.1162 | -200.2938 | -3029.41 | 2779.7854 | -1.0898 | 0.51158 | 1.179 | 1.1626 | 4.7135 | -11650.2879 | 7500 | 3 | 4 | 4775.8584 | 2109.4775 | 2150.4775 | 64808.8585 | -20.6834
398 | E-SOR-TOU-FC-ET-HC-OFF | -3708.992 | -236.2497 | -3945.2418 | 2779.8011 | -1.4193 | 0.4419 | 1.1789 | 1.0125 | 4.7133 | -15229.7177 | 6350 | 3 | 4 | 5589.3296 | 2109.487 | 2150.487 | 56422.3297 | -13.7563
399 | E-SOR-TOU-FC-ET-HC-OFF | -4942.9937 | -277.6857 | -5220.6794 | 2780.1369 | -1.8778 | 0.37149 | 1.1789 | 0.87655 | 4.7128 | -20234.7842 | 4050 | 3 | 4 | 6724.9941 | 2109.6884 | 2150.6884 | 39157.9942 | -7.0886
400 | E-SOR-TOU-FC-ET-HC-R100 | 1374.437 | -345.2672 | 1029.1698 | 10794.0267 | 0.095346 | 0.90821 | 0.84926 | 1.1593 | 4.7091 | 4922.3026 | 8150 | 3 | 4 | 8440.4222 | 9470.2552 | 9511.2552 | 73673.4222 | 62.3436
401 | E-SOR-TOU-FC-ET-HC-R100 | 634.8056 | -377.0353 | 257.7703 | 10794.0294 | 0.023881 | 0.84161 | 0.84915 | 1.01 | 4.702 | 1910.8302 | 6900 | 3 | 4 | 9125.1569 | 9470.2607 | 9511.2607 | 64358.157 | 212.7743
402 | E-SOR-TOU-FC-ET-HC-R100 | -283.8069 | -410.566 | -694.3729 | 10792.8636 | -0.064336 | 0.77179 | 0.84909 | 0.87463 | 4.6982 | -1819.5042 | 5650 | 3 | 4 | 9971.0038 | 9469.238 | 9510.238 | 55204.0039 | -65.8058
403 | E-SOR-TOU-FC-ET-HC-R100 | -1380.4593 | -452.8639 | -1833.3233 | 10792.0231 | -0.16988 | 0.70222 | 0.84916 | 0.74998 | 4.7028 | -6276.6106 | 4400 | 3 | 4 | 10982.6251 | 9468.4934 | 9509.4934 | 46215.6252 | -20.0216
404 | E-SOR-TOU-FC-ET-HC-R100 | -2616.6812 | -491.7456 | -3108.4268 | 10791.0137 | -0.28806 | 0.63779 | 0.84916 | 0.62879 | 4.7023 | -11286.3008 | 3150 | 3 | 4 | 12117.647 | 9467.5866 | 9508.5866 | 37350.647 | -8.957
405 | E-SOR-TOU-FC-ET-HC-R100 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 7800 | 3 | 4 | 0 | 0 | 41 | 62433.0001 | #DIV/0!
406 | E-SOR-TOU-FC-ET-HC-R600 | 856.1523 | -300.1173 | 556.035 | 8054.9303 | 0.06903 | 0.90411 | 0.87607 | 1.1515 | 4.7746 | 2924.4137 | 8150 | 3 | 4 | 6395.38 | 6985.8467 | 7026.8467 | 71628.38 | 116.1825
407 | E-SOR-TOU-FC-ET-HC-R600 | 100.3252 | -331.133 | -230.8078 | 8054.3171 | -0.028656 | 0.8179 | 0.8757 | 0.99193 | 4.761 | -150.5875 | 6900 | 3 | 4 | 7093.7349 | 6985.3478 | 7026.3478 | 62326.735 | -239.595
408 | E-SOR-TOU-FC-ET-HC-R600 | -699.403 | -362.7358 | -1062.1388 | 8053.6845 | -0.13188 | 0.74313 | 0.87549 | 0.87064 | 4.7524 | -3402.1718 | 5650 | 3 | 4 | 7831.8437 | 6984.7395 | 7025.7395 | 53064.8438 | -43.3457
409 | E-SOR-TOU-FC-ET-HC-R600 | -1717.5146 | -399.71 | -2117.2246 | 8052.0147 | -0.26294 | 0.66597 | 0.87544 | 0.74649 | 4.7502 | -7536.2418 | 4400 | 3 | 4 | 8768.8511 | 6983.2619 | 7024.2619 | 44001.8511 | -17.4651
410 | E-SOR-TOU-FC-ET-HC-R600 | -2905.6054 | -434.3508 | -3339.9562 | 8047.6276 | -0.41502 | 0.59466 | 0.87586 | 0.6267 | 4.7643 | -12346.3396 | 7800 | 3 | 4 | 9854.9423 | 6979.287 | 7020.287 | 72287.9424 | -19.5415
411 | E-SOR-TOU-FC-ET-WC-OFF0 | 233.0091 | 654.7169 | 887.726 | 5262.4899 | 0.16869 | 1.3354 | 1.1676 | 2.7199 | 4.6042 | 2023.2313 | 15925 | 3 | 4 | 3461.1447 | 4025.1966 | 4066.1966 | 130894.1447 | 142.8683
412 | E-SOR-TOU-FC-ET-WC-OFF0 | -823.3294 | 604.8452 | -218.4842 | 5263.241 | -0.041511 | 1.0657 | 1.1674 | 2.2208 | 4.6027 | -2285.2424 | 13425 | 3 | 4 | 4442.6455 | 4025.6473 | 4066.6473 | 111875.6455 | -493.4407
413 | E-SOR-TOU-FC-ET-WC-OFF0 | -2169.1347 | 552.481 | -1616.6536 | 5263.3678 | -0.30715 | 0.84902 | 1.1673 | 1.764 | 4.6014 | -7755.7369 | 11250 | 3 | 4 | 5685.8079 | 4025.7233 | 4066.7233 | 95718.8079 | -56.6925
414 | E-SOR-TOU-FC-ET-WC-OFF0 | -3925.0175 | 490.2491 | -3434.7684 | 5263.0054 | -0.65262 | 0.67163 | 1.1674 | 1.3962 | 4.6027 | -14882.9882 | 8750 | 3 | 4 | 7303.6148 | 4025.5059 | 4066.5059 | 77336.6148 | -21.3319
415 | E-SOR-TOU-FC-ET-WC-OFF0 | -6190.8781 | 422.6562 | -5768.222 | 5263.4648 | -1.0959 | 0.52954 | 1.1673 | 1.1072 | 4.6018 | -24059.0856 | 6250 | 3 | 4 | 9384.0383 | 4025.7815 | 4066.7815 | 59417.0384 | -9.5957
416 | E-SOR-TOU-FC-ET-WC-OFF0 | -98.9615 | 646.8717 | 547.9102 | 5262.5253 | 0.10412 | 1.2391 | 1.1675 | 2.5803 | 4.6037 | 682.2734 | 15325 | 3 | 4 | 3764.6757 | 4025.2179 | 4066.2179 | 126397.6757 | 223.2692
417 | E-SOR-TOU-FC-ET-WC-OFF0 | -1143.1678 | 598.97 | -544.1977 | 5262.997 | -0.1034 | 1.0058 | 1.1673 | 2.1253 | 4.6019 | -3574.3877 | 12925 | 3 | 4 | 4733.8665 | 4025.5009 | 4066.5009 | 108166.8665 | -191.2914
418 | E-SOR-TOU-FC-ET-WC-OFF0 | -2438.9992 | 548.3874 | -1890.6118 | 5263.2964 | -0.35921 | 0.81658 | 1.1674 | 1.7205 | 4.6021 | -8842.0178 | 10800 | 3 | 4 | 5931.0114 | 4025.6805 | 4066.6805 | 92364.0115 | -46.703
419 | E-SOR-TOU-FC-ET-WC-OFF0 | -4288.2387 | 485.7448 | -3802.4939 | 5263.0554 | -0.72249 | 0.64439 | 1.1674 | 1.3561 | 4.6027 | -16343.3802 | 8400 | 3 | 4 | 7633.1487 | 4025.5359 | 4066.5359 | 74866.1488 | -18.6193
420 | E-SOR-TOU-FC-ET-WC-OFF | -6457.2115 | 418.693 | -6038.5185 | 5263.6179 | -1.1472 | 0.51683 | 1.1672 | 1.0893 | 4.6008 | -25131.0243 | 6000 | 3 | 4 | 9626.125 | 4025.8734 | 4066.8734 | 57659.1251 | -8.8751
421 | E-SOR-TOU-FC-ET-WC-OFF | -1069.332 | 630.5088 | -438.8232 | 5262.6149 | -0.083385 | 1.0245 | 1.1674 | 2.21 | 4.6027 | -3226.4799 | 14675 | 3 | 4 | 4647.8198 | 4025.2716 | 4066.2716 | 122080.8199 | -268.9342
422 | E-SOR-TOU-FC-ET-WC-OFF | -2015.2474 | 586.486 | -1428.7614 | 5262.8478 | -0.27148 | 0.87293 | 1.1674 | 1.9152 | 4.6025 | -7083.5128 | 12375 | 3 | 4 | 5525.9849 | 4025.4114 | 4066.4114 | 104558.9849 | -70.3354
423 | E-SOR-TOU-FC-ET-WC-OFF | -3137.98 | 538.6829 | -2599.2971 | 5262.6215 | -0.49392 | 0.74304 | 1.1675 | 1.6222 | 4.6036 | -11654.1152 | 10350 | 3 | 4 | 6565.3002 | 4025.2756 | 4066.2756 | 89398.3003 | -32.8289
424 | E-SOR-TOU-FC-ET-WC-OFF | -4848.5295 | 473.0632 | -4375.4663 | 5263.0207 | -0.83136 | 0.60608 | 1.1674 | 1.3193 | 4.6027 | -18605.6793 | 8050 | 3 | 4 | 8144.7926 | 4025.5151 | 4066.5151 | 72577.7926 | -15.6581
425 | E-SOR-TOU-FC-ET-WC-OFF | -7555.7886 | 395.6097 | -7160.1789 | 5263.3154 | -1.3604 | 0.47021 | 1.1673 | 1.0642 | 4.602 | -29563.8048 | 5750 | 3 | 4 | 10628.2545 | 4025.6919 | 4066.6919 | 56661.2546 | -7.3454
426 | E-SOR-TOU-FC-ET-WC-R100 | 5037.7081 | 186.7551 | 5224.4632 | 20716.34 | 0.25219 | 1.1162 | 0.84911 | 1.9516 | 4.6242 | 20462.091 | 15925 | 3 | 4 | 13623.0122 | 18259.7377 | 18300.7377 | 141056.0122 | 23.4962
427 | E-SOR-TOU-FC-ET-WC-R100 | 3713.2893 | 157.522 | 3870.8113 | 20711.8859 | 0.18689 | 1.0266 | 0.84916 | 1.6703 | 4.6267 | 15115.6939 | 13425 | 3 | 4 | 14828.5446 | 18255.6957 | 18296.6957 | 122261.5446 | 26.8587
428 | E-SOR-TOU-FC-ET-WC-R100 | 2504.5376 | 129.7101 | 2634.2477 | 20700.165 | 0.12726 | 0.95646 | 0.84916 | 1.4428 | 4.6249 | 10234.3341 | 11250 | 3 | 4 | 15922.5886 | 18245.1159 | 18286.1159 | 105955.5886 | 33.2806
429 | E-SOR-TOU-FC-ET-WC-R100 | 849.9709 | 90.9729 | 940.9439 | 20680.2325 | 0.0455 | 0.87457 | 0.84921 | 1.1941 | 4.625 | 3551.5052 | 8750 | 3 | 4 | 17417.0081 | 18227.1156 | 18268.1156 | 87450.0081 | 73.5239
430 | E-SOR-TOU-FC-ET-WC-R100 | -1139.4611 | 44.8688 | -1094.5923 | 20660.001 | -0.052981 | 0.79279 | 0.84924 | 0.99227 | 4.6248 | -4483.0631 | 6250 | 3 | 4 | 19217.0543 | 18208.9527 | 18249.9527 | 69250.0544 | -46.5928
431 | E-SOR-TOU-FC-ET-WC-R100 | 4428.7098 | 188.5937 | 4617.3035 | 20720.934 | 0.22283 | 1.0741 | 0.84916 | 1.8315 | 4.6274 | 18029.162 | 15325 | 3 | 4 | 14174.0965 | 18263.7982 | 18304.7982 | 136807.0965 | 25.6648
432 | E-SOR-TOU-FC-ET-WC-R100 | 3323.2841 | 160.063 | 3483.3472 | 20711.7995 | 0.16818 | 1.0035 | 0.84917 | 1.5948 | 4.6269 | 13559.9083 | 12925 | 3 | 4 | 15177.9603 | 18255.6132 | 18296.6132 | 118610.9603 | 28.7983
433 | E-SOR-TOU-FC-ET-WC-R100 | 2080.392 | 130.2573 | 2210.6493 | 20699.2637 | 0.1068 | 0.93457 | 0.84918 | 1.3761 | 4.626 | 8538.6636 | 10800 | 3 | 4 | 16303.2038 | 18244.315 | 18285.315 | 102736.2039 | 38.2018
434 | E-SOR-TOU-FC-ET-WC-R100 | 370.6224 | 91.5332 | 462.1556 | 20685.364 | 0.022342 | 0.85384 | 0.84918 | 1.1446 | 4.6243 | 1635.0449 | 8400 | 3 | 4 | 17852.7203 | 18231.7557 | 18272.7557 | 85085.7204 | 144.5681
435 | E-SOR-TOU-FC-ET-WC-R10 | -1750.4478 | 42.5944 | -1707.8534 | 20665.7103 | -0.082642 | 0.77105 | 0.84921 | 0.9336 | 4.6238 | -6930.8005 | 6000 | 3 | 4 | 19773.4417 | 18214.0983 | 18255.0983 | 67806.4417 | -29.0138
436 | E-SOR-TOU-FC-ET-WC-R10 | 3118.3647 | 178.9858 | 3297.3505 | 20710.8192 | 0.15921 | 0.99279 | 0.84913 | 1.5655 | 4.6253 | 12771.7684 | 14675 | 3 | 4 | 15350.1614 | 18254.7898 | 18295.7898 | 132783.1614 | 34.721
437 | E-SOR-TOU-FC-ET-WC-R10 | 1789.4421 | 148.1374 | 1937.5795 | 20700.6029 | 0.0936 | 0.92092 | 0.84913 | 1.3807 | 4.6236 | 7404.6642 | 12375 | 3 | 4 | 16555.4822 | 18245.5345 | 18286.5345 | 115588.4822 | 50.2183
438 | E-SOR-TOU-FC-ET-WC-R10 | 520.0996 | 117.8852 | 637.9848 | 20690.67 | 0.030834 | 0.86131 | 0.84917 | 1.2071 | 4.6248 | 2276.8737 | 10350 | 3 | 4 | 17707.1306 | 18236.5826 | 18277.5826 | 100540.1307 | 128.9412
439 | E-SOR-TOU-FC-ET-WC-R10 | -1437.1264 | 78.701 | -1358.4254 | 20676.9265 | -0.065698 | 0.78331 | 0.8492 | 1.02 | 4.6247 | -5617.3372 | 8050 | 3 | 4 | 19479.8255 | 18224.2194 | 18265.2194 | 83912.8255 | -48.3263
440 | E-SOR-TOU-FC-ET-WC-R10 | -4338.9879 | 17.6647 | -4321.3232 | 20663.3138 | -0.20913 | 0.69041 | 0.84924 | 0.81701 | 4.6252 | -17326.5104 | 5750 | 3 | 4 | 22115.8862 | 18211.9538 | 18252.9538 | 68148.8862 | -11.5464
441 | E-SOR-TOU-FC-ET-WC-R600 | 3893.7018 | 334.0453 | 4227.747 | 15299.6933 | 0.27633 | 1.1855 | 0.87604 | 1.8961 | 4.6794 | 16131.5491 | 15925 | 3 | 4 | 9642.3469 | 13335.4905 | 13376.4905 | 137075.3469 | 29.2588
442 | E-SOR-TOU-FC-ET-WC-R600 | 2741.5658 | 305.0455 | 3046.6113 | 15286.5821 | 0.1993 | 1.0715 | 0.87609 | 1.6232 | 4.6789 | 11474.6723 | 13425 | 3 | 4 | 10684.9024 | 13323.639 | 13364.639 | 118117.9024 | 34.3835
443 | E-SOR-TOU-FC-ET-WC-R600 | 1502.4101 | 276.118 | 1778.5281 | 15275.481 | 0.11643 | 0.97109 | 0.87616 | 1.3857 | 4.6791 | 6469.8372 | 11250 | 3 | 4 | 11807.5215 | 13313.602 | 13354.602 | 101840.5215 | 49.7523
444 | E-SOR-TOU-FC-ET-WC-R600 | -73.2298 | 239.2422 | 166.0124 | 15258.0682 | 0.01088 | 0.86745 | 0.87615 | 1.1498 | 4.6761 | 105.8178 | 8750 | 3 | 4 | 13232.1112 | 13297.9174 | 13338.9174 | 83265.1112 | 421.2107
445 | E-SOR-TOU-FC-ET-WC-R600 | -1957.0149 | 193.794 | -1763.221 | 15214.9802 | -0.11589 | 0.7691 | 0.87643 | 0.94874 | 4.6789 | -7505.0698 | 6250 | 3 | 4 | 14916.0508 | 13259.1089 | 13300.1089 | 64949.0509 | -29.2924
446 | E-SOR-TOU-FC-ET-WC-R600 | 3257.1638 | 334.6962 | 3591.86 | 15299.2036 | 0.23477 | 1.1212 | 0.87607 | 1.7605 | 4.6805 | 13586.4821 | 15325 | 3 | 4 | 10214.4368 | 13335.0679 | 13376.0679 | 132847.4368 | 33.2617
447 | E-SOR-TOU-FC-ET-WC-R600 | 2141.8606 | 306.7186 | 2448.5792 | 15288.3905 | 0.16016 | 1.0216 | 0.87609 | 1.5237 | 4.6793 | 9078.6401 | 12925 | 3 | 4 | 11225.303 | 13325.3168 | 13366.3168 | 114658.303 | 41.3677
448 | E-SOR-TOU-FC-ET-WC-R600 | 993.9164 | 277.0757 | 1270.9921 | 15277.1088 | 0.083196 | 0.93588 | 0.87614 | 1.3219 | 4.6793 | 4437.4585 | 10800 | 3 | 4 | 12266.1196 | 13315.1319 | 13356.1319 | 98699.1197 | 67.1467
449 | E-SOR-TOU-FC-ET-WC-R600 | -537.6119 | 239.8174 | -297.7945 | 15258.0362 | -0.019517 | 0.8416 | 0.87617 | 1.1069 | 4.6768 | -1750.752 | 8400 | 3 | 4 | 13649.6709 | 13297.8914 | 13338.8914 | 80882.6709 | -226.8134
450 | E-SOR-TOU-FC-ET-WC-R60 | -2395.7273 | 190.9817 | -2204.7456 | 15214.374 | -0.14491 | 0.7496 | 0.87643 | 0.90764 | 4.6795 | -9264.6062 | 6000 | 3 | 4 | 15312.0733 | 13258.6265 | 13299.6265 | 63345.0733 | -22.699
451 | E-SOR-TOU-FC-ET-WC-R60 | 1927.9304 | 330.1259 | 2258.0563 | 15293.9328 | 0.14764 | 1.0066 | 0.87609 | 1.4837 | 4.6803 | 8261.9315 | 14675 | 3 | 4 | 11408.6985 | 13330.2877 | 13371.2877 | 128841.6986 | 51.1371
452 | E-SOR-TOU-FC-ET-WC-R60 | 850.3729 | 300.903 | 1151.2759 | 15279.9744 | 0.075345 | 0.9279 | 0.87611 | 1.3261 | 4.6789 | 3902.9966 | 12375 | 3 | 4 | 12383.5667 | 13317.7732 | 13358.7732 | 111416.5668 | 85.1732
453 | E-SOR-TOU-FC-ET-WC-R60 | -291.0705 | 268.5332 | -22.5373 | 15261.4554 | -0.0014767 | 0.85675 | 0.87615 | 1.158 | 4.6769 | -716.7267 | 10350 | 3 | 4 | 13413.5612 | 13301.0047 | 13342.0047 | 96246.5613 | -3678.5524
454 | E-SOR-TOU-FC-ET-WC-R60 | -2038.2656 | 228.9244 | -1809.3412 | 15229.9003 | -0.1188 | 0.76703 | 0.87634 | 0.98604 | 4.6791 | -7771.5218 | 8050 | 3 | 4 | 14981.5276 | 13272.6697 | 13313.6697 | 79414.5276 | -36.5331
455 | E-SOR-TOU-FC-ET-WC-R60 | -4872.5743 | 169.0901 | -4703.4842 | 15198.1992 | -0.30948 | 0.65539 | 0.87644 | 0.79497 | 4.6774 | -19208.4805 | 5750 | 3 | 4 | 17539.7647 | 13244.0963 | 13285.0963 | 63572.7647 | -10.6916
456 | E-SOR-TOU-FC-FP-HC-OFF0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 5550 | 3 | 4 | 0 | 0 | 41 | 44433 | #DIV/0!
457 | E-SOR-TOU-FC-FP-HC-OFF0 | -3571.2232 | -209.1979 | -3780.4211 | 2779.9638 | -1.3599 | 0.45232 | 1.1771 | 0.95665 | 4.7009 | -14633.5561 | 4700 | 3 | 4 | 5449.2042 | 2109.5845 | 2150.5845 | 43082.2043 | -10.8273
458 | E-SOR-TOU-FC-FP-HC-OFF0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 3850 | 3 | 4 | 0 | 0 | 41 | 30833.0001 | #DIV/0!
459 | E-SOR-TOU-FC-FP-HC-R100 | 765.3867 | -357.3578 | 408.0289 | 10794.0571 | 0.037801 | 0.85415 | 0.84951 | 0.97886 | 4.725 | 2465.9504 | 5550 | 3 | 4 | 8995.8638 | 9470.2972 | 9511.2972 | 53428.8638 | 107.6335
460 | E-SOR-TOU-FC-FP-HC-R100 | 64.8769 | -381.2073 | -316.3304 | 10793.3268 | -0.029308 | 0.79829 | 0.84934 | 0.87457 | 4.7134 | -375.8379 | 4700 | 3 | 4 | 9639.9597 | 9469.6245 | 9510.6245 | 47272.9598 | -119.3763
461 | E-SOR-TOU-FC-FP-HC-R100 | -771.4685 | -409.1967 | -1180.6652 | 10792.4619 | -0.1094 | 0.74056 | 0.84923 | 0.78368 | 4.7057 | -3767.8685 | 3850 | 3 | 4 | 10408.6508 | 9468.8112 | 9509.8112 | 41241.6509 | -26.8762
462 | E-SOR-TOU-FC-FP-HC-R100 | -1790.3626 | -443.8799 | -2234.2425 | 10792.1457 | -0.20702 | 0.68073 | 0.84932 | 0.6978 | 4.7122 | -7901.2502 | 3000 | 3 | 4 | 11346.2315 | 9468.5772 | 9509.5772 | 35379.2316 | -11.5787
463 | E-SOR-TOU-FC-FP-HC-R100 | -2837.1821 | -480.1476 | -3317.3297 | 10790.8258 | -0.30742 | 0.62848 | 0.84935 | 0.60337 | 4.7135 | -12148.9743 | 2150 | 3 | 4 | 12308.929 | 9467.3766 | 9508.3766 | 29541.929 | -6.0391
464 | E-SOR-TOU-FC-FP-HC-R100 | 224.3152 | -364.5349 | -140.2197 | 10793.538 | -0.012991 | 0.81122 | 0.84941 | 0.92837 | 4.7191 | 289.7027 | 5200 | 3 | 4 | 9486.7008 | 9469.8636 | 9510.8636 | 51119.7009 | -296.7403
465 | E-SOR-TOU-FC-FP-HC-R100 | -549.015 | -390.3107 | -939.3257 | 10793.3246 | -0.087028 | 0.75591 | 0.84934 | 0.84344 | 4.7133 | -2846.5779 | 4400 | 3 | 4 | 10197.8982 | 9469.5982 | 9510.5982 | 45430.8982 | -38.2405
466 | E-SOR-TOU-FC-FP-HC-R100 | -1172.763 | -422.2457 | -1595.0087 | 10792.9896 | -0.14778 | 0.71594 | 0.8494 | 0.75391 | 4.7168 | -5394.7948 | 3600 | 3 | 4 | 10778.1354 | 9469.3013 | 9510.3013 | 39611.1354 | -18.8719
467 | E-SOR-TOU-FC-FP-HC-R100 | -2408.7647 | -456.179 | -2864.9437 | 10792.2072 | -0.26546 | 0.64938 | 0.84942 | 0.65225 | 4.7182 | -10395.3572 | 2800 | 3 | 4 | 11910.2011 | 9468.6054 | 9509.6054 | 34343.2011 | -8.6681
468 | E-SOR-TOU-FC-FP-HC-R10 | -4614.798 | -481.0827 | -5095.8807 | 10791.5492 | -0.47221 | 0.55815 | 0.84937 | 0.52938 | 4.7154 | -19260.9966 | 2000 | 3 | 4 | 13910.0174 | 9468.0495 | 9509.0495 | 29943.0174 | -4.0099
469 | E-SOR-TOU-FC-FP-HC-R10 | -1048.6016 | -390.8039 | -1439.4055 | 10793.3874 | -0.13336 | 0.72507 | 0.84942 | 0.81144 | 4.7194 | -4845.7462 | 4900 | 3 | 4 | 10647.9403 | 9469.7166 | 9510.7166 | 49880.9404 | -28.0465
470 | E-SOR-TOU-FC-FP-HC-R10 | -2068.5727 | -419.877 | -2488.4497 | 10793.121 | -0.23056 | 0.6679 | 0.84955 | 0.73217 | 4.7267 | -8974.0859 | 4150 | 3 | 4 | 11583.0801 | 9469.4384 | 9510.4384 | 44816.0801 | -14.1878
471 | E-SOR-TOU-FC-FP-HC-R10 | -3596.266 | -435.7677 | -4032.0337 | 10792.8438 | -0.37358 | 0.59828 | 0.84944 | 0.61528 | 4.7199 | -15111.3436 | 2650 | 3 | 4 | 12967.297 | 9469.1969 | 9510.1969 | 34200.297 | -6.1235
472 | E-SOR-TOU-FC-FP-HC-R600 | 171.0539 | -308.9114 | -137.8575 | 8054.661 | -0.017115 | 0.8276 | 0.87614 | 0.96672 | 4.7773 | 169.3634 | 5550 | 3 | 4 | 7017.0041 | 6985.6057 | 7026.6057 | 51450.0041 | -322.2414
473 | E-SOR-TOU-FC-FP-HC-R600 | -458.5494 | -334.66 | -793.2094 | 8053.8886 | -0.098488 | 0.76616 | 0.87599 | 0.8735 | 4.7716 | -2391.9642 | 4700 | 3 | 4 | 7598.4232 | 6984.9328 | 7025.9328 | 45231.4233 | -48.1657
474 | E-SOR-TOU-FC-FP-HC-R600 | -1198.9964 | -360.9746 | -1559.971 | 8052.5503 | -0.19372 | 0.70493 | 0.87587 | 0.78756 | 4.7669 | -5397.61 | 3850 | 3 | 4 | 8279.4365 | 6983.755 | 7024.755 | 39112.4366 | -20.5694
475 | E-SOR-TOU-FC-FP-HC-R600 | -2091.6665 | -389.1027 | -2480.7692 | 8050.1681 | -0.30816 | 0.64319 | 0.87578 | 0.70137 | 4.7629 | -9015.1705 | 3000 | 3 | 4 | 9097.5797 | 6981.6183 | 7022.6183 | 33130.5798 | -10.5241
476 | E-SOR-TOU-FC-FP-HC-R600 | -3104.2551 | -418.8142 | -3523.0694 | 8046.6748 | -0.43783 | 0.58522 | 0.87585 | 0.60577 | 4.7641 | -13115.0443 | 2150 | 3 | 4 | 10023.569 | 6978.4508 | 7019.4508 | 27256.569 | -5.7442
477 | E-SOR-TOU-FC-FP-HC-R600 | -321.6925 | -317.7864 | -639.4789 | 8055.0082 | -0.079389 | 0.77993 | 0.87623 | 0.92344 | 4.781 | -1816.414 | 5200 | 3 | 4 | 7466.1411 | 6985.9461 | 7026.9461 | 49099.1412 | -65.7914
478 | E-SOR-TOU-FC-FP-HC-R600 | -991.9049 | -341.8989 | -1333.8038 | 8053.8889 | -0.16561 | 0.72206 | 0.87602 | 0.83888 | 4.7728 | -4537.4511 | 4400 | 3 | 4 | 8082.7914 | 6984.9377 | 7025.9377 | 43315.7915 | -27.2078
479 | E-SOR-TOU-FC-FP-HC-R600 | -1567.4673 | -366.8254 | -1934.2926 | 8052.0983 | -0.24022 | 0.67844 | 0.87579 | 0.74587 | 4.763 | -6881.2447 | 3600 | 3 | 4 | 8614.1299 | 6983.3142 | 7024.3142 | 37447.13 | -15.7281
480 | E-SOR-TOU-FC-FP-HC-R600 | -2713.3833 | -400.3326 | -3113.716 | 8050.1109 | -0.38679 | 0.60681 | 0.87591 | 0.64962 | 4.7671 | -11520.7544 | 2800 | 3 | 4 | 9663.7633 | 6981.5188 | 7022.5188 | 32096.7634 | -8.0528
481 | E-SOR-TOU-FC-FP-HC-R60 | -4784.7234 | -421.9677 | -5206.6911 | 8048.1829 | -0.64694 | 0.51103 | 0.87603 | 0.53365 | 4.7717 | -19842.1733 | 2000 | 3 | 4 | 11539.2627 | 6979.831 | 7020.831 | 27572.2627 | -3.9471
482 | E-SOR-TOU-FC-FP-HC-R60 | -1410.2762 | -336.5447 | -1746.8209 | 8053.8938 | -0.21689 | 0.69162 | 0.876 | 0.80399 | 4.7722 | -6202.0127 | 4900 | 3 | 4 | 8456.1216 | 6984.9462 | 7025.9462 | 47689.1216 | -23.2784
483 | E-SOR-TOU-FC-FP-HC-R60 | -2310.921 | -361.3478 | -2672.2688 | 8052.7003 | -0.33185 | 0.6319 | 0.87598 | 0.72365 | 4.771 | -9845.9304 | 4150 | 3 | 4 | 9280.5196 | 6983.882 | 7024.882 | 42513.5196 | -13.2803
484 | E-SOR-TOU-FC-FP-HC-R60 | -3756.3925 | -377.264 | -4133.6565 | 8051.7667 | -0.51339 | 0.55614 | 0.87604 | 0.61717 | 4.7728 | -15654.3432 | 2650 | 3 | 4 | 10590.1461 | 6983.0345 | 7024.0345 | 31823.1461 | -5.9993
485 | E-SOR-TOU-FC-FP-WC-OFF0 | -2641.7422 | 1071.267 | -1570.4751 | 5263.233 | -0.29839 | 0.85485 | 1.1674 | 1.7724 | 4.6023 | -8781.5237 | 10825 | 3 | 4 | 5784.1245 | 4025.6425 | 4066.6425 | 92417.1245 | -56.2572
486 | E-SOR-TOU-FC-FP-WC-OFF0 | -3658.7604 | 1044.0501 | -2614.7103 | 5263.3223 | -0.49678 | 0.74153 | 1.1674 | 1.5435 | 4.6021 | -12894.9581 | 9125 | 3 | 4 | 6715.9618 | 4025.6961 | 4066.6961 | 79748.9618 | -28.9448
487 | E-SOR-TOU-FC-FP-WC-OFF0 | -4733.8301 | 1014.6141 | -3719.216 | 5263.2023 | -0.70665 | 0.65036 | 1.1674 | 1.3506 | 4.6023 | -17244.2969 | 7650 | 3 | 4 | 7701.2264 | 4025.6241 | 4066.6241 | 68934.2264 | -17.4412
488 | E-SOR-TOU-FC-FP-WC-OFF0 | -6026.5159 | 978.9797 | -5047.5362 | 5263.364 | -0.95899 | 0.56654 | 1.1673 | 1.1812 | 4.6017 | -22474.4308 | 5950 | 3 | 4 | 8886.2328 | 4025.7211 | 4066.7211 | 56519.2328 | -10.3917
489 | E-SOR-TOU-FC-FP-WC-OFF0 | -7674.7784 | 937.462 | -6737.3164 | 5263.5134 | -1.28 | 0.48679 | 1.1673 | 1.0269 | 4.6018 | -29136.677 | 4250 | 3 | 4 | 10394.7584 | 4025.8107 | 4066.8107 | 44427.7585 | -5.9907
490 | E-SOR-TOU-FC-FP-WC-OFF0 | -3021.4568 | 1063.4525 | -1958.0043 | 5263.1549 | -0.37202 | 0.80898 | 1.1674 | 1.6915 | 4.6024 | -10313.4064 | 10225 | 3 | 4 | 6130.4841 | 4025.5956 | 4066.5956 | 87963.4841 | -42.8482
491 | E-SOR-TOU-FC-FP-WC-OFF0 | -4050.7566 | 1036.7926 | -3013.964 | 5262.9733 | -0.57267 | 0.70579 | 1.1674 | 1.4803 | 4.6029 | -14475.0388 | 8625 | 3 | 4 | 7072.8625 | 4025.4867 | 4066.4867 | 76105.8625 | -23.9019
492 | E-SOR-TOU-FC-FP-WC-OFF0 | -5021.5854 | 1008.0768 | -4013.5085 | 5263.3572 | -0.76254 | 0.62971 | 1.1673 | 1.3214 | 4.602 | -18406.2134 | 7200 | 3 | 4 | 7964.1765 | 4025.717 | 4066.717 | 65597.1766 | -15.3308
493 | E-SOR-TOU-FC-FP-WC-OFF0 | -6367.228 | 970.9251 | -5396.3029 | 5263.4297 | -1.0252 | 0.54802 | 1.1673 | 1.1596 | 4.6019 | -23850.7036 | 5600 | 3 | 4 | 9197.7064 | 4025.7605 | 4066.7605 | 54030.7064 | -9.2589
494 | E-SOR-TOU-FC-FP-WC-OFF | -7958.2639 | 927.5058 | -7030.7582 | 5263.2008 | -1.3358 | 0.47518 | 1.1674 | 1.0092 | 4.6024 | -30287.2129 | 4000 | 3 | 4 | 10655.6518 | 4025.6231 | 4066.6231 | 42688.6519 | -5.4933
495 | E-SOR-TOU-FC-FP-WC-OFF | -4086.3545 | 1044.2741 | -3042.0804 | 5262.656 | -0.57805 | 0.70342 | 1.1675 | 1.5142 | 4.6035 | -14604.9611 | 9575 | 3 | 4 | 7100.0105 | 4025.2963 | 4066.2963 | 83733.0106 | -26.1882
496 | E-SOR-TOU-FC-FP-WC-OFF | -5027.9274 | 1016.4246 | -4011.5028 | 5262.8504 | -0.76223 | 0.62989 | 1.1675 | 1.3651 | 4.6031 | -18417.6687 | 8075 | 3 | 4 | 7964.3743 | 4025.4129 | 4066.4129 | 72597.3744 | -17.0836
497 | E-SOR-TOU-FC-FP-WC-OFF | -5946.4141 | 989.2074 | -4957.2067 | 5263.0389 | -0.94189 | 0.57157 | 1.1674 | 1.229 | 4.6025 | -22136.9773 | 6750 | 3 | 4 | 8807.5597 | 4025.526 | 4066.526 | 62840.5598 | -11.8563
498 | E-SOR-TOU-FC-FP-WC-OFF | -7213.8212 | 948.5627 | -6265.2585 | 5263.2246 | -1.1904 | 0.50672 | 1.1674 | 1.0986 | 4.6022 | -27274.3469 | 5250 | 3 | 4 | 9972.8384 | 4025.6374 | 4066.6374 | 52005.8384 | -7.6516
499 | E-SOR-TOU-FC-FP-WC-OFF | -9277.4392 | 911.5273 | -8365.9119 | 5263.5866 | -1.5894 | 0.4286 | 1.1673 | 0.96141 | 4.6013 | -35590.5445 | 3750 | 3 | 4 | 11852.6301 | 4025.8546 | 4066.8546 | 41885.6301 | -4.5206
500 | E-SOR-TOU-FC-FP-WC-R100 | 4006.6963 | 159.2116 | 4165.9079 | 20708.8062 | 0.20117 | 1.045 | 0.84919 | 1.5883 | 4.6282 | 16292.138 | 10825 | 3 | 4 | 14560.7104 | 18252.9158 | 18293.9158 | 101193.7104 | 19.8996
501 | E-SOR-TOU-FC-FP-WC-R100 | 2799.103 | 137.8458 | 2936.9488 | 20698.3422 | 0.14189 | 0.97279 | 0.84918 | 1.3931 | 4.6258 | 11426.155 | 9125 | 3 | 4 | 15650.9872 | 18243.4936 | 18284.4936 | 88683.9872 | 23.9703
502 | E-SOR-TOU-FC-FP-WC-R100 | 1644.885 | 116.07 | 1760.9549 | 20684.7591 | 0.085133 | 0.91247 | 0.84922 | 1.2396 | 4.6263 | 6772.9899 | 7650 | 3 | 4 | 16690.6414 | 18231.2364 | 18272.2364 | 77923.6414 | 33.8745
503 | E-SOR-TOU-FC-FP-WC-R100 | 160.8119 | 85.141 | 245.9529 | 20668.5608 | 0.0119 | 0.84481 | 0.8492 | 1.0757 | 4.623 | 785.1491 | 5950 | 3 | 4 | 18030.2676 | 18216.6085 | 18257.6085 | 65663.2676 | 192.7429
504 | E-SOR-TOU-FC-FP-WC-R100 | -1655.6822 | 49.1108 | -1606.5714 | 20647.5814 | -0.077809 | 0.77452 | 0.84924 | 0.9288 | 4.6232 | -6540.8773 | 4250 | 3 | 4 | 19667.9127 | 18197.7429 | 18238.7429 | 53700.9127 | -22.0732
505 | E-SOR-TOU-FC-FP-WC-R100 | 3342.6065 | 158.8946 | 3501.501 | 20708.4049 | 0.16909 | 1.0046 | 0.84917 | 1.5018 | 4.627 | 13635.2501 | 10225 | 3 | 4 | 15158.2346 | 18252.5621 | 18293.5621 | 96991.2346 | 22.4754
506 | E-SOR-TOU-FC-FP-WC-R100 | 2253.4095 | 136.4335 | 2389.843 | 20696.5116 | 0.11547 | 0.94377 | 0.84921 | 1.3305 | 4.6275 | 9241.0272 | 8625 | 3 | 4 | 16141.3052 | 18241.8312 | 18282.8312 | 85174.3052 | 27.9899
507 | E-SOR-TOU-FC-FP-WC-R100 | 1098.1993 | 112.4337 | 1210.633 | 20685.876 | 0.058525 | 0.88669 | 0.84923 | 1.1883 | 4.6272 | 4580.1867 | 7200 | 3 | 4 | 17185.8587 | 18232.2604 | 18273.2604 | 74818.8588 | 46.7075
508 | E-SOR-TOU-FC-FP-WC-R100 | -491.8446 | 81.5288 | -410.3158 | 20672.21 | -0.019849 | 0.81853 | 0.84922 | 1.0355 | 4.6254 | -1831.497 | 5600 | 3 | 4 | 18623.2149 | 18220.0032 | 18261.0032 | 63456.215 | -110.1474
509 | E-SOR-TOU-FC-FP-WC-R10 | -2354.3528 | 44.0624 | -2310.2903 | 20654.1568 | -0.11186 | 0.75081 | 0.84924 | 0.8698 | 4.624 | -9343.9736 | 4000 | 3 | 4 | 20305.6418 | 18203.6493 | 18244.6493 | 52338.6418 | -14.7574
510 | E-SOR-TOU-FC-FP-WC-R10 | 1672.6812 | 142.5388 | 1815.22 | 20696.0939 | 0.087708 | 0.91501 | 0.84917 | 1.3036 | 4.6252 | 6928.2894 | 9575 | 3 | 4 | 16659.8603 | 18241.4466 | 18282.4466 | 93292.8604 | 41.323
511 | E-SOR-TOU-FC-FP-WC-R10 | 421.6499 | 120.8599 | 542.5098 | 20687.669 | 0.026224 | 0.85722 | 0.84916 | 1.1864 | 4.6239 | 1888.0329 | 8075 | 3 | 4 | 17791.2719 | 18233.8946 | 18274.8946 | 82424.272 | 118.2456
512 | E-SOR-TOU-FC-FP-WC-R10 | -649.7464 | 95.562 | -554.1844 | 20678.7613 | -0.0268 | 0.81299 | 0.8492 | 1.0521 | 4.6249 | -2439.7156 | 6750 | 3 | 4 | 18762.6857 | 18225.843 | 18266.843 | 72795.6858 | -98.3948
513 | E-SOR-TOU-FC-FP-WC-R10 | -2432.6609 | 64.6789 | -2367.982 | 20664.008 | -0.11459 | 0.74897 | 0.84924 | 0.91213 | 4.6252 | -9622.8455 | 5250 | 3 | 4 | 20372.6059 | 18212.5731 | 18253.5731 | 62405.6059 | -18.6454
514 | E-SOR-TOU-FC-FP-WC-R10 | -5426.0441 | 41.7017 | -5384.3424 | 20645.1724 | -0.2608 | 0.66214 | 0.84929 | 0.74595 | 4.6262 | -21634.6736 | 3750 | 3 | 4 | 23063.5319 | 18195.6432 | 18236.6432 | 53096.5319 | -6.4743
515 | E-SOR-TOU-FC-FP-WC-R600 | 2733.4629 | 307.5796 | 3041.0426 | 15285.1592 | 0.19895 | 1.071 | 0.87606 | 1.5206 | 4.6776 | 11446.4844 | 10825 | 3 | 4 | 10689.4177 | 13322.3623 | 13363.3623 | 97322.4177 | 27.6086
516 | E-SOR-TOU-FC-FP-WC-R600 | 1663.8758 | 285.9157 | 1949.7915 | 15273.669 | 0.12766 | 0.98356 | 0.87613 | 1.3438 | 4.6778 | 7132.0292 | 9125 | 3 | 4 | 11654.7159 | 13311.9849 | 13352.9849 | 84687.7159 | 36.5858
517 | E-SOR-TOU-FC-FP-WC-R600 | 557.0349 | 263.857 | 820.8919 | 15259.0141 | 0.053797 | 0.90683 | 0.87619 | 1.1917 | 4.6773 | 2667.9012 | 7650 | 3 | 4 | 12650.8986 | 13298.73 | 13339.73 | 73883.8986 | 73.7541
518 | E-SOR-TOU-FC-FP-WC-R600 | -810.1619 | 235.264 | -574.8979 | 15232.7694 | -0.037741 | 0.82688 | 0.87627 | 1.0407 | 4.6764 | -2848.5409 | 5950 | 3 | 4 | 13875.0199 | 13275.1733 | 13316.1733 | 61508.0199 | -83.8268
519 | E-SOR-TOU-FC-FP-WC-R600 | -2489.3075 | 200.8525 | -2288.455 | 15187.6156 | -0.15068 | 0.74589 | 0.87652 | 0.89646 | 4.6778 | -9622.4757 | 4250 | 3 | 4 | 15366.2582 | 13234.4804 | 13275.4804 | 49399.2583 | -15.7852
520 | E-SOR-TOU-FC-FP-WC-R600 | 2031.2842 | 304.1115 | 2335.3957 | 15284.1442 | 0.1528 | 1.0127 | 0.87611 | 1.4354 | 4.6796 | 8631.9893 | 10225 | 3 | 4 | 11322.5976 | 13321.4976 | 13362.4976 | 93155.5976 | 34.1668
521 | E-SOR-TOU-FC-FP-WC-R600 | 1044.4314 | 283.7949 | 1328.2263 | 15272.0869 | 0.086971 | 0.93971 | 0.87611 | 1.2838 | 4.677 | 4650.717 | 8625 | 3 | 4 | 12212.0375 | 13310.5423 | 13351.5423 | 81245.0375 | 51.1159
522 | E-SOR-TOU-FC-FP-WC-R600 | 0.96784 | 261.9427 | 262.9106 | 15256.9404 | 0.017232 | 0.8731 | 0.87621 | 1.1488 | 4.6781 | 440.4426 | 7200 | 3 | 4 | 13150.7002 | 13296.9322 | 13337.9322 | 70783.7003 | 218.4993
523 | E-SOR-TOU-FC-FP-WC-R600 | -1391.3856 | 233.7733 | -1157.6123 | 15228.2764 | -0.076017 | 0.79753 | 0.87634 | 1.0017 | 4.6782 | -5175.9202 | 5600 | 3 | 4 | 14394.9436 | 13271.1082 | 13312.1082 | 59227.9436 | -39.6643
524 | E-SOR-TOU-FC-FP-WC-R60 | -2990.0946 | 195.4684 | -2794.6262 | 15187.9578 | -0.184 | 0.72487 | 0.87648 | 0.8524 | 4.6763 | -11634.5977 | 4000 | 3 | 4 | 15820.4638 | 13234.7706 | 13275.7706 | 47853.4639 | -12.3729
525 | E-SOR-TOU-FC-FP-WC-R60 | 530.2219 | 293.2859 | 823.5079 | 15269.3171 | 0.053932 | 0.90693 | 0.87615 | 1.2446 | 4.6784 | 2609.6976 | 9575 | 3 | 4 | 12666.673 | 13308.1443 | 13349.1443 | 89299.6731 | 92.2281
526 | E-SOR-TOU-FC-FP-WC-R60 | -491.3751 | 274.452 | -216.9231 | 15251.1069 | -0.014223 | 0.84601 | 0.87621 | 1.1333 | 4.6776 | -1508.0805 | 8075 | 3 | 4 | 13581.058 | 13291.7616 | 13332.7616 | 78214.0581 | -299.0981
527 | E-SOR-TOU-FC-FP-WC-R60 | -1445.5921 | 248.2687 | -1197.3234 | 15232.3701 | -0.078604 | 0.79561 | 0.87633 | 1.0087 | 4.6789 | -5368.5871 | 6750 | 3 | 4 | 14438.6928 | 13274.8507 | 13315.8507 | 68471.6928 | -46.066
528 | E-SOR-TOU-FC-FP-WC-R60 | -3074.1143 | 218.9509 | -2855.1634 | 15202.8191 | -0.1878 | 0.72254 | 0.87645 | 0.88416 | 4.6781 | -11931.5389 | 5250 | 3 | 4 | 15895.3403 | 13248.1952 | 13289.1952 | 57928.3404 | -15.6345
529 | E-SOR-TOU-FC-FP-WC-R60 | -5927.1852 | 195.9796 | -5731.2056 | 15169.9763 | -0.3778 | 0.62296 | 0.87657 | 0.73006 | 4.6775 | -23382.1082 | 3750 | 3 | 4 | 18447.4154 | 13218.693 | 13259.693 | 48480.4155 | -6.1454
530 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
531 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
532 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
533 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
534 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
535 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
536 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
537 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
538 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
539 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
540 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
541 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
542 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
543 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
544 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
545 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
546 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
547 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
548 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
549 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
550 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
551 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
552 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
553 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
554 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
555 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
556 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
557 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
558 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
559 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
560 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
561 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
562 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
563 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
564 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
565 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
566 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
567 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
568 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
569 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
570 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
571 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
572 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
573 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
574 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
575 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
576 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
577 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
578 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
579 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
580 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
581 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
582 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
583 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
584 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
585 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
586 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
587 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
588 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
589 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
590 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
591 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
592 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
593 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
594 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
595 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
596 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
597 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
598 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
599 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
600 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
601 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
602 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
603 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
604 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
605 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
606 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
607 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
608 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
609 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
610 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
611 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
612 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
613 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
614 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
615 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
616 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
617 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
618 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
619 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
620 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
621 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
622 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
623 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
624 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
625 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
626 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
627 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
628 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
629 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
630 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
631 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
632 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
633 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
634 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
635 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
636 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
637 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
638 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
639 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
640 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
641 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
642 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
643 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
644 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
645 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
646 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
647 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
648 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
649 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
650 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
651 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
652 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
653 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
654 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
655 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
656 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
657 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
658 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
659 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!
660 | ------ | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 3 | 4 | 0 | 0 | 41 | 33 | #DIV/0!

## Energetic Results
Code | Code | A_coll | V_store | q_coll | eta_coll | COP_th | SF_cooling | SF_heating | SF_DHW | totalcoolingtime | solarcoolingtime | coolingdemandtime | stagnationtime | waterconsumption wet cooling tower | Q_aux_total | P_el_SC+_total | P_el_ref_total | thermal_COP_el_cooling | thermal_COP_el_heating | Total_elec_eff | relBoilerconsumption | ref_COP_el | P_heat, fossil, ref | Efficiency_storage | Q_loss_storage
|  | [m²] | [m³] | [kWh/m²] | [-] | [-] | [-] | [-] | [-] | [h] | [h] | [h] | [h] | [m³] | [kWh] | [kWh] | [kWh] | [-] | [-] | [-] | [-] | [-] | [kWh] | [-] | [kWh]
1 | E-SOR-NAP-CC-ET-HC-R100 | 31 | 2.3 | 560.9089 | 0.32609 | 0.49586 | 0.7349 | 0.55724 | #NAME? | 954.4 | 954.4 | 1854.725 | 745.35 | 0 | 6771.8082 | 1335.7264 | 1732.1366 | 4.5206 | 65.9377 | 0.010565 | 1.4491 | 3.084 | 10012.5046 | 0.81441 | 4483.8827
2 | E-SOR-NAP-CC-ET-HC-R100 | 26.5 | 2 | 599.8611 | 0.34873 | 0.49777 | 0.64593 | 0.48907 | #NAME? | 960.55 | 960.55 | 1854.725 | 636.7 | 0 | 8320.7446 | 1363.6395 | 1732.1358 | 4.475 | 65.397 | 0.01035 | 1.3516 | 3.0841 | 9999.8196 | 0.81045 | 4590.3729
3 | E-SOR-NAP-CC-ET-HC-R100 | 21.5 | 1.6 | 645.9676 | 0.37554 | 0.4996 | 0.51387 | 0.40199 | #NAME? | 966.4 | 966.4 | 1854.725 | 514.25 | 0 | 10498.4439 | 1398.5167 | 1732.1169 | 4.4333 | 64.955 | 0.010099 | 1.2424 | 3.0843 | 9992.8014 | 0.8031 | 4801.7396
4 | E-SOR-NAP-CC-ET-HC-R100 | 17 | 1.3 | 698.5795 | 0.40612 | 0.50137 | 0.40925 | 0.31976 | #NAME? | 972.3 | 972.3 | 1854.725 | 383.425 | 0 | 12325.7636 | 1428.3272 | 1732.137 | 4.3962 | 64.1338 | 0.0098912 | 1.1684 | 3.0843 | 9983.8333 | 0.80748 | 4659.3124
5 | E-SOR-NAP-CC-ET-HC-R100 | 12.5 | 0.95 | 767.5119 | 0.4462 | 0.5029 | 0.30512 | 0.22694 | #NAME? | 977.925 | 977.925 | 1854.725 | 235.375 | 0 | 14227.396 | 1459.8806 | 1732.1219 | 4.3621 | 63.5734 | 0.0096742 | 1.1021 | 3.0845 | 9964.6587 | 0.81836 | 4326.8337
6 | E-SOR-NAP-CC-ET-HC-R100 | 31 | 1.55 | 535.1336 | 0.3111 | 0.49473 | 0.68546 | 0.50177 | #NAME? | 952.225 | 952.225 | 1854.725 | 801.875 | 0 | 7809.7704 | 1338.7561 | 1732.1443 | 4.5312 | 67.0586 | 0.01055 | 1.4002 | 3.084 | 10023.3597 | 0.80779 | 4689.795
7 | E-SOR-NAP-CC-ET-HC-R100 | 26.5 | 1.35 | 578.4717 | 0.3363 | 0.49695 | 0.6156 | 0.44976 | #NAME? | 958.525 | 958.525 | 1854.725 | 688.025 | 0 | 9008.5309 | 1362.5391 | 1732.1294 | 4.4884 | 66.3221 | 0.010368 | 1.329 | 3.0843 | 10013.6947 | 0.80767 | 4681.0534
8 | E-SOR-NAP-CC-ET-HC-R100 | 21.5 | 1.1 | 630.1801 | 0.36636 | 0.499 | 0.50083 | 0.37874 | #NAME? | 965 | 965 | 1854.725 | 552.025 | 0 | 10855.1152 | 1395.8308 | 1732.1035 | 4.4434 | 65.5658 | 0.010124 | 1.2353 | 3.0844 | 10002.8329 | 0.80342 | 4797.2313
9 | E-SOR-NAP-CC-ET-HC-R100 | 17 | 0.85 | 684.1425 | 0.39773 | 0.50069 | 0.38585 | 0.29683 | #NAME? | 971.05 | 971.05 | 1854.725 | 421.15 | 0 | 12791.0336 | 1427.6679 | 1732.1172 | 4.4095 | 65.1519 | 0.0098995 | 1.1586 | 3.0843 | 9989.6792 | 0.80098 | 4860.4118
10 | E-SOR-NAP-CC-ET-HC-R10 | 12.5 | 0.65 | 751.4165 | 0.43684 | 0.50262 | 0.28448 | 0.20132 | #NAME? | 976.925 | 976.925 | 1854.725 | 271.65 | 0 | 14678.5535 | 1459.3115 | 1732.1092 | 4.3766 | 64.9856 | 0.0096794 | 1.0941 | 3.0841 | 9967.6011 | 0.81016 | 4569.7323
11 | E-SOR-NAP-CC-ET-HC-R10 | 31 | 0.8 | 493.517 | 0.28691 | 0.49296 | 0.62189 | 0.435 | #NAME? | 950.2 | 950.2 | 1854.725 | 887.775 | 0 | 9105.4364 | 1342.4806 | 1732.1549 | 4.54 | 67.99 | 0.010524 | 1.3354 | 3.0843 | 10025.41 | 0.80916 | 4657.4332
12 | E-SOR-NAP-CC-ET-HC-R10 | 26.5 | 0.65 | 532.8953 | 0.3098 | 0.49512 | 0.56661 | 0.37429 | #NAME? | 954.75 | 954.75 | 1854.725 | 797.2 | 0 | 10219.7778 | 1364.0573 | 1732.1491 | 4.5065 | 66.8889 | 0.010358 | 1.2717 | 3.0844 | 10014.5845 | 0.80907 | 4647.5579
13 | E-SOR-NAP-CC-ET-HC-R10 | 21.5 | 0.55 | 587.0689 | 0.34129 | 0.49797 | 0.47645 | 0.29792 | #NAME? | 962.3 | 962.3 | 1854.725 | 662.975 | 0 | 11836.2574 | 1397.8945 | 1732.1306 | 4.4581 | 66.0023 | 0.010109 | 1.1919 | 3.0843 | 10001.1498 | 0.80238 | 4833.4963
14 | E-SOR-NAP-CC-ET-HC-R10 | 17 | 0.45 | 640.7132 | 0.37248 | 0.49971 | 0.3607 | 0.22115 | #NAME? | 967.825 | 967.825 | 1854.725 | 527.525 | 0 | 13733.3043 | 1432.201 | 1732.1284 | 4.4258 | 65.9489 | 0.0098665 | 1.1148 | 3.0844 | 9984.9957 | 0.79493 | 5049.9389
15 | E-SOR-NAP-CC-ET-HC-R10 | 12.5 | 0.3 | 676.1645 | 0.39309 | 0.50126 | 0.26224 | 0.079431 | #NAME? | 973 | 973 | 1854.725 | 417.475 | 0 | 15986.098 | 1467.0011 | 1732.1145 | 4.3943 | 68.3919 | 0.0096201 | 1.0377 | 3.0842 | 9951.2155 | 0.79839 | 4927.0792
16 | E-SOR-NAP-CC-ET-HC-R600 | 31 | 2.3 | 560.4146 | 0.3258 | 0.4979 | 0.72258 | 0.69605 | #NAME? | 1063.2 | 1063.2 | 2104.7 | 730.25 | 0 | 5184.477 | 1412.2089 | 1880.4509 | 4.5108 | 59.8081 | 0.0086085 | 1.3912 | 3.1068 | 7360.7845 | 0.80358 | 4430.696
17 | E-SOR-NAP-CC-ET-HC-R600 | 26.5 | 2 | 604.3534 | 0.35134 | 0.5001 | 0.64807 | 0.63775 | #NAME? | 1070.575 | 1070.575 | 2104.7 | 607.925 | 0 | 6418.1434 | 1438.3806 | 1880.4415 | 4.4666 | 57.8676 | 0.0084493 | 1.305 | 3.1069 | 7346.669 | 0.80528 | 4368.1867
18 | E-SOR-NAP-CC-ET-HC-R600 | 21.5 | 1.6 | 655.0016 | 0.38079 | 0.50183 | 0.52015 | 0.55306 | #NAME? | 1077.575 | 1077.575 | 2104.7 | 477.25 | 0 | 8447.8069 | 1474.5744 | 1880.4098 | 4.4252 | 55.7846 | 0.0082358 | 1.1908 | 3.107 | 7323.6088 | 0.79916 | 4524.9068
19 | E-SOR-NAP-CC-ET-HC-R600 | 17 | 1.3 | 711.6781 | 0.41374 | 0.50363 | 0.41177 | 0.46355 | #NAME? | 1083.475 | 1083.475 | 2104.7 | 344.45 | 0 | 10251.8278 | 1505.4454 | 1880.4339 | 4.3931 | 53.371 | 0.008057 | 1.111 | 3.1066 | 7297.3406 | 0.80268 | 4410.2504
20 | E-SOR-NAP-CC-ET-HC-R600 | 12.5 | 0.95 | 782.0517 | 0.45465 | 0.50522 | 0.30527 | 0.35298 | #NAME? | 1089.425 | 1089.425 | 2104.7 | 197.175 | 0 | 12144.7699 | 1540.009 | 1880.4119 | 4.3605 | 50.5252 | 0.0078656 | 1.035 | 3.1072 | 7267.8017 | 0.81562 | 4041.7295
21 | E-SOR-NAP-CC-ET-HC-R600 | 31 | 1.55 | 532.5306 | 0.30959 | 0.49688 | 0.67358 | 0.63968 | #NAME? | 1061.325 | 1061.325 | 2104.7 | 790.15 | 0 | 6123.1265 | 1414.9876 | 1880.4707 | 4.5215 | 59.411 | 0.008592 | 1.3378 | 3.1068 | 7360.2601 | 0.80191 | 4483.1142
22 | E-SOR-NAP-CC-ET-HC-R600 | 26.5 | 1.35 | 579.341 | 0.3368 | 0.49915 | 0.60977 | 0.58021 | #NAME? | 1068.05 | 1068.05 | 2104.7 | 671.35 | 0 | 7232.7563 | 1438.8778 | 1880.4391 | 4.4832 | 57.4836 | 0.0084496 | 1.2686 | 3.1069 | 7351.2274 | 0.80097 | 4495.0601
23 | E-SOR-NAP-CC-ET-HC-R600 | 21.5 | 1.1 | 636.7004 | 0.37015 | 0.50143 | 0.50629 | 0.50751 | #NAME? | 1075.75 | 1075.75 | 2104.7 | 519.8 | 0 | 8892.0811 | 1472.3815 | 1880.4274 | 4.4389 | 55.4525 | 0.0082546 | 1.1782 | 3.1071 | 7334.1593 | 0.79824 | 4556.0816
24 | E-SOR-NAP-CC-ET-HC-R600 | 17 | 0.85 | 693.0182 | 0.40289 | 0.50308 | 0.39371 | 0.42481 | #NAME? | 1081.85 | 1081.85 | 2104.7 | 390.925 | 0 | 10710.1555 | 1505.5593 | 1880.4262 | 4.4054 | 53.3376 | 0.0080638 | 1.0947 | 3.1069 | 7308.632 | 0.79869 | 4527.6951
25 | E-SOR-NAP-CC-ET-HC-R60 | 12.5 | 0.65 | 764.7087 | 0.44457 | 0.50491 | 0.28491 | 0.32709 | #NAME? | 1088.475 | 1088.475 | 2104.7 | 235.85 | 0 | 12548.5306 | 1539.2486 | 1880.4198 | 4.3746 | 51.0875 | 0.0078724 | 1.0267 | 3.1071 | 7272.721 | 0.80923 | 4217.4971
26 | E-SOR-NAP-CC-ET-HC-R60 | 31 | 0.8 | 490.6891 | 0.28526 | 0.49516 | 0.60411 | 0.5492 | #NAME? | 1058.85 | 1058.85 | 2104.7 | 881.45 | 0 | 7521.9159 | 1421.1763 | 1880.4621 | 4.5343 | 58.2722 | 0.0085561 | 1.258 | 3.1066 | 7360.3656 | 0.79993 | 4548.1746
27 | E-SOR-NAP-CC-ET-HC-R60 | 26.5 | 0.65 | 534.5398 | 0.31076 | 0.49721 | 0.55531 | 0.48568 | #NAME? | 1064.125 | 1064.125 | 2104.7 | 784.45 | 0 | 8467.3848 | 1441.2272 | 1880.4627 | 4.5033 | 56.3162 | 0.0084308 | 1.2043 | 3.1068 | 7342.841 | 0.80078 | 4508.9125
28 | E-SOR-NAP-CC-ET-HC-R60 | 21.5 | 0.55 | 591.5683 | 0.34391 | 0.50022 | 0.46971 | 0.41619 | #NAME? | 1072.175 | 1072.175 | 2104.7 | 643.65 | 0 | 9878.081 | 1472.8359 | 1880.4378 | 4.4584 | 54.5102 | 0.0082439 | 1.1319 | 3.1071 | 7321.5302 | 0.79826 | 4558.6297
29 | E-SOR-NAP-CC-ET-HC-R60 | 17 | 0.45 | 648.1824 | 0.37682 | 0.502 | 0.35812 | 0.34117 | #NAME? | 1078.45 | 1078.45 | 2104.7 | 504 | 0 | 11634.7058 | 1509.2437 | 1880.4142 | 4.423 | 52.7828 | 0.0080361 | 1.0501 | 3.1068 | 7294.8858 | 0.79335 | 4681.47
30 | E-SOR-NAP-CC-ET-HC-R60 | 12.5 | 0.3 | 685.1505 | 0.39831 | 0.50357 | 0.24908 | 0.16964 | #NAME? | 1084.025 | 1084.025 | 2104.7 | 395.85 | 0 | 13887.5507 | 1543.4468 | 1880.3984 | 4.4009 | 52.1005 | 0.0078306 | 0.97375 | 3.1069 | 7239.0389 | 0.79652 | 4568.4141
31 | E-SOR-NAP-CC-ET-WC-R100 | 43.5 | 3.25 | 526.6258 | 0.30616 | 0.52747 | 0.78397 | 0.57948 | #NAME? | 1133.625 | 1133.625 | 1854.725 | 865.275 | 25.651 | 8207.3433 | 994.63 | 2384.7477 | 9.551 | 79.9406 | 0.019357 | 1.4545 | 3.0477 | 13796.9471 | 0.85311 | 4570.4556
32 | E-SOR-NAP-CC-ET-WC-R100 | 37 | 2.8 | 568.9526 | 0.33076 | 0.52991 | 0.70668 | 0.51306 | #NAME? | 1139.575 | 1139.575 | 1854.725 | 746.05 | 25.6381 | 10097.9122 | 1013.2179 | 2384.6995 | 9.4719 | 80.3647 | 0.018998 | 1.3596 | 3.0478 | 13769.8818 | 0.84945 | 4689.5013
33 | E-SOR-NAP-CC-ET-WC-R100 | 30.5 | 2.3 | 610.8021 | 0.35509 | 0.53232 | 0.5854 | 0.43478 | #NAME? | 1145.475 | 1145.475 | 1854.725 | 623.575 | 25.6399 | 12754.3107 | 1039.3715 | 2384.6246 | 9.391 | 80.9126 | 0.018533 | 1.2499 | 3.047 | 13754.9345 | 0.84067 | 5000.2639
34 | E-SOR-NAP-CC-ET-WC-R100 | 24 | 1.8 | 660.2704 | 0.38385 | 0.53454 | 0.44175 | 0.352 | #NAME? | 1151.225 | 1151.225 | 1854.725 | 490.475 | 25.6497 | 15770.8046 | 1068.4069 | 2384.613 | 9.3361 | 81.2226 | 0.018044 | 1.1524 | 3.0468 | 13739.265 | 0.83228 | 5302.9428
35 | E-SOR-NAP-CC-ET-WC-R100 | 17.5 | 1.3 | 728.8226 | 0.4237 | 0.53693 | 0.34042 | 0.25711 | #NAME? | 1157 | 1157 | 1854.725 | 326.175 | 25.6564 | 18297.877 | 1095.9243 | 2384.5612 | 9.2513 | 80.1958 | 0.017588 | 1.0797 | 3.0467 | 13705.5188 | 0.84452 | 4828.0636
36 | E-SOR-NAP-CC-ET-WC-R100 | 43.5 | 2.2 | 498.4693 | 0.28979 | 0.52711 | 0.72701 | 0.52705 | #NAME? | 1135.525 | 1135.525 | 1854.725 | 918.675 | 25.6947 | 9675.9889 | 1000.4275 | 2384.7578 | 9.542 | 81.8933 | 0.019268 | 1.3978 | 3.0481 | 13814.1397 | 0.84737 | 4786.4331
37 | E-SOR-NAP-CC-ET-WC-R100 | 37 | 1.85 | 540.5695 | 0.31426 | 0.52892 | 0.66237 | 0.46882 | #NAME? | 1139.325 | 1139.325 | 1854.725 | 810.225 | 25.6935 | 11289.8448 | 1015.1067 | 2384.7527 | 9.4864 | 81.921 | 0.018986 | 1.3216 | 3.0479 | 13792.542 | 0.84711 | 4784.2222
38 | E-SOR-NAP-CC-ET-WC-R100 | 30.5 | 1.55 | 589.5497 | 0.34274 | 0.5315 | 0.55974 | 0.40828 | #NAME? | 1144.525 | 1144.525 | 1854.725 | 675.275 | 25.6726 | 13462.2728 | 1037.7824 | 2384.6752 | 9.4168 | 82.0935 | 0.018578 | 1.2356 | 3.0475 | 13773.7736 | 0.84037 | 5019.448
39 | E-SOR-NAP-CC-ET-WC-R100 | 24 | 1.2 | 644.863 | 0.37489 | 0.5338 | 0.42522 | 0.33058 | #NAME? | 1149.825 | 1149.825 | 1854.725 | 527.825 | 25.6633 | 16282.0574 | 1066.5817 | 2384.6382 | 9.368 | 82.3582 | 0.018082 | 1.1457 | 3.0472 | 13748.3196 | 0.82947 | 5415.8276
40 | E-SOR-NAP-CC-ET-WC-R10 | 17.5 | 0.9 | 715.0928 | 0.41572 | 0.53662 | 0.32365 | 0.239 | #NAME? | 1156.475 | 1156.475 | 1854.725 | 360.9 | 25.6642 | 18761.7446 | 1094.1676 | 2384.5872 | 9.2881 | 81.7128 | 0.017617 | 1.0764 | 3.0471 | 13707.9472 | 0.83884 | 5040.4573
41 | E-SOR-NAP-CC-ET-WC-R10 | 43.5 | 1.1 | 451.6924 | 0.26259 | 0.52587 | 0.64622 | 0.45887 | #NAME? | 1135.85 | 1135.85 | 1854.725 | 1009.05 | 25.7564 | 11679.0067 | 1005.7634 | 2384.7965 | 9.5441 | 83.9305 | 0.019169 | 1.3195 | 3.0481 | 13810.2089 | 0.84907 | 4728.3301
42 | E-SOR-NAP-CC-ET-WC-R10 | 37 | 0.95 | 497.4706 | 0.28921 | 0.52744 | 0.60491 | 0.40905 | #NAME? | 1138.475 | 1138.475 | 1854.725 | 897.05 | 25.7434 | 12854.9544 | 1019.1225 | 2384.7678 | 9.4987 | 83.1717 | 0.018915 | 1.2635 | 3.048 | 13791.381 | 0.84903 | 4719.4577
43 | E-SOR-NAP-CC-ET-WC-R10 | 30.5 | 0.75 | 545.1385 | 0.31692 | 0.52995 | 0.53118 | 0.33879 | #NAME? | 1142.75 | 1142.75 | 1854.725 | 787.25 | 25.7113 | 14722.8736 | 1040.0091 | 2384.6701 | 9.4353 | 82.8291 | 0.018532 | 1.1905 | 3.0471 | 13765.1256 | 0.84374 | 4898.6324
44 | E-SOR-NAP-CC-ET-WC-R10 | 24 | 0.6 | 599.1751 | 0.34833 | 0.53271 | 0.4098 | 0.25731 | #NAME? | 1148.275 | 1148.275 | 1854.725 | 643.925 | 25.6939 | 17389.394 | 1071.4717 | 2384.6534 | 9.3779 | 83.1291 | 0.01799 | 1.1031 | 3.0471 | 13732.1776 | 0.82947 | 5417.5636
45 | E-SOR-NAP-CC-ET-WC-R10 | 17.5 | 0.45 | 664.9576 | 0.38658 | 0.53565 | 0.2916 | 0.17277 | #NAME? | 1154.8 | 1154.8 | 1854.725 | 481.45 | 25.6779 | 20009.9354 | 1099.588 | 2384.5801 | 9.3281 | 84.2513 | 0.017514 | 1.0385 | 3.0467 | 13684.3674 | 0.82893 | 5413.8897
46 | E-SOR-NAP-CC-ET-WC-R600 | 43.5 | 3.25 | 522.3267 | 0.30366 | 0.5278 | 0.77037 | 0.72065 | #NAME? | 1276.55 | 1276.55 | 2104.7 | 857.675 | 28.908 | 5959.1868 | 1033.1155 | 2604.241 | 9.3975 | 71.9529 | 0.01592 | 1.4015 | 3.0721 | 9966.7012 | 0.84455 | 4458.3238
47 | E-SOR-NAP-CC-ET-WC-R600 | 37 | 2.8 | 568.1831 | 0.33032 | 0.53007 | 0.69882 | 0.66058 | #NAME? | 1282.75 | 1282.75 | 2104.7 | 731.225 | 28.9082 | 7570.8883 | 1051.4147 | 2604.2007 | 9.329 | 70.7199 | 0.015629 | 1.3078 | 3.0719 | 9933.8533 | 0.84378 | 4466.8631
48 | E-SOR-NAP-CC-ET-WC-R600 | 30.5 | 2.3 | 615.9299 | 0.35807 | 0.53266 | 0.5851 | 0.59011 | #NAME? | 1289.85 | 1289.85 | 2104.7 | 596.675 | 28.9092 | 9927.5154 | 1076.999 | 2604.1377 | 9.2582 | 69.7253 | 0.015251 | 1.2006 | 3.071 | 9903.5861 | 0.83666 | 4690.0287
49 | E-SOR-NAP-CC-ET-WC-R600 | 24 | 1.8 | 670.3404 | 0.3897 | 0.53485 | 0.45946 | 0.50101 | #NAME? | 1296.625 | 1296.625 | 2104.7 | 454 | 28.9325 | 12603.5242 | 1107.9338 | 2604.124 | 9.1917 | 67.2564 | 0.014812 | 1.0959 | 3.0715 | 9859.1334 | 0.83381 | 4768.2708
50 | E-SOR-NAP-CC-ET-WC-R600 | 17.5 | 1.3 | 741.8806 | 0.43129 | 0.53721 | 0.34399 | 0.38925 | #NAME? | 1303.35 | 1303.35 | 2104.7 | 285.775 | 28.9516 | 15265.8969 | 1138.6246 | 2604.0956 | 9.1233 | 64.0633 | 0.014394 | 1.0142 | 3.0715 | 9810.8326 | 0.84297 | 4436.002
51 | E-SOR-NAP-CC-ET-WC-R600 | 43.5 | 2.2 | 491.794 | 0.28591 | 0.52733 | 0.7124 | 0.66938 | #NAME? | 1278.175 | 1278.175 | 2104.7 | 917.85 | 28.9683 | 7310.2713 | 1039.0708 | 2604.2515 | 9.3963 | 72.3021 | 0.015825 | 1.335 | 3.0722 | 9955.8437 | 0.84396 | 4478.7743
52 | E-SOR-NAP-CC-ET-WC-R600 | 37 | 1.85 | 537.0964 | 0.31224 | 0.52922 | 0.65019 | 0.60494 | #NAME? | 1282.9 | 1282.9 | 2104.7 | 798.45 | 28.968 | 8810.2438 | 1054.6031 | 2604.205 | 9.3513 | 70.7944 | 0.015589 | 1.2593 | 3.0723 | 9937.6051 | 0.84216 | 4527.3741
53 | E-SOR-NAP-CC-ET-WC-R600 | 30.5 | 1.55 | 592.0244 | 0.34418 | 0.53188 | 0.5651 | 0.5375 | #NAME? | 1288.85 | 1288.85 | 2104.7 | 652.125 | 28.9468 | 10682.296 | 1077.6935 | 2604.134 | 9.2829 | 69.0957 | 0.015254 | 1.175 | 3.0712 | 9916.9847 | 0.83713 | 4680.7569
54 | E-SOR-NAP-CC-ET-WC-R600 | 24 | 1.2 | 651.1614 | 0.37855 | 0.53424 | 0.4391 | 0.45804 | #NAME? | 1295.5 | 1295.5 | 2104.7 | 502.275 | 28.9532 | 13287.3772 | 1109.1482 | 2604.1235 | 9.2232 | 67.3147 | 0.014811 | 1.0782 | 3.0716 | 9875.9252 | 0.82851 | 4958.696
55 | E-SOR-NAP-CC-ET-WC-R60 | 17.5 | 0.9 | 725.5045 | 0.42177 | 0.53695 | 0.3304 | 0.3677 | #NAME? | 1302.575 | 1302.575 | 2104.7 | 329.45 | 28.9533 | 15659.6711 | 1138.5896 | 2604.052 | 9.1456 | 64.357 | 0.0144 | 1.0049 | 3.071 | 9818.3008 | 0.84021 | 4531.0719
56 | E-SOR-NAP-CC-ET-WC-R60 | 43.5 | 1.1 | 446.0146 | 0.25929 | 0.52626 | 0.6323 | 0.57577 | #NAME? | 1279.225 | 1279.225 | 2104.7 | 1008.725 | 29.0442 | 9369.9606 | 1047.3105 | 2604.2428 | 9.4139 | 71.7455 | 0.015708 | 1.2434 | 3.0724 | 9956.1663 | 0.84301 | 4516.7469
57 | E-SOR-NAP-CC-ET-WC-R60 | 37 | 0.95 | 495.2181 | 0.2879 | 0.52787 | 0.59491 | 0.52427 | #NAME? | 1282.4 | 1282.4 | 2104.7 | 889.675 | 29.0291 | 10360.0132 | 1059.437 | 2604.2444 | 9.3736 | 70.1026 | 0.015517 | 1.1957 | 3.0721 | 9932.132 | 0.8432 | 4497.3721
58 | E-SOR-NAP-CC-ET-WC-R60 | 30.5 | 0.75 | 546.7289 | 0.31784 | 0.53037 | 0.52708 | 0.46015 | #NAME? | 1287.625 | 1287.625 | 2104.7 | 770.775 | 29.0058 | 11919.5118 | 1079.8214 | 2604.1805 | 9.308 | 68.2887 | 0.015209 | 1.1268 | 3.072 | 9895.7523 | 0.84216 | 4513.4325
59 | E-SOR-NAP-CC-ET-WC-R60 | 24 | 0.6 | 604.4575 | 0.3514 | 0.53324 | 0.41749 | 0.38294 | #NAME? | 1293.475 | 1293.475 | 2104.7 | 624.15 | 28.9732 | 14227.4504 | 1111.6346 | 2604.1132 | 9.2365 | 66.3473 | 0.014757 | 1.0385 | 3.0712 | 9850.6992 | 0.8337 | 4778.653
60 | E-SOR-NAP-CC-ET-WC-R60 | 17.5 | 0.45 | 673.4039 | 0.39149 | 0.53599 | 0.29613 | 0.28777 | #NAME? | 1300.675 | 1300.675 | 2104.7 | 455.25 | 28.9639 | 16825.009 | 1142.2773 | 2604.0842 | 9.1908 | 65.029 | 0.014323 | 0.96895 | 3.0711 | 9778.2922 | 0.83225 | 4799.2483
61 | E-SOR-NAP-CC-FP-HC-R100 | 31 | 2.3 | 509.4054 | 0.29614 | 0.49696 | 0.65174 | 0.51501 | #NAME? | 959.45 | 959.45 | 1854.725 | 415.725 | 0 | 8038.0295 | 1360.9328 | 1743.4823 | 4.4692 | 64.9434 | 0.010372 | 1.3708 | 3.0619 | 10003.0309 | 0.82444 | 4183.4717
62 | E-SOR-NAP-CC-FP-HC-R100 | 26.5 | 2 | 542.8712 | 0.3156 | 0.49876 | 0.56435 | 0.45484 | #NAME? | 964.55 | 964.55 | 1854.725 | 349.975 | 0 | 9497.7005 | 1382.088 | 1743.4704 | 4.4396 | 64.8905 | 0.010215 | 1.2955 | 3.0619 | 9995.8501 | 0.82081 | 4279.7458
63 | E-SOR-NAP-CC-FP-HC-R100 | 21.5 | 1.6 | 584.2433 | 0.33965 | 0.50041 | 0.44471 | 0.37803 | #NAME? | 970.225 | 970.225 | 1854.725 | 275.075 | 0 | 11446.3424 | 1410.4358 | 1743.48 | 4.4105 | 64.6305 | 0.010014 | 1.2072 | 3.062 | 9987.4865 | 0.81492 | 4443.2047
64 | E-SOR-NAP-CC-FP-HC-R100 | 17 | 1.3 | 634.0814 | 0.36863 | 0.5019 | 0.35298 | 0.30016 | #NAME? | 974.575 | 974.575 | 1854.725 | 194.575 | 0 | 13091.8741 | 1434.6924 | 1743.4404 | 4.3874 | 64.0381 | 0.0098428 | 1.1432 | 3.0619 | 9974.3179 | 0.81781 | 4349.0417
65 | E-SOR-NAP-CC-FP-HC-R100 | 12.5 | 0.95 | 700.9047 | 0.40747 | 0.50308 | 0.27075 | 0.21351 | #NAME? | 978.9 | 978.9 | 1854.725 | 105.3 | 0 | 14704.0652 | 1460.6097 | 1743.4386 | 4.3608 | 63.4907 | 0.0096626 | 1.0858 | 3.062 | 9954.242 | 0.83016 | 3985.3613
66 | E-SOR-NAP-CC-FP-HC-R100 | 31 | 1.55 | 481.7359 | 0.28006 | 0.49623 | 0.60222 | 0.46162 | #NAME? | 957.7 | 957.7 | 1854.725 | 453.15 | 0 | 9055.8186 | 1365.861 | 1743.4629 | 4.4768 | 65.5622 | 0.010343 | 1.3262 | 3.062 | 10013.0667 | 0.81995 | 4319.2324
67 | E-SOR-NAP-CC-FP-HC-R100 | 26.5 | 1.35 | 519.564 | 0.30205 | 0.49792 | 0.5382 | 0.41265 | #NAME? | 962.525 | 962.525 | 1854.725 | 384.35 | 0 | 10164.1393 | 1384.0106 | 1743.5019 | 4.4487 | 65.1249 | 0.010209 | 1.2687 | 3.062 | 10005.7144 | 0.82025 | 4301.9688
68 | E-SOR-NAP-CC-FP-HC-R100 | 21.5 | 1.1 | 565.3869 | 0.32869 | 0.49979 | 0.42897 | 0.3454 | #NAME? | 968.175 | 968.175 | 1854.725 | 298.725 | 0 | 11911.3389 | 1410.2422 | 1743.4549 | 4.4212 | 65.0774 | 0.010018 | 1.1936 | 3.0619 | 9992.1973 | 0.81358 | 4486.564
69 | E-SOR-NAP-CC-FP-HC-R100 | 17 | 0.85 | 613.8126 | 0.35684 | 0.50134 | 0.33404 | 0.26804 | #NAME? | 973.2 | 973.2 | 1854.725 | 219.9 | 0 | 13586.3121 | 1436.2065 | 1743.4569 | 4.3976 | 64.78 | 0.0098351 | 1.1286 | 3.062 | 9977.4062 | 0.8133 | 4484.8037
70 | E-SOR-NAP-CC-FP-HC-R10 | 12.5 | 0.65 | 675.5068 | 0.39271 | 0.50284 | 0.24927 | 0.17729 | #NAME? | 977.575 | 977.575 | 1854.725 | 133.375 | 0 | 15256.5011 | 1461.8992 | 1743.4469 | 4.3752 | 65.0307 | 0.0096564 | 1.0717 | 3.0618 | 9957.4766 | 0.82224 | 4213.0362
71 | E-SOR-NAP-CC-FP-HC-R10 | 31 | 0.8 | 433.9344 | 0.25227 | 0.49493 | 0.54101 | 0.37549 | #NAME? | 956.8 | 956.8 | 1854.725 | 524.975 | 0 | 10489.1804 | 1374.9319 | 1743.5055 | 4.478 | 65.695 | 0.010277 | 1.2555 | 3.0619 | 10012.0043 | 0.82263 | 4246.4285
72 | E-SOR-NAP-CC-FP-HC-R10 | 26.5 | 0.65 | 466.3391 | 0.27111 | 0.49657 | 0.48907 | 0.31225 | #NAME? | 960.45 | 960.45 | 1854.725 | 468.925 | 0 | 11585.8291 | 1391.8248 | 1743.4907 | 4.4562 | 65.4388 | 0.010149 | 1.2042 | 3.0619 | 9998.8234 | 0.82064 | 4294.4465
73 | E-SOR-NAP-CC-FP-HC-R10 | 21.5 | 0.55 | 510.9477 | 0.29704 | 0.49886 | 0.40616 | 0.24365 | #NAME? | 966.4 | 966.4 | 1854.725 | 380.9 | 0 | 13053.9955 | 1416.289 | 1743.4907 | 4.4274 | 65.6156 | 0.0099728 | 1.1432 | 3.0621 | 9985.3336 | 0.81501 | 4446.976
74 | E-SOR-NAP-CC-FP-HC-R10 | 17 | 0.45 | 561.5012 | 0.32643 | 0.50043 | 0.3024 | 0.18597 | #NAME? | 971.475 | 971.475 | 1854.725 | 297.075 | 0 | 14652.3956 | 1443.6731 | 1743.4297 | 4.4075 | 66.0301 | 0.0097827 | 1.084 | 3.0622 | 9971.6483 | 0.80785 | 4649.5307
75 | E-SOR-NAP-CC-FP-HC-R10 | 12.5 | 0.3 | 572.178 | 0.33264 | 0.50192 | 0.21142 | 0.041465 | #NAME? | 975.375 | 975.375 | 1854.725 | 243.05 | 0 | 16842.4925 | 1471.4025 | 1743.4586 | 4.39 | 70.2992 | 0.0095829 | 1.0125 | 3.0621 | 9935.7923 | 0.81201 | 4510.682
76 | E-SOR-NAP-CC-FP-HC-R600 | 31 | 2.3 | 560.4146 | 0.3258 | 0.4979 | 0.72258 | 0.69605 | #NAME? | 1063.2 | 1063.2 | 2104.7 | 730.25 | 0 | 5184.477 | 1412.2089 | 1892.6671 | 4.5108 | 59.8081 | 0.0086085 | 1.3912 | 3.085 | 7360.7845 | 0.80358 | 4430.696
77 | E-SOR-NAP-CC-FP-HC-R600 | 26.5 | 2 | 604.3534 | 0.35134 | 0.5001 | 0.64807 | 0.63775 | #NAME? | 1070.575 | 1070.575 | 2104.7 | 607.925 | 0 | 6418.1434 | 1438.3806 | 1892.652 | 4.4666 | 57.8676 | 0.0084493 | 1.305 | 3.085 | 7346.669 | 0.80528 | 4368.1867
78 | E-SOR-NAP-CC-FP-HC-R600 | 21.5 | 1.6 | 655.0016 | 0.38079 | 0.50183 | 0.52015 | 0.55306 | #NAME? | 1077.575 | 1077.575 | 2104.7 | 477.25 | 0 | 8447.8069 | 1474.5744 | 1892.6092 | 4.4252 | 55.7846 | 0.0082358 | 1.1908 | 3.0852 | 7323.6088 | 0.79916 | 4524.9068
79 | E-SOR-NAP-CC-FP-HC-R600 | 17 | 1.3 | 711.6781 | 0.41374 | 0.50363 | 0.41177 | 0.46355 | #NAME? | 1083.475 | 1083.475 | 2104.7 | 344.45 | 0 | 10251.8278 | 1505.4454 | 1892.6374 | 4.3931 | 53.371 | 0.008057 | 1.111 | 3.0848 | 7297.3406 | 0.80268 | 4410.2504
80 | E-SOR-NAP-CC-FP-HC-R600 | 12.5 | 0.95 | 782.0517 | 0.45465 | 0.50522 | 0.30527 | 0.35298 | #NAME? | 1089.425 | 1089.425 | 2104.7 | 197.175 | 0 | 12144.7699 | 1540.009 | 1892.6075 | 4.3605 | 50.5252 | 0.0078656 | 1.035 | 3.0854 | 7267.8017 | 0.81562 | 4041.7295
81 | E-SOR-NAP-CC-FP-HC-R600 | 31 | 1.55 | 532.5306 | 0.30959 | 0.49688 | 0.67358 | 0.63968 | #NAME? | 1061.325 | 1061.325 | 2104.7 | 790.15 | 0 | 6123.1265 | 1414.9876 | 1892.6934 | 4.5215 | 59.411 | 0.008592 | 1.3378 | 3.085 | 7360.2601 | 0.80191 | 4483.1142
82 | E-SOR-NAP-CC-FP-HC-R600 | 26.5 | 1.35 | 579.341 | 0.3368 | 0.49915 | 0.60977 | 0.58021 | #NAME? | 1068.05 | 1068.05 | 2104.7 | 671.35 | 0 | 7232.7563 | 1438.8778 | 1892.6503 | 4.4832 | 57.4836 | 0.0084496 | 1.2686 | 3.085 | 7351.2274 | 0.80097 | 4495.0601
83 | E-SOR-NAP-CC-FP-HC-R600 | 21.5 | 1.1 | 636.7004 | 0.37015 | 0.50143 | 0.50629 | 0.50751 | #NAME? | 1075.75 | 1075.75 | 2104.7 | 519.8 | 0 | 8892.0811 | 1472.3815 | 1892.6321 | 4.4389 | 55.4525 | 0.0082546 | 1.1782 | 3.0853 | 7334.1593 | 0.79824 | 4556.0816
84 | E-SOR-NAP-CC-FP-HC-R600 | 17 | 0.85 | 693.0182 | 0.40289 | 0.50308 | 0.39371 | 0.42481 | #NAME? | 1081.85 | 1081.85 | 2104.7 | 390.925 | 0 | 10710.1555 | 1505.5593 | 1892.6283 | 4.4054 | 53.3376 | 0.0080638 | 1.0947 | 3.0851 | 7308.632 | 0.79869 | 4527.6951
85 | E-SOR-NAP-CC-FP-HC-R60 | 12.5 | 0.65 | 764.7087 | 0.44457 | 0.50491 | 0.28491 | 0.32709 | #NAME? | 1088.475 | 1088.475 | 2104.7 | 235.85 | 0 | 12548.5306 | 1539.2486 | 1892.6178 | 4.3746 | 51.0875 | 0.0078724 | 1.0267 | 3.0853 | 7272.721 | 0.80923 | 4217.4971
86 | E-SOR-NAP-CC-FP-HC-R60 | 31 | 0.8 | 490.6891 | 0.28526 | 0.49516 | 0.60411 | 0.5492 | #NAME? | 1058.85 | 1058.85 | 2104.7 | 881.45 | 0 | 7521.9159 | 1421.1763 | 1892.6849 | 4.5343 | 58.2722 | 0.0085561 | 1.258 | 3.0848 | 7360.3656 | 0.79993 | 4548.1746
87 | E-SOR-NAP-CC-FP-HC-R60 | 26.5 | 0.65 | 534.5398 | 0.31076 | 0.49721 | 0.55531 | 0.48568 | #NAME? | 1064.125 | 1064.125 | 2104.7 | 784.45 | 0 | 8467.3848 | 1441.2272 | 1892.683 | 4.5033 | 56.3162 | 0.0084308 | 1.2043 | 3.085 | 7342.841 | 0.80078 | 4508.9125
88 | E-SOR-NAP-CC-FP-HC-R60 | 21.5 | 0.55 | 591.5683 | 0.34391 | 0.50022 | 0.46971 | 0.41619 | #NAME? | 1072.175 | 1072.175 | 2104.7 | 643.65 | 0 | 9878.081 | 1472.8359 | 1892.6474 | 4.4584 | 54.5102 | 0.0082439 | 1.1319 | 3.0852 | 7321.5302 | 0.79826 | 4558.6297
89 | E-SOR-NAP-CC-FP-HC-R60 | 17 | 0.45 | 648.1824 | 0.37682 | 0.502 | 0.35812 | 0.34117 | #NAME? | 1078.45 | 1078.45 | 2104.7 | 504 | 0 | 11634.7058 | 1509.2437 | 1892.6149 | 4.423 | 52.7828 | 0.0080361 | 1.0501 | 3.0849 | 7294.8858 | 0.79335 | 4681.47
90 | E-SOR-NAP-CC-FP-HC-R60 | 12.5 | 0.3 | 685.1505 | 0.39831 | 0.50357 | 0.24908 | 0.16964 | #NAME? | 1084.025 | 1084.025 | 2104.7 | 395.85 | 0 | 13887.5507 | 1543.4468 | 1892.5926 | 4.4009 | 52.1005 | 0.0078306 | 0.97375 | 3.0851 | 7239.0389 | 0.79652 | 4568.4141
91 | E-SOR-NAP-CC-FP-WC-R100 | 43.5 | 3.25 | 484.0549 | 0.28141 | 0.52948 | 0.7225 | 0.53895 | #NAME? | 1138.825 | 1138.825 | 1854.725 | 489.175 | 25.6466 | 9564.0595 | 1019.831 | 2384.7553 | 9.3926 | 77.786 | 0.018889 | 1.381 | 3.0481 | 13776.3667 | 0.86471 | 4142.5309
92 | E-SOR-NAP-CC-FP-WC-R100 | 37 | 2.8 | 518.8462 | 0.30163 | 0.53162 | 0.63988 | 0.48028 | #NAME? | 1144.05 | 1144.05 | 1854.725 | 417.375 | 25.6477 | 11433.1273 | 1033.5357 | 2384.6941 | 9.3475 | 78.7186 | 0.018634 | 1.299 | 3.0474 | 13756.68 | 0.86202 | 4226.3661
93 | E-SOR-NAP-CC-FP-WC-R100 | 30.5 | 2.3 | 556.1516 | 0.32332 | 0.53384 | 0.52908 | 0.40964 | #NAME? | 1149.975 | 1149.975 | 1854.725 | 345.125 | 25.6558 | 13842.1827 | 1053.6972 | 2384.677 | 9.3045 | 79.4631 | 0.018287 | 1.2093 | 3.0475 | 13743.4532 | 0.85501 | 4466.5073
94 | E-SOR-NAP-CC-FP-WC-R100 | 24 | 1.8 | 602.2759 | 0.35013 | 0.53553 | 0.39702 | 0.33093 | #NAME? | 1154.1 | 1154.1 | 1854.725 | 262.975 | 25.6605 | 16638.6481 | 1077.2998 | 2384.6126 | 9.2913 | 80.1357 | 0.01789 | 1.1252 | 3.0472 | 13722.1234 | 0.84506 | 4817.6492
95 | E-SOR-NAP-CC-FP-WC-R100 | 17.5 | 1.3 | 667.596 | 0.38811 | 0.53739 | 0.31158 | 0.24272 | #NAME? | 1158.125 | 1158.125 | 1854.725 | 159 | 25.6577 | 18857.6907 | 1099.4797 | 2384.564 | 9.2282 | 79.4127 | 0.017516 | 1.0615 | 3.0467 | 13684.7261 | 0.85763 | 4348.1745
96 | E-SOR-NAP-CC-FP-WC-R100 | 43.5 | 2.2 | 455.3457 | 0.26472 | 0.52915 | 0.66848 | 0.4871 | #NAME? | 1139.9 | 1139.9 | 1854.725 | 524.375 | 25.6849 | 10977.8553 | 1026.1667 | 2384.7405 | 9.3856 | 79.0981 | 0.018792 | 1.332 | 3.048 | 13789.9317 | 0.86077 | 4286.239
97 | E-SOR-NAP-CC-FP-WC-R100 | 37 | 1.85 | 491.3165 | 0.28563 | 0.53077 | 0.60009 | 0.43706 | #NAME? | 1143.55 | 1143.55 | 1854.725 | 455.175 | 25.6874 | 12544.8039 | 1037.4258 | 2384.6985 | 9.3544 | 79.5904 | 0.018587 | 1.2655 | 3.0478 | 13776.0872 | 0.86075 | 4278.1378
98 | E-SOR-NAP-CC-FP-WC-R100 | 30.5 | 1.55 | 534.5228 | 0.31075 | 0.53287 | 0.50811 | 0.37651 | #NAME? | 1148.125 | 1148.125 | 1854.725 | 378.55 | 25.6726 | 14558.4283 | 1054.0222 | 2384.6712 | 9.324 | 80.2621 | 0.01829 | 1.1942 | 3.0475 | 13752.737 | 0.85449 | 4490.5804
99 | E-SOR-NAP-CC-FP-WC-R100 | 24 | 1.2 | 582.234 | 0.33848 | 0.53488 | 0.38597 | 0.3046 | #NAME? | 1152.6 | 1152.6 | 1854.725 | 290.45 | 25.667 | 17123.7683 | 1077.4035 | 2384.6182 | 9.3047 | 80.7667 | 0.01789 | 1.1153 | 3.0469 | 13725.0694 | 0.8455 | 4804.5746
100 | E-SOR-NAP-CC-FP-WC-R10 | 17.5 | 0.9 | 647.0045 | 0.37614 | 0.53707 | 0.29327 | 0.21566 | #NAME? | 1157.45 | 1157.45 | 1854.725 | 184.4 | 25.6621 | 19448.6693 | 1099.2731 | 2384.5872 | 9.2618 | 81.1122 | 0.01752 | 1.0538 | 3.0465 | 13686.6972 | 0.85148 | 4570.0615
101 | E-SOR-NAP-CC-FP-WC-R10 | 43.5 | 1.1 | 402.9209 | 0.23424 | 0.52847 | 0.58554 | 0.40245 | #NAME? | 1141.15 | 1141.15 | 1854.725 | 598.65 | 25.7417 | 13200.8549 | 1036.486 | 2384.7576 | 9.3719 | 80.349 | 0.018611 | 1.2497 | 3.0481 | 13784.7884 | 0.86276 | 4217.1475
102 | E-SOR-NAP-CC-FP-WC-R10 | 37 | 0.95 | 441.9443 | 0.25693 | 0.52983 | 0.54107 | 0.35767 | #NAME? | 1143.8 | 1143.8 | 1854.725 | 530.7 | 25.7343 | 14356.2347 | 1046.221 | 2384.7242 | 9.3501 | 80.4928 | 0.018431 | 1.2017 | 3.0481 | 13765.1741 | 0.8616 | 4249.8767
103 | E-SOR-NAP-CC-FP-WC-R10 | 30.5 | 0.75 | 480.2348 | 0.27919 | 0.53173 | 0.46919 | 0.29073 | #NAME? | 1147.3 | 1147.3 | 1854.725 | 466.4 | 25.714 | 16152.6219 | 1061.862 | 2384.6924 | 9.3224 | 81.0895 | 0.018147 | 1.1389 | 3.0477 | 13734.6782 | 0.85652 | 4419.2565
104 | E-SOR-NAP-CC-FP-WC-R10 | 24 | 0.6 | 525.0075 | 0.30521 | 0.53397 | 0.36689 | 0.21804 | #NAME? | 1151.375 | 1151.375 | 1854.725 | 375.725 | 25.6911 | 18436.5181 | 1084.1241 | 2384.6369 | 9.3017 | 82.085 | 0.017768 | 1.0698 | 3.0473 | 13703.7662 | 0.84721 | 4742.1554
105 | E-SOR-NAP-CC-FP-WC-R10 | 17.5 | 0.45 | 586.7051 | 0.34108 | 0.53629 | 0.24359 | 0.14172 | #NAME? | 1156.3 | 1156.3 | 1854.725 | 271.4 | 25.6728 | 21032.4999 | 1106.3219 | 2384.5823 | 9.3263 | 84.9484 | 0.017391 | 1.015 | 3.0467 | 13657.8012 | 0.83679 | 5108.5734
106 | E-SOR-NAP-CC-FP-WC-R600 | 43.5 | 3.25 | 477.2265 | 0.27744 | 0.52987 | 0.70672 | 0.67378 | #NAME? | 1282.975 | 1282.975 | 2104.7 | 457.225 | 28.9187 | 7337.75 | 1060.7244 | 2604.2219 | 9.2411 | 68.5472 | 0.015494 | 1.3171 | 3.0723 | 9926.0839 | 0.85869 | 3970.4785
107 | E-SOR-NAP-CC-FP-WC-R600 | 37 | 2.8 | 513.2485 | 0.29838 | 0.53197 | 0.62818 | 0.61694 | #NAME? | 1289.025 | 1289.025 | 2104.7 | 389.6 | 28.9243 | 9027.5765 | 1074.1509 | 2604.1923 | 9.2073 | 68.1959 | 0.015285 | 1.2353 | 3.0721 | 9896.0626 | 0.85801 | 3978.1533
108 | E-SOR-NAP-CC-FP-WC-R600 | 30.5 | 2.3 | 553.2085 | 0.32161 | 0.53397 | 0.52194 | 0.54923 | #NAME? | 1294.625 | 1294.625 | 2104.7 | 315.175 | 28.9322 | 11236.3533 | 1094.4463 | 2604.1565 | 9.175 | 67.3344 | 0.014991 | 1.1453 | 3.0719 | 9866.1161 | 0.85222 | 4153.8623
109 | E-SOR-NAP-CC-FP-WC-R600 | 24 | 1.8 | 604.7687 | 0.35158 | 0.53576 | 0.40144 | 0.46567 | #NAME? | 1299.65 | 1299.65 | 2104.7 | 231.25 | 28.9465 | 13782.5828 | 1119.1049 | 2604.1288 | 9.1598 | 65.8873 | 0.014648 | 1.0588 | 3.0717 | 9829.8331 | 0.84359 | 4425.8962
110 | E-SOR-NAP-CC-FP-WC-R600 | 17.5 | 1.3 | 672.333 | 0.39086 | 0.53765 | 0.30596 | 0.36513 | #NAME? | 1304.625 | 1304.625 | 2104.7 | 130.175 | 28.9591 | 16034.7637 | 1143.1348 | 2604.0853 | 9.1124 | 63.158 | 0.014315 | 0.98972 | 3.0716 | 9780.2822 | 0.85506 | 4029.4671
111 | E-SOR-NAP-CC-FP-WC-R600 | 43.5 | 2.2 | 446.4217 | 0.25953 | 0.52948 | 0.65064 | 0.61814 | #NAME? | 1284 | 1284 | 2104.7 | 504.25 | 28.964 | 8690.6762 | 1068.5662 | 2604.2436 | 9.2376 | 68.0897 | 0.015387 | 1.2555 | 3.072 | 9926.416 | 0.85862 | 3974.07
112 | E-SOR-NAP-CC-FP-WC-R600 | 37 | 1.85 | 484.3002 | 0.28155 | 0.53107 | 0.58673 | 0.5566 | #NAME? | 1288.2 | 1288.2 | 2104.7 | 433.625 | 28.9684 | 10188.8094 | 1079.8477 | 2604.2077 | 9.2218 | 67.462 | 0.015219 | 1.1904 | 3.0723 | 9906.5826 | 0.85653 | 4032.7723
113 | E-SOR-NAP-CC-FP-WC-R600 | 30.5 | 1.55 | 530.8967 | 0.30864 | 0.53314 | 0.50333 | 0.49215 | #NAME? | 1292.975 | 1292.975 | 2104.7 | 352.5 | 28.9566 | 12002.0495 | 1096.6339 | 2604.16 | 9.1954 | 66.7218 | 0.014972 | 1.1211 | 3.0715 | 9877.4751 | 0.85077 | 4207.5359
114 | E-SOR-NAP-CC-FP-WC-R600 | 24 | 1.2 | 583.1874 | 0.33904 | 0.53527 | 0.38734 | 0.42194 | #NAME? | 1298.6 | 1298.6 | 2104.7 | 262.8 | 28.9627 | 14366.3318 | 1121.0145 | 2604.1183 | 9.175 | 65.6548 | 0.014633 | 1.0422 | 3.0717 | 9840.7802 | 0.84246 | 4468.3563
115 | E-SOR-NAP-CC-FP-WC-R60 | 17.5 | 0.9 | 651.7624 | 0.3789 | 0.53731 | 0.28764 | 0.3362 | #NAME? | 1303.875 | 1303.875 | 2104.7 | 157.525 | 28.964 | 16560.4992 | 1144.2573 | 2604.1145 | 9.1408 | 63.5947 | 0.014303 | 0.97865 | 3.0715 | 9782.1099 | 0.85036 | 4184.8332
116 | E-SOR-NAP-CC-FP-WC-R60 | 43.5 | 1.1 | 395.8531 | 0.23013 | 0.52881 | 0.56909 | 0.50595 | #NAME? | 1285.575 | 1285.575 | 2104.7 | 587.375 | 29.0333 | 10906.1626 | 1080.0794 | 2604.2478 | 9.2442 | 66.9849 | 0.015223 | 1.1662 | 3.0721 | 9915.8714 | 0.85844 | 3981.5349
117 | E-SOR-NAP-CC-FP-WC-R60 | 37 | 0.95 | 436.8895 | 0.25399 | 0.53025 | 0.52668 | 0.46346 | #NAME? | 1288.525 | 1288.525 | 2104.7 | 514.7 | 29.0198 | 11898.5348 | 1088.5834 | 2604.2298 | 9.2272 | 66.4417 | 0.015089 | 1.1244 | 3.0719 | 9890.4253 | 0.85802 | 3984.3512
118 | E-SOR-NAP-CC-FP-WC-R60 | 30.5 | 0.75 | 479.0919 | 0.27852 | 0.53212 | 0.4588 | 0.4037 | #NAME? | 1292.325 | 1292.325 | 2104.7 | 447.075 | 28.9999 | 13417.3453 | 1103.983 | 2604.1916 | 9.1988 | 65.5442 | 0.014855 | 1.0648 | 3.0717 | 9850.2152 | 0.8558 | 4041.9407
119 | E-SOR-NAP-CC-FP-WC-R60 | 24 | 0.6 | 528.398 | 0.30719 | 0.53434 | 0.36145 | 0.33242 | #NAME? | 1297.075 | 1297.075 | 2104.7 | 353.8 | 28.9823 | 15478.3788 | 1125.9905 | 2604.1403 | 9.1792 | 64.8151 | 0.014541 | 0.99866 | 3.0719 | 9803.1496 | 0.8481 | 4277.4571
120 | E-SOR-NAP-CC-FP-WC-R60 | 17.5 | 0.45 | 590.1297 | 0.34307 | 0.53662 | 0.24767 | 0.24639 | #NAME? | 1302.625 | 1302.625 | 2104.7 | 252.125 | 28.9688 | 17878.2975 | 1147.9121 | 2604.1047 | 9.1925 | 64.863 | 0.01422 | 0.94557 | 3.0713 | 9733.9255 | 0.84205 | 4454.9434
121 | E-SOR-NAP-FC-ET-WC-OFF0 | 25.5 | 1.9 | 651.5619 | 0.37879 | 0.39466 | 0.84698 | 0.99267 | 1 | 1324.925 | 1324.925 | 2468.675 | 682.475 | 45.6791 | 2020.6404 | 1384.5662 | 2057.2577 | 4.0957 | 88.985 | 0.0041757 | 1.2397 | 2.6717 | 580.9311 | 0.73829 | 4877.0308
122 | E-SOR-NAP-FC-ET-WC-OFF0 | 21.5 | 1.6 | 709.7693 | 0.41263 | 0.39837 | 0.73394 | 0.99096 | 1 | 1344.05 | 1344.05 | 2468.675 | 566.6 | 46.042 | 3478.6397 | 1419.1556 | 2057.2634 | 4.041 | 81.8314 | 0.004074 | 1.1565 | 2.6717 | 580.9311 | 0.7277 | 5102.6311
123 | E-SOR-NAP-FC-ET-WC-OFF0 | 18 | 1.35 | 765.0513 | 0.44476 | 0.40126 | 0.59621 | 0.95517 | 1 | 1361.875 | 1361.875 | 2468.675 | 448.2 | 46.4156 | 5259.5956 | 1455.1212 | 2057.4368 | 4.0015 | 73.7261 | 0.0039734 | 1.0747 | 2.6715 | 580.9311 | 0.7116 | 5488.4463
124 | E-SOR-NAP-FC-ET-WC-OFF0 | 14 | 1.05 | 830.0834 | 0.48257 | 0.4046 | 0.46341 | 0.84067 | 1 | 1380.25 | 1380.25 | 2468.675 | 317.85 | 46.833 | 6989.8335 | 1491.6729 | 2057.9017 | 3.9527 | 64.8004 | 0.0038759 | 1.0017 | 2.6708 | 580.9311 | 0.72187 | 5176.217
125 | E-SOR-NAP-FC-ET-WC-OFF0 | 10 | 0.75 | 899.17 | 0.52274 | 0.40764 | 0.30509 | 0.65578 | 1 | 1395.55 | 1395.55 | 2468.675 | 190.95 | 47.211 | 9065.7899 | 1528.7867 | 2057.7102 | 3.926 | 57.9453 | 0.0037819 | 0.92713 | 2.6711 | 580.9311 | 0.7387 | 4718.4074
126 | E-SOR-NAP-FC-ET-WC-OFF0 | 25.5 | 1.3 | 637.853 | 0.37082 | 0.39393 | 0.82444 | 0.97686 | 1 | 1326.85 | 1326.85 | 2468.675 | 705.25 | 45.7485 | 2331.2201 | 1387.4496 | 2056.9682 | 4.0925 | 87.2048 | 0.0041671 | 1.2179 | 2.6721 | 580.9311 | 0.74116 | 4813.5818
127 | E-SOR-NAP-FC-ET-WC-OFF0 | 21.5 | 1.1 | 696.8067 | 0.40509 | 0.39741 | 0.72449 | 0.95022 | 1 | 1342.225 | 1342.225 | 2468.675 | 592.225 | 46.0497 | 3634.4662 | 1417.9995 | 2057.3274 | 4.0448 | 80.0434 | 0.0040774 | 1.1438 | 2.6716 | 580.9311 | 0.7342 | 4948.0513
128 | E-SOR-NAP-FC-ET-WC-OFF0 | 18 | 0.9 | 748.9103 | 0.43538 | 0.40037 | 0.59739 | 0.87863 | 1 | 1357.55 | 1357.55 | 2468.675 | 481.675 | 46.3586 | 5300.378 | 1451.3251 | 2057.4495 | 4.0072 | 73.1365 | 0.0039838 | 1.0646 | 2.6715 | 580.9311 | 0.7226 | 5209.8326
129 | E-SOR-NAP-FC-ET-WC-OFF0 | 14 | 0.7 | 816.0614 | 0.47442 | 0.40368 | 0.45911 | 0.75197 | 1 | 1375.175 | 1375.175 | 2468.675 | 347.025 | 46.7359 | 7112.6072 | 1489.4102 | 2057.5937 | 3.9615 | 66.0522 | 0.0038819 | 0.98782 | 2.6712 | 580.9311 | 0.72633 | 5073.1154
130 | E-SOR-NAP-FC-ET-WC-OFF | 10 | 0.5 | 886.7079 | 0.51549 | 0.40695 | 0.30519 | 0.53375 | 1 | 1391.625 | 1391.625 | 2468.675 | 215.35 | 47.1281 | 9150.7022 | 1528.7032 | 2057.823 | 3.9292 | 61.9543 | 0.0037822 | 0.91311 | 2.671 | 580.9311 | 0.74155 | 4656.6448
131 | E-SOR-NAP-FC-ET-WC-OFF | 25.5 | 0.65 | 606.4165 | 0.35254 | 0.39273 | 0.78077 | 0.86116 | 1 | 1324.175 | 1324.175 | 2468.675 | 767.1 | 45.7732 | 2983.8085 | 1388.1952 | 2057.1464 | 4.1035 | 79.6013 | 0.0041649 | 1.1705 | 2.6719 | 580.9311 | 0.74935 | 4623.9343
132 | E-SOR-NAP-FC-ET-WC-OFF | 21.5 | 0.55 | 666.501 | 0.38747 | 0.3957 | 0.69968 | 0.79055 | 1 | 1336.675 | 1336.675 | 2468.675 | 659.9 | 45.9827 | 4068.8306 | 1415.961 | 2057.1666 | 4.0579 | 75.241 | 0.0040832 | 1.1068 | 2.6718 | 580.9311 | 0.74593 | 4674.5667
133 | E-SOR-NAP-FC-ET-WC-OFF | 18 | 0.45 | 718.2159 | 0.41754 | 0.39877 | 0.59466 | 0.68485 | 1 | 1348.725 | 1348.725 | 2468.675 | 553.5 | 46.1995 | 5469.3789 | 1446.4634 | 2057.3001 | 4.0191 | 71.7179 | 0.0039971 | 1.0344 | 2.6716 | 580.9311 | 0.74048 | 4774.548
134 | E-SOR-NAP-FC-ET-WC-OFF | 14 | 0.35 | 783.4462 | 0.45546 | 0.40229 | 0.4601 | 0.47961 | 1 | 1366.825 | 1366.825 | 2468.675 | 418.8 | 46.5848 | 7281.9937 | 1488.8075 | 2057.4468 | 3.9662 | 69.5293 | 0.0038834 | 0.95092 | 2.6714 | 580.9311 | 0.74019 | 4741.6524
135 | E-SOR-NAP-FC-ET-WC-OFF | 10 | 0.25 | 835.1162 | 0.4855 | 0.40513 | 0.29979 | -0.15501 | 1 | 1379.125 | 1379.125 | 2468.675 | 294.525 | 46.8618 | 9659.7654 | 1530.1123 | 2057.7407 | 3.9435 | 102.9017 | 0.0037786 | 0.86251 | 2.671 | 580.9311 | 0.745 | 4592.7504
136 | E-SOR-NAP-FC-ET-WC-R100 | 25.5 | 1.9 | 577.9466 | 0.33599 | 0.393 | 0.64249 | 0.59661 | #NAME? | 1061.275 | 1061.275 | 2227.75 | 674.6 | 19.9542 | 6153.9593 | 911.472 | 1575.1571 | 5.7189 | 63.299 | 0.010808 | 1.4844 | 2.7496 | 6718.884 | 0.78938 | 4400.1579
137 | E-SOR-NAP-FC-ET-WC-R100 | 21.5 | 1.6 | 618.4675 | 0.35955 | 0.39479 | 0.55349 | 0.51206 | #NAME? | 1068.425 | 1068.425 | 2227.75 | 567.775 | 19.9868 | 7573.1677 | 939.5893 | 1575.1078 | 5.65 | 61.301 | 0.0105 | 1.3779 | 2.7487 | 6714.5709 | 0.78769 | 4430.9755
138 | E-SOR-NAP-FC-ET-WC-R100 | 18 | 1.35 | 658.1722 | 0.38263 | 0.39634 | 0.46371 | 0.42131 | #NAME? | 1075.175 | 1075.175 | 2227.75 | 467.25 | 20.0256 | 9032.3463 | 965.8549 | 1575.0704 | 5.5994 | 59.9973 | 0.010229 | 1.2926 | 2.7489 | 6711.0149 | 0.78536 | 4481.4687
139 | E-SOR-NAP-FC-ET-WC-R100 | 14 | 1.05 | 711.3155 | 0.41353 | 0.39836 | 0.37501 | 0.31505 | #NAME? | 1083.675 | 1083.675 | 2227.75 | 341.425 | 20.0671 | 10553.5445 | 997.8823 | 1575.2888 | 5.5226 | 57.9895 | 0.0099194 | 1.2053 | 2.7485 | 6709.0922 | 0.79696 | 4164.8221
140 | E-SOR-NAP-FC-ET-WC-R100 | 10 | 0.75 | 783.023 | 0.45521 | 0.39984 | 0.2784 | 0.18708 | #NAME? | 1089.725 | 1089.725 | 2227.75 | 196.825 | 20.1038 | 12278.8776 | 1031.8282 | 1575.1999 | 5.4596 | 57.6801 | 0.0096086 | 1.1263 | 2.748 | 6705.5931 | 0.81087 | 3803.3301
141 | E-SOR-NAP-FC-ET-WC-R100 | 25.5 | 1.3 | 551.6144 | 0.32068 | 0.3922 | 0.60309 | 0.53518 | #NAME? | 1059.675 | 1059.675 | 2227.75 | 734.35 | 19.9803 | 6936.0903 | 916.5716 | 1575.0392 | 5.7325 | 63.1913 | 0.010753 | 1.4314 | 2.7496 | 6720.754 | 0.78621 | 4490.0409
142 | E-SOR-NAP-FC-ET-WC-R100 | 21.5 | 1.1 | 596.7083 | 0.3469 | 0.39426 | 0.52588 | 0.45854 | #NAME? | 1067.15 | 1067.15 | 2227.75 | 617.05 | 20.0022 | 8180.8578 | 941.2328 | 1575.0047 | 5.6713 | 61.761 | 0.010486 | 1.3508 | 2.7492 | 6717.317 | 0.78324 | 4554.0506
143 | E-SOR-NAP-FC-ET-WC-R100 | 18 | 0.9 | 637.2561 | 0.37047 | 0.39574 | 0.44582 | 0.38335 | #NAME? | 1073.15 | 1073.15 | 2227.75 | 516.5 | 20.031 | 9449.0239 | 967.2078 | 1575.1273 | 5.614 | 60.2029 | 0.01022 | 1.2698 | 2.7488 | 6714.7065 | 0.78475 | 4502.9017
144 | E-SOR-NAP-FC-ET-WC-R100 | 14 | 0.7 | 693.919 | 0.40341 | 0.3979 | 0.35559 | 0.28051 | #NAME? | 1081.7 | 1081.7 | 2227.75 | 387.575 | 20.0622 | 10963.9364 | 997.6626 | 1575.2599 | 5.5474 | 58.9887 | 0.0099235 | 1.193 | 2.7479 | 6712.1549 | 0.7911 | 4319.7649
145 | E-SOR-NAP-FC-ET-WC-R10 | 10 | 0.5 | 766.8648 | 0.44582 | 0.39946 | 0.24758 | 0.16239 | #NAME? | 1087.775 | 1087.775 | 2227.75 | 240.675 | 20.0888 | 12753.7657 | 1034.4019 | 1575.2528 | 5.4984 | 58.9855 | 0.0095877 | 1.1099 | 2.7469 | 6708.6973 | 0.79885 | 4108.0282
146 | E-SOR-NAP-FC-ET-WC-R10 | 25.5 | 0.65 | 507.6233 | 0.29511 | 0.39081 | 0.55234 | 0.43152 | #NAME? | 1056.075 | 1056.075 | 2227.75 | 846.575 | 20.0103 | 8086.4637 | 924.1594 | 1575.0053 | 5.752 | 62.5404 | 0.01067 | 1.3501 | 2.7494 | 6719.6823 | 0.7867 | 4485.8635
147 | E-SOR-NAP-FC-ET-WC-R10 | 21.5 | 0.55 | 550.6825 | 0.32014 | 0.39299 | 0.48603 | 0.35623 | #NAME? | 1063.15 | 1063.15 | 2227.75 | 737.2 | 20.018 | 9205.1427 | 948.983 | 1575.1895 | 5.6903 | 61.1883 | 0.010407 | 1.2788 | 2.7491 | 6717.9821 | 0.78353 | 4555.6344
148 | E-SOR-NAP-FC-ET-WC-R10 | 18 | 0.45 | 591.0581 | 0.34361 | 0.39481 | 0.4029 | 0.28029 | #NAME? | 1069.675 | 1069.675 | 2227.75 | 639.675 | 20.0285 | 10506.1188 | 975.3932 | 1575.0232 | 5.6399 | 60.5919 | 0.010141 | 1.2077 | 2.7487 | 6716.5697 | 0.77749 | 4705.0142
149 | E-SOR-NAP-FC-ET-WC-R10 | 14 | 0.35 | 638.9564 | 0.37146 | 0.39669 | 0.31107 | 0.15856 | #NAME? | 1077.05 | 1077.05 | 2227.75 | 507.2 | 20.0612 | 12148.9812 | 1007.9471 | 1575.2543 | 5.585 | 60.779 | 0.0098296 | 1.1307 | 2.748 | 6713.2123 | 0.77699 | 4704.3068
150 | E-SOR-NAP-FC-ET-WC-R10 | 10 | 0.25 | 665.3523 | 0.3868 | 0.39802 | 0.19381 | -0.036172 | #NAME? | 1082.075 | 1082.075 | 2227.75 | 391.4 | 20.0719 | 14476.8048 | 1050.8326 | 1575.2506 | 5.5588 | 66.4502 | 0.0094484 | 1.0275 | 2.7484 | 6708.7675 | 0.77397 | 4776.0388
151 | E-SOR-NAP-FC-ET-WC-R600 | 25.5 | 1.9 | 569.6961 | 0.33119 | 0.39358 | 0.63902 | 0.72696 | #NAME? | 1154.15 | 1154.15 | 2346.175 | 663.225 | 21.8286 | 5271.9907 | 931.7018 | 1665.5739 | 5.6937 | 60.2213 | 0.0090834 | 1.406 | 2.7614 | 4887.2223 | 0.7821 | 4314.1861
152 | E-SOR-NAP-FC-ET-WC-R600 | 21.5 | 1.6 | 612.5385 | 0.3561 | 0.39554 | 0.55661 | 0.65241 | #NAME? | 1163.625 | 1163.625 | 2346.175 | 548.75 | 21.881 | 6494.5416 | 956.3862 | 1665.5518 | 5.6298 | 56.7398 | 0.0088571 | 1.3179 | 2.762 | 4879.4367 | 0.7845 | 4237.5987
153 | E-SOR-NAP-FC-ET-WC-R600 | 18 | 1.35 | 655.1976 | 0.3809 | 0.39714 | 0.46641 | 0.57145 | #NAME? | 1170.8 | 1170.8 | 2346.175 | 440.55 | 21.9214 | 7825.8249 | 980.3159 | 1665.6841 | 5.5854 | 53.9642 | 0.0086478 | 1.2406 | 2.7609 | 4873.7658 | 0.78368 | 4244.1514
154 | E-SOR-NAP-FC-ET-WC-R600 | 14 | 1.05 | 711.3138 | 0.41352 | 0.39894 | 0.36986 | 0.45139 | #NAME? | 1179.55 | 1179.55 | 2346.175 | 306.725 | 21.9844 | 9359.8063 | 1010.3153 | 1665.8282 | 5.5255 | 50.4052 | 0.0083982 | 1.1567 | 2.7605 | 4864.9572 | 0.79295 | 3999.8523
155 | E-SOR-NAP-FC-ET-WC-R600 | 10 | 0.75 | 783.1525 | 0.45529 | 0.40036 | 0.26867 | 0.29733 | #NAME? | 1186.575 | 1186.575 | 2346.175 | 163.55 | 22.0335 | 11067.5328 | 1044.3722 | 1665.7295 | 5.4718 | 47.683 | 0.0081331 | 1.0739 | 2.761 | 4856.0706 | 0.80818 | 3625.1287
156 | E-SOR-NAP-FC-ET-WC-R600 | 25.5 | 1.3 | 544.5148 | 0.31656 | 0.39288 | 0.60334 | 0.66664 | #NAME? | 1153.125 | 1153.125 | 2346.175 | 727.55 | 21.8675 | 5920.2761 | 935.4026 | 1665.5748 | 5.7059 | 58.6807 | 0.0090471 | 1.3577 | 2.7616 | 4884.2626 | 0.78269 | 4303.8705
157 | E-SOR-NAP-FC-ET-WC-R600 | 21.5 | 1.1 | 590.0239 | 0.34301 | 0.39503 | 0.5291 | 0.58668 | #NAME? | 1161.925 | 1161.925 | 2346.175 | 604.7 | 21.9006 | 7061.9354 | 958.9098 | 1665.5169 | 5.6472 | 55.6316 | 0.0088349 | 1.2827 | 2.7612 | 4880.2428 | 0.78176 | 4309.6455
158 | E-SOR-NAP-FC-ET-WC-R600 | 18 | 0.9 | 633.3234 | 0.36818 | 0.39667 | 0.44548 | 0.50309 | #NAME? | 1169.4 | 1169.4 | 2346.175 | 495.425 | 21.941 | 8328.0503 | 983.4491 | 1665.7312 | 5.601 | 53.1744 | 0.0086262 | 1.2095 | 2.7612 | 4877.6111 | 0.78027 | 4334.8279
159 | E-SOR-NAP-FC-ET-WC-R600 | 14 | 0.7 | 692.5263 | 0.4026 | 0.39857 | 0.35619 | 0.39222 | #NAME? | 1178.05 | 1178.05 | 2346.175 | 356.975 | 21.9863 | 9742.8873 | 1012.2495 | 1665.6753 | 5.541 | 50.3398 | 0.0083885 | 1.1364 | 2.7611 | 4870.1785 | 0.78888 | 4103.7574
160 | E-SOR-NAP-FC-ET-WC-R60 | 10 | 0.5 | 766.6968 | 0.44572 | 0.39995 | 0.23782 | 0.2665 | #NAME? | 1184.7 | 1184.7 | 2346.175 | 206.825 | 22.0289 | 11551.4289 | 1048.8036 | 1665.7497 | 5.5088 | 48.2266 | 0.0081064 | 1.0519 | 2.761 | 4862.3532 | 0.79564 | 3927.4215
161 | E-SOR-NAP-FC-ET-WC-R60 | 25.5 | 0.65 | 501.1554 | 0.29135 | 0.39162 | 0.54481 | 0.54035 | #NAME? | 1149.725 | 1149.725 | 2346.175 | 846.525 | 21.9077 | 7088.1345 | 942.4863 | 1665.4949 | 5.7319 | 55.8783 | 0.0089837 | 1.2748 | 2.762 | 4884.0052 | 0.782 | 4331.0644
162 | E-SOR-NAP-FC-ET-WC-R60 | 21.5 | 0.55 | 546.0509 | 0.31745 | 0.39351 | 0.48296 | 0.46599 | #NAME? | 1156.625 | 1156.625 | 2346.175 | 726.325 | 21.9077 | 8065.0461 | 964.6051 | 1665.4746 | 5.6755 | 53.5128 | 0.0087866 | 1.2129 | 2.7616 | 4880.3341 | 0.78162 | 4325.133
163 | E-SOR-NAP-FC-ET-WC-R60 | 18 | 0.45 | 587.9285 | 0.34179 | 0.39541 | 0.40154 | 0.38578 | #NAME? | 1164.725 | 1164.725 | 2346.175 | 619.675 | 21.9485 | 9289.358 | 988.4868 | 1665.7841 | 5.6339 | 52.1182 | 0.0085841 | 1.1516 | 2.7618 | 4875.6673 | 0.77632 | 4444.8956
164 | E-SOR-NAP-FC-ET-WC-R60 | 14 | 0.35 | 640.8806 | 0.37258 | 0.39731 | 0.30899 | 0.25895 | #NAME? | 1172.65 | 1172.65 | 2346.175 | 478.85 | 21.9746 | 10799.5904 | 1019.9572 | 1665.7657 | 5.5826 | 50.283 | 0.0083284 | 1.0777 | 2.7613 | 4869.0188 | 0.77726 | 4403.9285
165 | E-SOR-NAP-FC-ET-WC-R60 | 10 | 0.25 | 670.6431 | 0.38988 | 0.39845 | 0.19085 | 0.014646 | #NAME? | 1177.125 | 1177.125 | 2346.175 | 355.4 | 21.9921 | 13032.7808 | 1061.386 | 1665.5698 | 5.5626 | 51.4569 | 0.0080115 | 0.97507 | 2.7611 | 4857.7113 | 0.77635 | 4414.6117
166 | E-SOR-NAP-FC-FP-WC-OFF0 | 25.5 | 1.9 | 523.3451 | 0.30425 | 0.40205 | 0.64477 | 0.96339 | 1 | 1365.425 | 1365.425 | 2468.675 | 233.875 | 46.4899 | 4616.44 | 1445.7954 | 2057.6201 | 3.9765 | 73.091 | 0.003999 | 1.1038 | 2.6712 | 580.9311 | 0.75253 | 4445.0709
167 | E-SOR-NAP-FC-FP-WC-OFF0 | 21.5 | 1.6 | 555.4398 | 0.32291 | 0.40409 | 0.51012 | 0.90462 | 1 | 1377.975 | 1377.975 | 2468.675 | 182.825 | 46.7847 | 6360.2264 | 1471.2592 | 2057.5763 | 3.9654 | 68.1106 | 0.0039297 | 1.0345 | 2.6713 | 580.9311 | 0.73495 | 4851.0828
168 | E-SOR-NAP-FC-FP-WC-OFF0 | 18 | 1.35 | 585.8606 | 0.34059 | 0.4061 | 0.42302 | 0.82255 | 1 | 1389.175 | 1389.175 | 2468.675 | 135.875 | 47.0504 | 7492.1907 | 1491.1289 | 2057.7074 | 3.9425 | 63.6429 | 0.0038774 | 0.99029 | 2.6711 | 580.9311 | 0.74219 | 4650.2384
169 | E-SOR-NAP-FC-FP-WC-OFF0 | 14 | 1.05 | 622.7901 | 0.36206 | 0.40799 | 0.31679 | 0.70242 | 1 | 1398.575 | 1398.575 | 2468.675 | 90.8 | 47.2619 | 8881.9704 | 1513.8052 | 2057.9711 | 3.9253 | 58.7417 | 0.0038193 | 0.935 | 2.6707 | 580.9311 | 0.75724 | 4272.8433
170 | E-SOR-NAP-FC-FP-WC-OFF0 | 10 | 0.75 | 667.3386 | 0.38796 | 0.40961 | 0.19203 | 0.47852 | 1 | 1405.4 | 1405.4 | 2468.675 | 48.175 | 47.4239 | 10561.3715 | 1535.9521 | 2057.918 | 3.9358 | 58.0286 | 0.0037642 | 0.88091 | 2.6707 | 580.9311 | 0.77039 | 3957.251
171 | E-SOR-NAP-FC-FP-WC-OFF0 | 25.5 | 1.3 | 508.6103 | 0.29568 | 0.40094 | 0.62805 | 0.89843 | 1 | 1362.6 | 1362.6 | 2468.675 | 260.7 | 46.4815 | 4883.6743 | 1444.8206 | 2057.4907 | 3.9822 | 71.7653 | 0.0040016 | 1.0904 | 2.6713 | 580.9311 | 0.75909 | 4300.9596
172 | E-SOR-NAP-FC-FP-WC-OFF0 | 21.5 | 1.1 | 541.0039 | 0.31451 | 0.4034 | 0.51558 | 0.82185 | 1 | 1374.35 | 1374.35 | 2468.675 | 208.325 | 46.723 | 6348.738 | 1468.5616 | 2057.6339 | 3.9646 | 68.0708 | 0.0039369 | 1.0264 | 2.6712 | 580.9311 | 0.74933 | 4507.1974
173 | E-SOR-NAP-FC-FP-WC-OFF0 | 18 | 0.9 | 570.5187 | 0.33167 | 0.40499 | 0.40351 | 0.73468 | 1 | 1383.5 | 1383.5 | 2468.675 | 160.375 | 46.9387 | 7814.8476 | 1491.1236 | 2057.8119 | 3.9565 | 64.8317 | 0.0038777 | 0.96949 | 2.6712 | 580.9311 | 0.7423 | 4660.2166
174 | E-SOR-NAP-FC-FP-WC-OFF0 | 14 | 0.7 | 609.4605 | 0.35431 | 0.40713 | 0.29611 | 0.58007 | 1 | 1393.775 | 1393.775 | 2468.675 | 107.525 | 47.1746 | 9235.5455 | 1512.7033 | 2057.7308 | 3.9448 | 62.5973 | 0.0038221 | 0.92186 | 2.6711 | 580.9311 | 0.75163 | 4412.9579
175 | E-SOR-NAP-FC-FP-WC-OFF | 10 | 0.5 | 654.0065 | 0.38021 | 0.40903 | 0.18212 | 0.3525 | 1 | 1401.975 | 1401.975 | 2468.675 | 62.8 | 47.3593 | 10775.0545 | 1536.9341 | 2057.9838 | 3.9459 | 64.7291 | 0.0037618 | 0.8685 | 2.6707 | 580.9311 | 0.76785 | 4019.6637
176 | E-SOR-NAP-FC-FP-WC-OFF | 25.5 | 0.65 | 472.818 | 0.27487 | 0.39918 | 0.5821 | 0.71106 | 1 | 1356.9 | 1356.9 | 2468.675 | 326.65 | 46.4016 | 5612.5521 | 1446.9586 | 2057.2302 | 3.9928 | 70.3197 | 0.0039958 | 1.0411 | 2.6717 | 580.9311 | 0.77023 | 4059.9007
177 | E-SOR-NAP-FC-FP-WC-OFF | 21.5 | 0.55 | 506.0945 | 0.29422 | 0.40174 | 0.49408 | 0.60133 | 1 | 1366.025 | 1366.025 | 2468.675 | 271.875 | 46.5831 | 6781.0625 | 1466.4085 | 2057.4326 | 3.976 | 69.3363 | 0.0039428 | 0.99161 | 2.6715 | 580.9311 | 0.76585 | 4135.5962
178 | E-SOR-NAP-FC-FP-WC-OFF | 18 | 0.45 | 536.587 | 0.31195 | 0.40357 | 0.38733 | 0.48659 | 1 | 1375.5 | 1375.5 | 2468.675 | 220.225 | 46.7773 | 8194.0291 | 1490.6376 | 2057.3111 | 3.9659 | 69.4495 | 0.0038788 | 0.93673 | 2.6718 | 580.9311 | 0.75442 | 4384.2122
179 | E-SOR-NAP-FC-FP-WC-OFF | 14 | 0.35 | 573.0731 | 0.33316 | 0.40591 | 0.29254 | 0.24287 | 1 | 1386.125 | 1386.125 | 2468.675 | 157.525 | 47.006 | 9505.0521 | 1515.3417 | 2057.8055 | 3.9447 | 75.2649 | 0.0038157 | 0.88492 | 2.6712 | 580.9311 | 0.76418 | 4133.4482
180 | E-SOR-NAP-FC-FP-WC-OFF | 10 | 0.25 | 574.5214 | 0.334 | 0.40765 | 0.16775 | -0.43489 | 1 | 1393.05 | 1393.05 | 2468.675 | 111.15 | 47.1777 | 11452.5746 | 1537.7774 | 2057.6601 | 3.9553 | 267.1963 | 0.0037602 | 0.81044 | 2.6715 | 580.9311 | 0.7757 | 3857.5024
181 | E-SOR-NAP-FC-FP-WC-R100 | 25.5 | 1.9 | 519.3194 | 0.30191 | 0.3942 | 0.5694 | 0.54433 | #NAME? | 1067.3 | 1067.3 | 2227.75 | 371.425 | 19.9953 | 7227.6809 | 931.0038 | 1575.0228 | 5.6495 | 61.4691 | 0.010593 | 1.4064 | 2.7496 | 6715.8793 | 0.80398 | 4012.6803
182 | E-SOR-NAP-FC-FP-WC-R100 | 21.5 | 1.6 | 553.6444 | 0.32186 | 0.3959 | 0.48886 | 0.46805 | #NAME? | 1074.25 | 1074.25 | 2227.75 | 306.5 | 20.0316 | 8505.5527 | 953.9488 | 1575.1553 | 5.599 | 60.0337 | 0.01035 | 1.3218 | 2.7492 | 6711.9545 | 0.80414 | 3997.314
183 | E-SOR-NAP-FC-FP-WC-R100 | 18 | 1.35 | 588.2797 | 0.342 | 0.39718 | 0.40805 | 0.38577 | #NAME? | 1079.425 | 1079.425 | 2227.75 | 247.625 | 20.0539 | 9819.3018 | 975.085 | 1575.1673 | 5.5671 | 59.1822 | 0.010138 | 1.2511 | 2.7487 | 6710.2342 | 0.80245 | 4031.6731
184 | E-SOR-NAP-FC-FP-WC-R100 | 14 | 1.05 | 638.8602 | 0.3714 | 0.39873 | 0.32755 | 0.28944 | #NAME? | 1085.275 | 1085.275 | 2227.75 | 169.525 | 20.0796 | 11197.7752 | 1000.5391 | 1575.3529 | 5.5178 | 57.9348 | 0.0098925 | 1.1791 | 2.7474 | 6708.0284 | 0.81095 | 3807.8499
185 | E-SOR-NAP-FC-FP-WC-R100 | 10 | 0.75 | 706.9394 | 0.41098 | 0.40006 | 0.24779 | 0.16875 | #NAME? | 1091 | 1091 | 2227.75 | 92.725 | 20.1162 | 12704.7996 | 1028.9584 | 1575.2456 | 5.4674 | 58.1055 | 0.009633 | 1.1106 | 2.7482 | 6704.239 | 0.82432 | 3473.9662
186 | E-SOR-NAP-FC-FP-WC-R100 | 25.5 | 1.3 | 492.026 | 0.28604 | 0.39382 | 0.53692 | 0.48206 | #NAME? | 1066.975 | 1066.975 | 2227.75 | 416.75 | 20.0209 | 7934.0217 | 936.1577 | 1574.9922 | 5.6543 | 61.228 | 0.010539 | 1.3651 | 2.7492 | 6717.2445 | 0.80402 | 4013.7768
187 | E-SOR-NAP-FC-FP-WC-R100 | 21.5 | 1.1 | 529.7741 | 0.30799 | 0.3953 | 0.45822 | 0.41175 | #NAME? | 1072.425 | 1072.425 | 2227.75 | 339.75 | 20.0371 | 9160.8449 | 957.8941 | 1575.1941 | 5.6156 | 60.3498 | 0.010312 | 1.2904 | 2.7486 | 6714.4419 | 0.79931 | 4124.2911
188 | E-SOR-NAP-FC-FP-WC-R100 | 18 | 0.9 | 564.8223 | 0.32836 | 0.3967 | 0.3879 | 0.33765 | #NAME? | 1077.8 | 1077.8 | 2227.75 | 276.775 | 20.0638 | 10316.972 | 978.4614 | 1575.2172 | 5.58 | 59.4829 | 0.010109 | 1.226 | 2.7492 | 6713.0863 | 0.80032 | 4090.1939
189 | E-SOR-NAP-FC-FP-WC-R100 | 14 | 0.7 | 614.3979 | 0.35718 | 0.39837 | 0.31366 | 0.24218 | #NAME? | 1084.525 | 1084.525 | 2227.75 | 200.5 | 20.0833 | 11621.5754 | 1003.6448 | 1575.1992 | 5.5275 | 58.6764 | 0.0098667 | 1.1596 | 2.7486 | 6709.9789 | 0.80836 | 3875.5984
190 | E-SOR-NAP-FC-FP-WC-R10 | 10 | 0.5 | 685.7878 | 0.39868 | 0.39972 | 0.2103 | 0.13922 | #NAME? | 1089.525 | 1089.525 | 2227.75 | 127.8 | 20.1025 | 13279.7941 | 1032.6991 | 1575.1815 | 5.5153 | 59.8185 | 0.0096025 | 1.093 | 2.7484 | 6706.7862 | 0.80997 | 3826.8136
191 | E-SOR-NAP-FC-FP-WC-R10 | 25.5 | 0.65 | 439.7229 | 0.25563 | 0.39275 | 0.4756 | 0.35586 | #NAME? | 1064.925 | 1064.925 | 2227.75 | 505.575 | 20.0501 | 9322.9564 | 950.091 | 1574.9107 | 5.6594 | 60.5352 | 0.010395 | 1.2716 | 2.7494 | 6717.5441 | 0.80318 | 4041.9707
192 | E-SOR-NAP-FC-FP-WC-R10 | 21.5 | 0.55 | 475.0625 | 0.27618 | 0.39445 | 0.41721 | 0.28275 | #NAME? | 1070.05 | 1070.05 | 2227.75 | 432 | 20.0481 | 10342.9082 | 968.8135 | 1574.9933 | 5.6236 | 60.097 | 0.010205 | 1.2159 | 2.7493 | 6715.4631 | 0.80021 | 4106.9761
193 | E-SOR-NAP-FC-FP-WC-R10 | 18 | 0.45 | 510.5417 | 0.2968 | 0.3959 | 0.33387 | 0.22083 | #NAME? | 1075.5 | 1075.5 | 2227.75 | 371.35 | 20.0673 | 11569.5467 | 989.5557 | 1575.1224 | 5.6055 | 60.6453 | 0.010003 | 1.1624 | 2.7497 | 6713.3863 | 0.7907 | 4344.9107
194 | E-SOR-NAP-FC-FP-WC-R10 | 14 | 0.35 | 544.3411 | 0.31645 | 0.39742 | 0.25409 | 0.10751 | #NAME? | 1081.025 | 1081.025 | 2227.75 | 294.375 | 20.0859 | 13035.461 | 1015.2432 | 1575.2287 | 5.5724 | 61.7957 | 0.0097613 | 1.0955 | 2.7489 | 6709.9913 | 0.79258 | 4284.5076
195 | E-SOR-NAP-FC-FP-WC-R10 | 10 | 0.25 | 525.0603 | 0.30525 | 0.3987 | 0.14431 | -0.092871 | #NAME? | 1085.225 | 1085.225 | 2227.75 | 231.65 | 20.0917 | 15306.032 | 1039.9392 | 1575.3291 | 5.5877 | 71.4086 | 0.0095369 | 1.0015 | 2.7474 | 6704.8207 | 0.79444 | 4225.6403
196 | E-SOR-NAP-FC-FP-WC-R600 | 25.5 | 1.9 | 508.9734 | 0.29589 | 0.3946 | 0.56787 | 0.67322 | #NAME? | 1161.325 | 1161.325 | 2346.175 | 355.6 | 21.8998 | 6297.9242 | 947.245 | 1665.5647 | 5.6373 | 57.3753 | 0.0089385 | 1.3354 | 2.7622 | 4880.5995 | 0.80167 | 3823.1586
197 | E-SOR-NAP-FC-FP-WC-R600 | 21.5 | 1.6 | 546.3194 | 0.3176 | 0.3964 | 0.48973 | 0.59825 | #NAME? | 1168.8 | 1168.8 | 2346.175 | 292.625 | 21.9254 | 7466.4594 | 966.8763 | 1665.724 | 5.5982 | 54.8399 | 0.0087621 | 1.2635 | 2.7616 | 4874.3443 | 0.80148 | 3813.9745
198 | E-SOR-NAP-FC-FP-WC-R600 | 18 | 1.35 | 584.1306 | 0.33959 | 0.39775 | 0.41481 | 0.51597 | #NAME? | 1174.625 | 1174.625 | 2346.175 | 229.25 | 21.9677 | 8622.3617 | 986.6909 | 1665.748 | 5.5655 | 52.4592 | 0.0085915 | 1.1968 | 2.7612 | 4869.0351 | 0.80244 | 3780.6396
199 | E-SOR-NAP-FC-FP-WC-R600 | 14 | 1.05 | 639.0064 | 0.37149 | 0.39915 | 0.32981 | 0.41133 | #NAME? | 1181.5 | 1181.5 | 2346.175 | 151.05 | 22.009 | 9970.0497 | 1011.6332 | 1665.9222 | 5.5238 | 49.7953 | 0.008386 | 1.1265 | 2.7612 | 4861.379 | 0.80952 | 3603.0853
200 | E-SOR-NAP-FC-FP-WC-R600 | 10 | 0.75 | 709.6808 | 0.41258 | 0.40041 | 0.24698 | 0.27155 | #NAME? | 1187.3 | 1187.3 | 2346.175 | 75.15 | 22.0474 | 11411.0569 | 1039.5367 | 1665.724 | 5.4766 | 47.6323 | 0.0081659 | 1.0565 | 2.7615 | 4852.3061 | 0.82509 | 3237.2014
201 | E-SOR-NAP-FC-FP-WC-R600 | 25.5 | 1.3 | 482.4887 | 0.2805 | 0.39407 | 0.53017 | 0.60172 | #NAME? | 1159.825 | 1159.825 | 2346.175 | 406.225 | 21.9209 | 7007.7772 | 952.3137 | 1665.6118 | 5.6484 | 55.8374 | 0.0088923 | 1.2886 | 2.7615 | 4879.6711 | 0.80082 | 3846.3528
202 | E-SOR-NAP-FC-FP-WC-R600 | 21.5 | 1.1 | 522.7598 | 0.30391 | 0.39583 | 0.46647 | 0.52395 | #NAME? | 1166.95 | 1166.95 | 2346.175 | 327.7 | 21.9439 | 8017.8881 | 971.2758 | 1665.7613 | 5.6083 | 53.5412 | 0.0087276 | 1.2271 | 2.7616 | 4877.0613 | 0.80055 | 3840.9067
203 | E-SOR-NAP-FC-FP-WC-R600 | 18 | 0.9 | 561.1191 | 0.32621 | 0.39718 | 0.39296 | 0.44549 | #NAME? | 1172.55 | 1172.55 | 2346.175 | 261.85 | 21.9788 | 9143.9723 | 990.7888 | 1665.7071 | 5.5792 | 51.8055 | 0.0085615 | 1.1669 | 2.7613 | 4872.4393 | 0.79894 | 3869.2964
204 | E-SOR-NAP-FC-FP-WC-R600 | 14 | 0.7 | 613.8219 | 0.35685 | 0.39882 | 0.31216 | 0.34108 | #NAME? | 1180.3 | 1180.3 | 2346.175 | 185.775 | 22.0106 | 10437.7149 | 1014.5487 | 1665.6653 | 5.5386 | 49.8747 | 0.0083669 | 1.1041 | 2.7619 | 4864.9955 | 0.80529 | 3705.5213
205 | E-SOR-NAP-FC-FP-WC-R60 | 10 | 0.5 | 688.0996 | 0.40003 | 0.40007 | 0.2112 | 0.2364 | #NAME? | 1185.625 | 1185.625 | 2346.175 | 109.825 | 22.0413 | 11964.408 | 1044.0229 | 1665.8412 | 5.5206 | 48.4197 | 0.0081362 | 1.0363 | 2.761 | 4856.425 | 0.81094 | 3562.9898
206 | E-SOR-NAP-FC-FP-WC-R60 | 25.5 | 0.65 | 433.6202 | 0.25209 | 0.39321 | 0.47036 | 0.4503 | #NAME? | 1158.375 | 1158.375 | 2346.175 | 498.775 | 21.9583 | 8275.4914 | 964.222 | 1665.4976 | 5.6565 | 52.9335 | 0.0087887 | 1.2022 | 2.7621 | 4878.3707 | 0.80113 | 3844.7606
207 | E-SOR-NAP-FC-FP-WC-R60 | 21.5 | 0.55 | 471.8155 | 0.27429 | 0.39483 | 0.41598 | 0.37758 | #NAME? | 1163.775 | 1163.775 | 2346.175 | 425.375 | 21.9566 | 9154.9648 | 980.8253 | 1665.5636 | 5.623 | 51.5553 | 0.0086447 | 1.154 | 2.7616 | 4874.1723 | 0.79998 | 3860.1559
208 | E-SOR-NAP-FC-FP-WC-R60 | 18 | 0.45 | 508.8001 | 0.29579 | 0.39621 | 0.33783 | 0.32086 | #NAME? | 1169.125 | 1169.125 | 2346.175 | 359.325 | 21.9734 | 10256.8728 | 999.0888 | 1665.7093 | 5.6077 | 51.1618 | 0.0084922 | 1.107 | 2.7613 | 4869.7019 | 0.79306 | 4017.8208
209 | E-SOR-NAP-FC-FP-WC-R60 | 14 | 0.35 | 548.1136 | 0.31865 | 0.3978 | 0.25654 | 0.19534 | #NAME? | 1175.6 | 1175.6 | 2346.175 | 275.8 | 21.9959 | 11629.722 | 1024.0228 | 1665.5772 | 5.5778 | 50.2563 | 0.0082901 | 1.0428 | 2.7615 | 4861.4566 | 0.79504 | 3956.3932
210 | E-SOR-NAP-FC-FP-WC-R60 | 10 | 0.25 | 531.6127 | 0.30905 | 0.39899 | 0.14714 | -0.064314 | #NAME? | 1180.425 | 1180.425 | 2346.175 | 213.8 | 22.0158 | 13807.6233 | 1047.1798 | 1665.7167 | 5.5945 | 54.2397 | 0.0081053 | 0.94999 | 2.761 | 4848.1445 | 0.80012 | 3822.5293
211 | E-SOR-STR-FC-ET-HC-OFF0 | 13 | 1 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
212 | E-SOR-STR-FC-ET-HC-OFF0 | 11 | 0.85 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
213 | E-SOR-STR-FC-ET-HC-OFF0 | 9 | 0.7 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
214 | E-SOR-STR-FC-ET-HC-OFF0 | 7 | 0.55 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
215 | E-SOR-STR-FC-ET-HC-OFF0 | 5 | 0.4 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
216 | E-SOR-STR-FC-ET-HC-OFF0 | 13 | 0.65 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
217 | E-SOR-STR-FC-ET-HC-OFF0 | 11 | 0.55 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
218 | E-SOR-STR-FC-ET-HC-OFF0 | 9 | 0.45 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
219 | E-SOR-STR-FC-ET-HC-OFF0 | 7 | 0.35 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
220 | E-SOR-STR-FC-ET-HC-OFF | 5 | 0.25 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
221 | E-SOR-STR-FC-ET-HC-OFF | 13 | 0.35 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
222 | E-SOR-STR-FC-ET-HC-OFF | 11 | 0.3 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
223 | E-SOR-STR-FC-ET-HC-OFF | 7 | 0.2 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
224 | E-SOR-STR-FC-ET-WC-OFF0 | 25.5 | 1.9 | 388.4186 | 0.33767 | 0.35336 | 0.6197 | 0.44407 | 1 | 840.975 | 840.975 | 1446.5 | 322.475 | 12.3918 | 5918.1965 | 783.4763 | 1155.9784 | 5.1891 | 54.236 | 0.010397 | 1.3226 | 2.7561 | 5474.3465 | 0.82374 | 2788.9769
225 | E-SOR-STR-FC-ET-WC-OFF0 | 21.5 | 1.6 | 409.2381 | 0.35577 | 0.35543 | 0.52275 | 0.40906 | 1 | 844.95 | 844.95 | 1446.5 | 264.075 | 12.3576 | 6822.8837 | 799.8509 | 1156.0402 | 5.1287 | 54.4366 | 0.010185 | 1.2645 | 2.7567 | 5474.3465 | 0.83168 | 2629.3521
226 | E-SOR-STR-FC-ET-WC-OFF0 | 18 | 1.35 | 428.9788 | 0.37293 | 0.35757 | 0.43486 | 0.3758 | 1 | 847.15 | 847.15 | 1446.5 | 209.125 | 12.2996 | 7633.6164 | 815.316 | 1156.018 | 5.0778 | 53.7941 | 0.0099866 | 1.2132 | 2.7525 | 5474.3465 | 0.84241 | 2419.7703
227 | E-SOR-STR-FC-ET-WC-OFF0 | 14 | 1.05 | 454.4837 | 0.3951 | 0.35991 | 0.32375 | 0.33372 | 1 | 850.85 | 850.85 | 1446.5 | 145.35 | 12.257 | 8661.4093 | 835.7891 | 1156.0376 | 5.0338 | 52.3731 | 0.0097427 | 1.1546 | 2.7531 | 5474.3465 | 0.85786 | 2135.5298
228 | E-SOR-STR-FC-ET-WC-OFF0 | 10 | 0.75 | 485.4476 | 0.42202 | 0.36215 | 0.20915 | 0.29277 | 1 | 852.575 | 852.575 | 1446.5 | 78.65 | 12.1934 | 9689.2324 | 857.5124 | 1155.9014 | 5.0048 | 49.3892 | 0.0094906 | 1.097 | 2.7488 | 5474.3465 | 0.8822 | 1713.2087
229 | E-SOR-STR-FC-ET-WC-OFF0 | 25.5 | 1.3 | 379.7095 | 0.3301 | 0.3526 | 0.59541 | 0.43986 | 1 | 840.225 | 840.225 | 1446.5 | 339.6 | 12.4118 | 6132.0297 | 785.8661 | 1156.0822 | 5.1834 | 54.5802 | 0.010366 | 1.3065 | 2.7562 | 5474.3465 | 0.82527 | 2763.2688
230 | E-SOR-STR-FC-ET-WC-OFF0 | 21.5 | 1.1 | 400.7891 | 0.34842 | 0.35464 | 0.50315 | 0.39711 | 1 | 843.7 | 843.7 | 1446.5 | 279.8 | 12.3732 | 7043.3398 | 802.5666 | 1155.9196 | 5.13 | 54.6169 | 0.01015 | 1.2492 | 2.7566 | 5474.3465 | 0.83061 | 2652.6396
231 | E-SOR-STR-FC-ET-WC-OFF0 | 18 | 0.9 | 420.1924 | 0.36529 | 0.35678 | 0.41908 | 0.3599 | 1 | 846.1 | 846.1 | 1446.5 | 227.4 | 12.3199 | 7848.998 | 817.848 | 1156.1299 | 5.0839 | 54.0014 | 0.0099564 | 1.2 | 2.7528 | 5474.3465 | 0.84046 | 2458.9009
232 | E-SOR-STR-FC-ET-WC-OFF0 | 14 | 0.7 | 445.7776 | 0.38753 | 0.35939 | 0.31464 | 0.31213 | 1 | 849.4 | 849.4 | 1446.5 | 164.375 | 12.2618 | 8851.2407 | 839.0104 | 1156.042 | 5.038 | 52.5809 | 0.0097032 | 1.1407 | 2.7513 | 5474.3465 | 0.8544 | 2197.4871
233 | E-SOR-STR-FC-ET-WC-OFF | 10 | 0.5 | 480.3109 | 0.41756 | 0.36176 | 0.19811 | 0.29831 | 1 | 851.9 | 851.9 | 1446.5 | 94.45 | 12.2013 | 9745.8025 | 859.1967 | 1155.8603 | 5.0096 | 49.0982 | 0.0094718 | 1.0903 | 2.7487 | 5474.3465 | 0.88238 | 1711.2758
234 | E-SOR-STR-FC-ET-WC-OFF | 25.5 | 0.65 | 358.8169 | 0.31194 | 0.35109 | 0.54966 | 0.39706 | 1 | 839.675 | 839.675 | 1446.5 | 389.9 | 12.4684 | 6732.0573 | 793.7669 | 1156.2078 | 5.1817 | 55.0306 | 0.010267 | 1.2642 | 2.7595 | 5474.3465 | 0.82445 | 2788.0012
235 | E-SOR-STR-FC-ET-WC-OFF | 21.5 | 0.55 | 380.2787 | 0.33059 | 0.35313 | 0.46956 | 0.34282 | 1 | 842.075 | 842.075 | 1446.5 | 327.1 | 12.4167 | 7612.1126 | 810.0382 | 1156.1583 | 5.1383 | 54.9796 | 0.010057 | 1.2121 | 2.757 | 5474.3465 | 0.8261 | 2745.6217
236 | E-SOR-STR-FC-ET-WC-OFF | 18 | 0.45 | 402.6802 | 0.35007 | 0.35555 | 0.39355 | 0.36888 | 1 | 844.875 | 844.875 | 1446.5 | 273.3 | 12.3612 | 8009.1523 | 826.3006 | 1155.9944 | 5.0595 | 52.965 | 0.0098564 | 1.1659 | 2.7548 | 5474.3465 | 0.85099 | 2273.4351
237 | E-SOR-STR-FC-ET-WC-OFF | 14 | 0.35 | 427.9075 | 0.372 | 0.35832 | 0.3016 | 0.31739 | 1 | 847.675 | 847.675 | 1446.5 | 203.225 | 12.2927 | 8933.5897 | 847.5532 | 1156.077 | 5.0098 | 51.2265 | 0.0096048 | 1.1106 | 2.7506 | 5474.3465 | 0.86538 | 2009.043
238 | E-SOR-STR-FC-ET-WC-OFF | 10 | 0.25 | 438.6838 | 0.38137 | 0.36032 | 0.15678 | 0.10159 | 1 | 849.725 | 849.725 | 1446.5 | 131.475 | 12.2412 | 11150.0144 | 874.5337 | 1156.0817 | 5.099 | 57.3069 | 0.0093048 | 1.0392 | 2.7473 | 5474.3465 | 0.82802 | 2672.0231
239 | E-SOR-STR-FC-FP-HC-OFF0 | 13 | 1 | 331.6089 | 0.28828 | 0.38102 | 0.34322 | 0.07404 | 1 | 460.825 | 460.825 | 1446.5 | 39.15 | 0 | 5004.9968 | 813.9481 | 668.7113 | 2.4723 | 44.6937 | 0.0051515 | 1.4384 | 2.9193 | 2786.0994 | 0.69543 | 2837.3019
240 | E-SOR-STR-FC-FP-HC-OFF0 | 11 | 0.85 | 347.3011 | 0.30192 | 0.38196 | 0.25894 | 0.023956 | 1 | 462.875 | 462.875 | 1446.5 | 25.425 | 0 | 5449.4729 | 825.662 | 668.7865 | 2.466 | 46.5997 | 0.0050787 | 1.3984 | 2.9193 | 2786.0994 | 0.69798 | 2799.6227
241 | E-SOR-STR-FC-FP-HC-OFF0 | 9 | 0.7 | 361.8189 | 0.31455 | 0.38265 | 0.16737 | -0.049227 | 1 | 464.5 | 464.5 | 1446.5 | 14.8 | 0 | 5984.041 | 839.4545 | 668.7555 | 2.467 | 50.2228 | 0.0049946 | 1.3498 | 2.9184 | 2786.0994 | 0.69933 | 2778.2754
242 | E-SOR-STR-FC-FP-HC-OFF0 | 7 | 0.55 | 379.9071 | 0.33027 | 0.38316 | 0.061769 | -0.12169 | 1 | 465.475 | 465.475 | 1446.5 | 5.8 | 0 | 6569.4768 | 854.0352 | 668.875 | 2.4876 | 57.5482 | 0.0049093 | 1.3007 | 2.9176 | 2786.0994 | 0.69968 | 2771.6171
243 | E-SOR-STR-FC-FP-HC-OFF0 | 5 | 0.4 | 408.4164 | 0.35505 | 0.38325 | -0.057507 | -0.1707 | 1 | 465.525 | 465.525 | 1446.5 | 0 | 0 | 7141.8563 | 866.5883 | 668.7971 | 2.5499 | 73.9065 | 0.0048377 | 1.2612 | 2.9173 | 2786.0994 | 0.70289 | 2728.6838
244 | E-SOR-STR-FC-FP-HC-OFF0 | 13 | 0.65 | 316.9565 | 0.27554 | 0.37999 | 0.30875 | 0.016912 | 1 | 458.05 | 458.05 | 1446.5 | 53.475 | 0 | 5297.0592 | 818.5655 | 668.6268 | 2.4849 | 45.5911 | 0.0051215 | 1.3999 | 2.9183 | 2786.0994 | 0.6888 | 2930.7423
245 | E-SOR-STR-FC-FP-HC-OFF0 | 11 | 0.55 | 329.8261 | 0.28673 | 0.38103 | 0.22877 | -0.04486 | 1 | 460.45 | 460.45 | 1446.5 | 40 | 0 | 5757.3436 | 832.3205 | 668.7973 | 2.4766 | 47.9713 | 0.0050369 | 1.3549 | 2.9173 | 2786.0994 | 0.69008 | 2908.7784
246 | E-SOR-STR-FC-FP-HC-OFF0 | 9 | 0.45 | 355.6714 | 0.3092 | 0.38175 | 0.13376 | -0.064903 | 1 | 462 | 462 | 1446.5 | 26.4 | 0 | 6159.0363 | 843.5049 | 668.858 | 2.484 | 51.0614 | 0.0049708 | 1.3287 | 2.918 | 2786.0994 | 0.69135 | 2888.959
247 | E-SOR-STR-FC-FP-HC-OFF0 | 7 | 0.35 | 365.2802 | 0.31755 | 0.38225 | 0.023366 | -0.15811 | 1 | 463.225 | 463.225 | 1446.5 | 13.25 | 0 | 6821.5429 | 858.5169 | 668.6802 | 2.5119 | 61.1307 | 0.0048841 | 1.2741 | 2.9196 | 2786.0994 | 0.68956 | 2911.4746
248 | E-SOR-STR-FC-FP-HC-OFF | 5 | 0.25 | 311.1283 | 0.27048 | 0.38252 | -0.11181 | -0.36327 | 1 | 463.775 | 463.775 | 1446.5 | 2 | 0 | 7887.8019 | 868.1645 | 668.6666 | 2.5937 | 148.0286 | 0.0048299 | 1.1841 | 2.9198 | 2786.0994 | 0.68454 | 2979.0093
249 | E-SOR-STR-FC-FP-HC-OFF | 13 | 0.35 | 288.2747 | 0.25061 | 0.37853 | 0.23237 | -0.07357 | 1 | 455.2 | 455.2 | 1446.5 | 86.15 | 0 | 5844.2899 | 828.9472 | 668.7619 | 2.5041 | 47.9208 | 0.0050583 | 1.3375 | 2.9191 | 2786.0994 | 0.67797 | 3088.8552
250 | E-SOR-STR-FC-FP-HC-OFF | 11 | 0.3 | 297.3728 | 0.25852 | 0.37966 | 0.15659 | -0.15567 | 1 | 457.35 | 457.35 | 1446.5 | 69.6 | 0 | 6345.0632 | 842.7613 | 668.673 | 2.5024 | 52.372 | 0.0049752 | 1.2937 | 2.9192 | 2786.0994 | 0.67507 | 3124.5855
251 | E-SOR-STR-FC-FP-HC-OFF | 7 | 0.2 | 349.7497 | 0.30405 | 0.38033 | 0.053841 | -0.30561 | 1 | 459.2 | 459.2 | 1446.5 | 54.85 | 0 | 7137.6218 | 851.5671 | 668.8018 | 2.5193 | 64.5975 | 0.0049239 | 1.2248 | 2.9187 | 2786.0994 | 0.67655 | 3100.5361
252 | E-SOR-STR-FC-FP-WC-OFF0 | 25.5 | 1.9 | 290.9043 | 0.2529 | 0.40235 | 0.48677 | 0.40593 | 1 | 744.15 | 744.15 | 1446.5 | 103.975 | 18.9231 | 6776.8933 | 768.8684 | 1157.3821 | 5.5413 | 53.4374 | 0.010714 | 1.2559 | 2.847 | 5474.3465 | 0.86948 | 1852.7367
253 | E-SOR-STR-FC-FP-WC-OFF0 | 21.5 | 1.6 | 306.2306 | 0.26622 | 0.40356 | 0.40416 | 0.3751 | 1 | 748.525 | 748.525 | 1446.5 | 82.85 | 19.0018 | 7501.0593 | 781.7544 | 1157.3577 | 5.4956 | 53.2357 | 0.010538 | 1.2148 | 2.8472 | 5474.3465 | 0.87483 | 1762.9763
254 | E-SOR-STR-FC-FP-WC-OFF0 | 18 | 1.35 | 320.762 | 0.27885 | 0.40464 | 0.33651 | 0.35442 | 1 | 751.975 | 751.975 | 1446.5 | 60.525 | 19.0692 | 8065.3084 | 794.6044 | 1157.3152 | 5.4478 | 52.0417 | 0.010367 | 1.1758 | 2.8473 | 5474.3465 | 0.88905 | 1535.4055
255 | E-SOR-STR-FC-FP-WC-OFF0 | 14 | 1.05 | 340.0838 | 0.29565 | 0.40571 | 0.25248 | 0.31341 | 1 | 755.35 | 755.35 | 1446.5 | 36.375 | 19.1246 | 8850.372 | 810.7503 | 1157.3273 | 5.4117 | 50.4291 | 0.010161 | 1.1309 | 2.8473 | 5474.3465 | 0.90261 | 1325.6432
256 | E-SOR-STR-FC-FP-WC-OFF0 | 10 | 0.75 | 365.418 | 0.31767 | 0.40666 | 0.16746 | 0.27592 | 1 | 758 | 758 | 1446.5 | 16.2 | 19.1706 | 9621.4356 | 828.4422 | 1157.3933 | 5.385 | 47.4757 | 0.0099438 | 1.0864 | 2.8471 | 5474.3465 | 0.92424 | 1005.7185
257 | E-SOR-STR-FC-FP-WC-OFF0 | 25.5 | 1.3 | 280.8371 | 0.24414 | 0.40148 | 0.45953 | 0.38744 | 1 | 742.075 | 742.075 | 1446.5 | 116.325 | 18.8915 | 7073.492 | 772.2799 | 1157.3132 | 5.5467 | 53.5712 | 0.010667 | 1.2377 | 2.8473 | 5474.3465 | 0.86812 | 1877.2971
258 | E-SOR-STR-FC-FP-WC-OFF0 | 21.5 | 1.1 | 295.5165 | 0.25691 | 0.40288 | 0.38641 | 0.35516 | 1 | 746.25 | 746.25 | 1446.5 | 95.55 | 18.9632 | 7738.499 | 785.149 | 1157.3542 | 5.5017 | 53.1309 | 0.010492 | 1.1968 | 2.847 | 5474.3465 | 0.87518 | 1759.0275
259 | E-SOR-STR-FC-FP-WC-OFF0 | 18 | 0.9 | 308.9417 | 0.26858 | 0.40405 | 0.32277 | 0.32244 | 1 | 749.7 | 749.7 | 1446.5 | 71.2 | 19.0248 | 8340.6599 | 797.6536 | 1157.4347 | 5.4617 | 52.2534 | 0.010327 | 1.1596 | 2.8467 | 5474.3465 | 0.88574 | 1588.4505
260 | E-SOR-STR-FC-FP-WC-OFF0 | 14 | 0.7 | 327.6248 | 0.28482 | 0.40524 | 0.23685 | 0.28667 | 1 | 753.8 | 753.8 | 1446.5 | 46.675 | 19.0978 | 9109.5908 | 814.7553 | 1157.4319 | 5.4246 | 50.7145 | 0.010111 | 1.1151 | 2.8472 | 5474.3465 | 0.89763 | 1402.0853
261 | E-SOR-STR-FC-FP-WC-OFF | 10 | 0.5 | 360.5565 | 0.31345 | 0.40628 | 0.14993 | 0.27944 | 1 | 756.475 | 756.475 | 1446.5 | 24.925 | 19.1427 | 9726.6752 | 831.7674 | 1157.3965 | 5.4017 | 47.1012 | 0.009904 | 1.077 | 2.8471 | 5474.3465 | 0.92079 | 1055.9997
262 | E-SOR-STR-FC-FP-WC-OFF | 25.5 | 0.65 | 254.4547 | 0.22121 | 0.40017 | 0.4088 | 0.33399 | 1 | 738.2 | 738.2 | 1446.5 | 153.475 | 18.8375 | 7728.6154 | 783.1039 | 1157.2592 | 5.5458 | 53.1989 | 0.010519 | 1.1874 | 2.8475 | 5474.3465 | 0.87077 | 1837.2222
263 | E-SOR-STR-FC-FP-WC-OFF | 21.5 | 0.55 | 268.1486 | 0.23311 | 0.40173 | 0.34774 | 0.23868 | 1 | 742.2 | 742.2 | 1446.5 | 126.025 | 18.8948 | 8654.4434 | 795.7192 | 1157.3099 | 5.5412 | 54.4081 | 0.010353 | 1.1504 | 2.8473 | 5474.3465 | 0.85668 | 2066.5506
264 | E-SOR-STR-FC-FP-WC-OFF | 18 | 0.45 | 287.595 | 0.25002 | 0.40287 | 0.28585 | 0.32376 | 1 | 745.775 | 745.775 | 1446.5 | 100.275 | 18.9632 | 8600.5858 | 807.535 | 1157.4175 | 5.4481 | 50.8655 | 0.010201 | 1.1239 | 2.847 | 5474.3465 | 0.89522 | 1443.5615
265 | E-SOR-STR-FC-FP-WC-OFF | 14 | 0.35 | 301.0651 | 0.26173 | 0.40425 | 0.20104 | 0.27331 | 1 | 749.825 | 749.825 | 1446.5 | 73 | 19.0342 | 9439.9838 | 823.689 | 1157.535 | 5.4316 | 49.8182 | 0.010001 | 1.0805 | 2.8467 | 5474.3465 | 0.90154 | 1344.4136
266 | E-SOR-STR-FC-FP-WC-OFF | 10 | 0.25 | 277.668 | 0.24139 | 0.40534 | 0.11668 | 0.11666 | 1 | 752.875 | 752.875 | 1446.5 | 49.35 | 19.0915 | 10858.0684 | 837.1278 | 1157.3538 | 5.4709 | 53.0535 | 0.0098407 | 1.0158 | 2.8473 | 5474.3465 | 0.90154 | 1342.4792
267 | E-SOR-TOU-CC-ET-HC-R100 | 31 | 2.3 | 457.2793 | 0.30847 | 0.49213 | 0.79318 | 0.30915 | #NAME? | 354.675 | 354.675 | 850.5 | 658.825 | 0 | 13810.8889 | 807.4746 | 788.5974 | 4.5482 | 81.776 | 0.02471 | 1.3733 | 3.0971 | 19782.8679 | 0.83679 | 4567.6666
268 | E-SOR-TOU-CC-ET-HC-R100 | 26.5 | 2 | 494.8992 | 0.33385 | 0.494 | 0.74556 | 0.26369 | #NAME? | 356.525 | 356.525 | 850.5 | 554.7 | 0 | 14876.4814 | 821.683 | 788.5986 | 4.5016 | 81.8477 | 0.024304 | 1.3305 | 3.0964 | 19774.2825 | 0.83582 | 4595.5968
269 | E-SOR-TOU-CC-ET-HC-R100 | 21.5 | 1.6 | 543.9589 | 0.36694 | 0.49726 | 0.67031 | 0.21124 | #NAME? | 359.6 | 359.6 | 850.5 | 428.075 | 0 | 16191.6315 | 839.7908 | 788.5884 | 4.4354 | 82.2025 | 0.023796 | 1.284 | 3.097 | 19753.8385 | 0.83739 | 4534.5929
270 | E-SOR-TOU-CC-ET-HC-R100 | 17 | 1.3 | 596.6292 | 0.40247 | 0.50013 | 0.57479 | 0.15745 | #NAME? | 363.175 | 363.175 | 850.5 | 303.8 | 0 | 17620.6934 | 861.7064 | 788.5889 | 4.3631 | 82.7943 | 0.023206 | 1.2336 | 3.0976 | 19727.5046 | 0.83945 | 4457.4766
271 | E-SOR-TOU-CC-ET-HC-R100 | 12.5 | 0.95 | 661.9552 | 0.44654 | 0.5018 | 0.45883 | 0.096789 | #NAME? | 365 | 365 | 850.5 | 165.4 | 0 | 19272.9383 | 886.3589 | 788.5886 | 4.2995 | 84.418 | 0.022577 | 1.18 | 3.095 | 19702.7116 | 0.84459 | 4281.2106
272 | E-SOR-TOU-CC-ET-HC-R100 | 31 | 1.55 | 444.2812 | 0.2997 | 0.49249 | 0.76982 | 0.2846 | #NAME? | 355.2 | 355.2 | 850.5 | 691.575 | 0 | 14382.3857 | 803.6653 | 788.618 | 4.5434 | 84.0955 | 0.024823 | 1.3754 | 3.097 | 19786.7584 | 0.83183 | 4734.9512
273 | E-SOR-TOU-CC-ET-HC-R100 | 26.5 | 1.35 | 481.7756 | 0.325 | 0.49461 | 0.72346 | 0.24716 | #NAME? | 357.1 | 357.1 | 850.5 | 587.95 | 0 | 15290.0993 | 818.4531 | 788.6117 | 4.4962 | 83.5623 | 0.024394 | 1.3321 | 3.0959 | 19775.1945 | 0.83371 | 4665.5625
274 | E-SOR-TOU-CC-ET-HC-R100 | 21.5 | 1.1 | 529.1391 | 0.35695 | 0.49746 | 0.65153 | 0.19732 | #NAME? | 360 | 360 | 850.5 | 465.375 | 0 | 16540.4042 | 838.8184 | 788.5979 | 4.4315 | 83.2735 | 0.023822 | 1.2785 | 3.0963 | 19754.2415 | 0.83642 | 4566.5165
275 | E-SOR-TOU-CC-ET-HC-R100 | 17 | 0.85 | 579.5573 | 0.39096 | 0.49969 | 0.55261 | 0.14408 | #NAME? | 362.525 | 362.525 | 850.5 | 345.35 | 0 | 17982.3945 | 860.4085 | 788.5948 | 4.3719 | 83.9354 | 0.023245 | 1.2267 | 3.0972 | 19733.7345 | 0.83761 | 4520.0224
276 | E-SOR-TOU-CC-ET-HC-R10 | 12.5 | 0.65 | 643.6143 | 0.43417 | 0.50161 | 0.43339 | 0.081635 | #NAME? | 364.975 | 364.975 | 850.5 | 200.65 | 0 | 19677.8554 | 885.5659 | 788.5787 | 4.3082 | 86.386 | 0.022597 | 1.1746 | 3.0953 | 19703.3653 | 0.83932 | 4454.5184
277 | E-SOR-TOU-CC-ET-HC-R10 | 31 | 0.8 | 413.0534 | 0.27864 | 0.4919 | 0.71821 | 0.23917 | #NAME? | 354.4 | 354.4 | 850.5 | 776.45 | 0 | 15469.0633 | 806.5665 | 788.6037 | 4.5465 | 85.7854 | 0.024726 | 1.3362 | 3.0967 | 19774.0831 | 0.82803 | 4862.2721
278 | E-SOR-TOU-CC-ET-HC-R10 | 26.5 | 0.65 | 439.9904 | 0.29681 | 0.49363 | 0.66313 | 0.19194 | #NAME? | 356.575 | 356.575 | 850.5 | 698.05 | 0 | 16596.2739 | 821.2052 | 788.5855 | 4.4993 | 86.146 | 0.024298 | 1.2904 | 3.0962 | 19757.2392 | 0.82747 | 4875.0384
279 | E-SOR-TOU-CC-ET-HC-R10 | 21.5 | 0.55 | 482.2967 | 0.32535 | 0.49609 | 0.5949 | 0.13997 | #NAME? | 358.85 | 358.85 | 850.5 | 578.725 | 0 | 17870.6177 | 842.0685 | 788.587 | 4.4436 | 86.4044 | 0.023721 | 1.238 | 3.0964 | 19740.1076 | 0.82671 | 4893.7768
280 | E-SOR-TOU-CC-ET-HC-R10 | 17 | 0.45 | 530.4384 | 0.35782 | 0.4985 | 0.49728 | 0.09242 | #NAME? | 360.9 | 360.9 | 850.5 | 462.05 | 0 | 19200.5991 | 864.1291 | 788.59 | 4.3922 | 87.3113 | 0.023138 | 1.1879 | 3.0958 | 19722.017 | 0.82607 | 4908.0551
281 | E-SOR-TOU-CC-ET-HC-R10 | 12.5 | 0.3 | 560.4552 | 0.37807 | 0.49969 | 0.34943 | 0.0032102 | #NAME? | 363.025 | 363.025 | 850.5 | 362.4 | 0 | 21526.818 | 892.0647 | 788.5705 | 4.3506 | 95.2036 | 0.022426 | 1.1229 | 3.0968 | 19686.0831 | 0.81544 | 5265.905
282 | E-SOR-TOU-CC-ET-HC-R600 | 31 | 2.3 | 447.06 | 0.30303 | 0.49844 | 0.77292 | 0.37607 | #NAME? | 452.975 | 452.975 | 1048.625 | 659.55 | 0 | 9476.1886 | 867.8634 | 929.2098 | 4.5705 | 63.9199 | 0.017939 | 1.3496 | 3.1397 | 14422.2074 | 0.81769 | 4254.1528
283 | E-SOR-TOU-CC-ET-HC-R600 | 26.5 | 2 | 485.1149 | 0.32882 | 0.50095 | 0.71734 | 0.32837 | #NAME? | 456.6 | 456.6 | 1048.625 | 553.75 | 0 | 10418.2198 | 882.4139 | 929.1958 | 4.5134 | 64.0001 | 0.017647 | 1.3085 | 3.1393 | 14406.3681 | 0.81814 | 4232.6667
284 | E-SOR-TOU-CC-ET-HC-R600 | 21.5 | 1.6 | 533.5545 | 0.36166 | 0.5036 | 0.6291 | 0.26488 | #NAME? | 460.25 | 460.25 | 1048.625 | 427.475 | 0 | 11756.8337 | 903.2131 | 929.1931 | 4.4471 | 64.1526 | 0.017249 | 1.2525 | 3.1384 | 14388.8142 | 0.81787 | 4230.4974
285 | E-SOR-TOU-CC-ET-HC-R600 | 17 | 1.3 | 590.5305 | 0.40028 | 0.50518 | 0.53068 | 0.20894 | #NAME? | 463.125 | 463.125 | 1048.625 | 291.375 | 0 | 13053.4941 | 924.8522 | 929.185 | 4.3889 | 64.253 | 0.016849 | 1.2017 | 3.1389 | 14365.3353 | 0.82106 | 4132.0783
286 | E-SOR-TOU-CC-ET-HC-R600 | 12.5 | 0.95 | 658.5209 | 0.44636 | 0.50718 | 0.40488 | 0.14742 | #NAME? | 465.85 | 465.85 | 1048.625 | 153.475 | 0 | 14555.7228 | 950.4215 | 929.186 | 4.3319 | 64.5614 | 0.016373 | 1.1456 | 3.1384 | 14312.8506 | 0.82894 | 3897.9828
287 | E-SOR-TOU-CC-ET-HC-R600 | 31 | 1.55 | 433.6099 | 0.29391 | 0.49854 | 0.74182 | 0.3427 | #NAME? | 453.4 | 453.4 | 1048.625 | 696.775 | 0 | 10099.5768 | 866.5566 | 929.2006 | 4.567 | 65.6402 | 0.017964 | 1.3419 | 3.1392 | 14422.6902 | 0.81047 | 4461.8204
288 | E-SOR-TOU-CC-ET-HC-R600 | 26.5 | 1.35 | 470.6764 | 0.31904 | 0.50063 | 0.69162 | 0.29819 | #NAME? | 456.75 | 456.75 | 1048.625 | 593.825 | 0 | 10968.1533 | 881.6812 | 929.1999 | 4.5134 | 65.3627 | 0.017661 | 1.2991 | 3.139 | 14407.6155 | 0.81246 | 4396.2245
289 | E-SOR-TOU-CC-ET-HC-R600 | 21.5 | 1.1 | 519.6184 | 0.35221 | 0.50296 | 0.60651 | 0.24487 | #NAME? | 459.3 | 459.3 | 1048.625 | 464.55 | 0 | 12155.5104 | 901.1207 | 929.1813 | 4.4562 | 65.2209 | 0.017286 | 1.2462 | 3.1375 | 14389.0015 | 0.8146 | 4324.8866
290 | E-SOR-TOU-CC-ET-HC-R600 | 17 | 0.85 | 574.7045 | 0.38955 | 0.50495 | 0.50694 | 0.19337 | #NAME? | 462.55 | 462.55 | 1048.625 | 332.75 | 0 | 13398.3201 | 923.424 | 929.1904 | 4.3974 | 65.1625 | 0.01687 | 1.1948 | 3.1385 | 14363.0247 | 0.81835 | 4208.4393
291 | E-SOR-TOU-CC-ET-HC-R60 | 12.5 | 0.65 | 641.9396 | 0.43512 | 0.50689 | 0.38486 | 0.12972 | #NAME? | 465.325 | 465.325 | 1048.625 | 186.5 | 0 | 14901.7715 | 948.8955 | 929.162 | 4.3435 | 65.8749 | 0.016392 | 1.1409 | 3.1382 | 14307.5106 | 0.82378 | 4040.0045
292 | E-SOR-TOU-CC-ET-HC-R60 | 31 | 0.8 | 402.9236 | 0.27311 | 0.49723 | 0.67453 | 0.29232 | #NAME? | 452.3 | 452.3 | 1048.625 | 775.875 | 0 | 11163.7027 | 867.2056 | 929.2101 | 4.569 | 67.4165 | 0.017941 | 1.3073 | 3.1383 | 14413.7107 | 0.80669 | 4572.6964
293 | E-SOR-TOU-CC-ET-HC-R60 | 26.5 | 0.65 | 433.4923 | 0.29383 | 0.49918 | 0.62026 | 0.24471 | #NAME? | 454.525 | 454.525 | 1048.625 | 691.85 | 0 | 12091.9179 | 881.9383 | 929.2062 | 4.5295 | 67.1725 | 0.01764 | 1.2614 | 3.1396 | 14391.5637 | 0.80761 | 4536.363
294 | E-SOR-TOU-CC-ET-HC-R60 | 21.5 | 0.55 | 478.7892 | 0.32454 | 0.50153 | 0.54583 | 0.19157 | #NAME? | 457.5 | 457.5 | 1048.625 | 570.25 | 0 | 13204.014 | 903.347 | 929.1849 | 4.473 | 66.774 | 0.017222 | 1.2075 | 3.1387 | 14364.939 | 0.80829 | 4504.689
295 | E-SOR-TOU-CC-ET-HC-R60 | 17 | 0.45 | 531.4102 | 0.3602 | 0.50371 | 0.45302 | 0.14606 | #NAME? | 460.875 | 460.875 | 1048.625 | 442.2 | 0 | 14317.8674 | 925.6689 | 929.188 | 4.4173 | 66.7209 | 0.0168 | 1.1597 | 3.1393 | 14330.1458 | 0.81105 | 4412.4336
296 | E-SOR-TOU-CC-ET-HC-R60 | 12.5 | 0.3 | 561.7715 | 0.38078 | 0.50516 | 0.30793 | 0.031916 | #NAME? | 462.625 | 462.625 | 1048.625 | 343.725 | 0 | 16600.7826 | 952.6424 | 929.1638 | 4.389 | 71.8321 | 0.016293 | 1.092 | 3.1377 | 14268.4029 | 0.79846 | 4760.9984
297 | E-SOR-TOU-CC-ET-WC-R100 | 43.5 | 3.25 | 424.9966 | 0.28669 | 0.52874 | 0.83494 | 0.32997 | #NAME? | 413.725 | 413.725 | 850.5 | 779.25 | 10.676 | 18274.9136 | 692.5111 | 1030.3789 | 9.7586 | 103.32 | 0.039408 | 1.3678 | 3.0647 | 27361.6244 | 0.8735 | 4650.4036
298 | E-SOR-TOU-CC-ET-WC-R100 | 37 | 2.8 | 462.2342 | 0.31181 | 0.53079 | 0.79025 | 0.28309 | #NAME? | 415.525 | 415.525 | 850.5 | 661.55 | 10.6851 | 19752.3412 | 700.9707 | 1030.3483 | 9.669 | 104.7261 | 0.038951 | 1.3248 | 3.0624 | 27346.7288 | 0.8703 | 4780.096
299 | E-SOR-TOU-CC-ET-WC-R100 | 30.5 | 2.3 | 507.1463 | 0.34211 | 0.53336 | 0.72393 | 0.2357 | #NAME? | 418.025 | 418.025 | 850.5 | 536.025 | 10.7041 | 21368.2123 | 712.1833 | 1030.323 | 9.5504 | 105.9602 | 0.038355 | 1.2809 | 3.0624 | 27319.6438 | 0.86939 | 4811.1754
300 | E-SOR-TOU-CC-ET-WC-R100 | 24 | 1.8 | 560.0956 | 0.37783 | 0.53704 | 0.64287 | 0.18172 | #NAME? | 422.175 | 422.175 | 850.5 | 401.125 | 10.7495 | 23224.2532 | 728.8024 | 1030.3168 | 9.3745 | 107.0284 | 0.037496 | 1.2292 | 3.0625 | 27274.4795 | 0.8713 | 4718.8438
301 | E-SOR-TOU-CC-ET-WC-R100 | 17.5 | 1.3 | 625.9048 | 0.42222 | 0.53973 | 0.52625 | 0.12139 | #NAME? | 425.375 | 425.375 | 850.5 | 248.65 | 10.7839 | 25464.0676 | 751.6416 | 1030.2828 | 9.1798 | 108.5969 | 0.036397 | 1.1696 | 3.0623 | 27233.5099 | 0.87548 | 4534.5473
302 | E-SOR-TOU-CC-ET-WC-R100 | 43.5 | 2.2 | 412.9601 | 0.27857 | 0.5293 | 0.81444 | 0.30168 | #NAME? | 414.7 | 414.7 | 850.5 | 810.85 | 10.688 | 19136.9497 | 688.5454 | 1030.3836 | 9.7473 | 106.7417 | 0.039622 | 1.3688 | 3.0649 | 27366.1892 | 0.86553 | 4988.9519
303 | E-SOR-TOU-CC-ET-WC-R100 | 37 | 1.85 | 448.6713 | 0.30266 | 0.53145 | 0.76712 | 0.26304 | #NAME? | 416.75 | 416.75 | 850.5 | 703.325 | 10.6955 | 20415.9529 | 696.1886 | 1030.3419 | 9.6593 | 107.644 | 0.039198 | 1.3279 | 3.0633 | 27347.638 | 0.8664 | 4945.4595
304 | E-SOR-TOU-CC-ET-WC-R100 | 30.5 | 1.55 | 492.7313 | 0.33239 | 0.53424 | 0.70703 | 0.22063 | #NAME? | 419.35 | 419.35 | 850.5 | 573.725 | 10.7187 | 21859.2839 | 709.5175 | 1030.32 | 9.5359 | 107.8801 | 0.038483 | 1.2788 | 3.0625 | 27316.7053 | 0.86789 | 4873.2285
305 | E-SOR-TOU-CC-ET-WC-R100 | 24 | 1.2 | 542.9829 | 0.36628 | 0.53704 | 0.61916 | 0.17105 | #NAME? | 422.275 | 422.275 | 850.5 | 444.825 | 10.7518 | 23654.7496 | 727.6332 | 1030.3288 | 9.3815 | 108.1973 | 0.03756 | 1.2221 | 3.0626 | 27281.2502 | 0.87102 | 4731.7521
306 | E-SOR-TOU-CC-ET-WC-R10 | 17.5 | 0.9 | 610.3779 | 0.41175 | 0.53979 | 0.50641 | 0.1098 | #NAME? | 425.65 | 425.65 | 850.5 | 283.275 | 10.7936 | 25890.4534 | 750.178 | 1030.2853 | 9.1982 | 110.605 | 0.036467 | 1.1663 | 3.0635 | 27236.2031 | 0.87189 | 4685.3069
307 | E-SOR-TOU-CC-ET-WC-R10 | 43.5 | 1.1 | 382.3135 | 0.2579 | 0.52907 | 0.76096 | 0.25564 | #NAME? | 415.125 | 415.125 | 850.5 | 890.575 | 10.6988 | 20651.1205 | 688.2827 | 1030.3888 | 9.7298 | 110.2821 | 0.039608 | 1.3369 | 3.0638 | 27346.2626 | 0.8608 | 5189.5203
308 | E-SOR-TOU-CC-ET-WC-R10 | 37 | 0.95 | 415.3833 | 0.28021 | 0.53094 | 0.71691 | 0.21952 | #NAME? | 416.775 | 416.775 | 850.5 | 790.15 | 10.7108 | 21840.591 | 696.484 | 1030.3542 | 9.6559 | 111.022 | 0.039151 | 1.2964 | 3.0628 | 27324.0984 | 0.86138 | 5158.1807
309 | E-SOR-TOU-CC-ET-WC-R10 | 30.5 | 0.75 | 449.3008 | 0.30309 | 0.53365 | 0.65466 | 0.17207 | #NAME? | 419.15 | 419.15 | 850.5 | 688.975 | 10.7211 | 23424.9012 | 709.6007 | 1030.3165 | 9.5456 | 112.0312 | 0.038448 | 1.2457 | 3.063 | 27292.5798 | 0.86177 | 5132.3669
310 | E-SOR-TOU-CC-ET-WC-R10 | 24 | 0.6 | 492.3307 | 0.33212 | 0.53624 | 0.56825 | 0.11604 | #NAME? | 421.825 | 421.825 | 850.5 | 564.9 | 10.7522 | 25376.512 | 729.2161 | 1030.3231 | 9.4082 | 113.8939 | 0.037458 | 1.1883 | 3.0638 | 27258.6408 | 0.8588 | 5251.6464
311 | E-SOR-TOU-CC-ET-WC-R10 | 17.5 | 0.45 | 550.3847 | 0.37128 | 0.53884 | 0.43863 | 0.065739 | #NAME? | 424.425 | 424.425 | 850.5 | 420.625 | 10.7753 | 27433.344 | 751.9237 | 1030.3011 | 9.271 | 116.4882 | 0.036359 | 1.1325 | 3.0622 | 27212.5414 | 0.85983 | 5195.4784
312 | E-SOR-TOU-CC-ET-WC-R600 | 43.5 | 3.25 | 412.3706 | 0.27952 | 0.53049 | 0.81532 | 0.39731 | #NAME? | 538.025 | 538.025 | 1048.625 | 786.5 | 13.9972 | 12215.721 | 716.8604 | 1238.6458 | 9.6124 | 80.494 | 0.029352 | 1.345 | 3.1055 | 19706.9238 | 0.8572 | 4305.904
313 | E-SOR-TOU-CC-ET-WC-R600 | 37 | 2.8 | 449.6107 | 0.30476 | 0.53295 | 0.76485 | 0.34688 | #NAME? | 541.6 | 541.6 | 1048.625 | 671.775 | 14.0298 | 13496.8146 | 726.039 | 1238.6091 | 9.5124 | 81.2638 | 0.028977 | 1.2992 | 3.1057 | 19679.42 | 0.85597 | 4340.0743
314 | E-SOR-TOU-CC-ET-WC-R600 | 30.5 | 2.3 | 493.4278 | 0.33446 | 0.53615 | 0.68969 | 0.29112 | #NAME? | 545.975 | 545.975 | 1048.625 | 547.325 | 14.0736 | 15062.8722 | 740.4072 | 1238.5583 | 9.3748 | 81.8588 | 0.028426 | 1.2454 | 3.1045 | 19653.3535 | 0.85436 | 4385.4814
315 | E-SOR-TOU-CC-ET-WC-R600 | 24 | 1.8 | 546.9758 | 0.37076 | 0.5387 | 0.59028 | 0.23088 | #NAME? | 549.9 | 549.9 | 1048.625 | 407.425 | 14.1277 | 16891.7433 | 759.9342 | 1238.5555 | 9.2251 | 82.176 | 0.027716 | 1.1849 | 3.1056 | 19621.3184 | 0.85506 | 4350.8868
316 | E-SOR-TOU-CC-ET-WC-R600 | 17.5 | 1.3 | 619.6931 | 0.42004 | 0.54136 | 0.46818 | 0.16818 | #NAME? | 553.875 | 553.875 | 1048.625 | 236.475 | 14.1806 | 18915.6152 | 783.0148 | 1238.5416 | 9.0586 | 82.7253 | 0.026899 | 1.1279 | 3.105 | 19568.3739 | 0.85969 | 4175.7879
317 | E-SOR-TOU-CC-ET-WC-R600 | 43.5 | 2.2 | 399.488 | 0.27078 | 0.53108 | 0.78896 | 0.365 | #NAME? | 539.725 | 539.725 | 1048.625 | 821.675 | 14.0274 | 13002.4196 | 714.3252 | 1238.646 | 9.5973 | 82.9042 | 0.029446 | 1.3404 | 3.1064 | 19705.4315 | 0.8506 | 4538.8362
318 | E-SOR-TOU-CC-ET-WC-R600 | 37 | 1.85 | 434.6842 | 0.29464 | 0.53322 | 0.73524 | 0.31613 | #NAME? | 542.6 | 542.6 | 1048.625 | 711.575 | 14.0506 | 14283.4557 | 724.6481 | 1238.6218 | 9.507 | 83.3979 | 0.029032 | 1.29 | 3.106 | 19682.2557 | 0.84937 | 4574.1281
319 | E-SOR-TOU-CC-ET-WC-R600 | 30.5 | 1.55 | 478.423 | 0.32429 | 0.5359 | 0.66409 | 0.26765 | #NAME? | 545.825 | 545.825 | 1048.625 | 585.625 | 14.0764 | 15687.6999 | 738.1697 | 1238.5713 | 9.3877 | 83.6766 | 0.028509 | 1.2394 | 3.1044 | 19656.2591 | 0.84984 | 4546.9337
320 | E-SOR-TOU-CC-ET-WC-R600 | 24 | 1.2 | 532.6767 | 0.36106 | 0.5385 | 0.56867 | 0.21471 | #NAME? | 549.7 | 549.7 | 1048.625 | 443.075 | 14.1302 | 17353.3276 | 756.5269 | 1238.5789 | 9.2473 | 83.8857 | 0.027832 | 1.1845 | 3.106 | 19621.816 | 0.85183 | 4465.4407
321 | E-SOR-TOU-CC-ET-WC-R60 | 17.5 | 0.9 | 606.1248 | 0.41085 | 0.54115 | 0.44958 | 0.16002 | #NAME? | 553.55 | 553.55 | 1048.625 | 268.9 | 14.1719 | 19204.3245 | 780.2219 | 1238.5343 | 9.0836 | 83.8461 | 0.02698 | 1.1274 | 3.1049 | 19561.836 | 0.85806 | 4231.4461
322 | E-SOR-TOU-CC-ET-WC-R60 | 43.5 | 1.1 | 368.812 | 0.24999 | 0.5306 | 0.71787 | 0.31121 | #NAME? | 539.725 | 539.725 | 1048.625 | 904.275 | 14.0385 | 14527.2823 | 714.8755 | 1238.6465 | 9.5843 | 85.7329 | 0.029407 | 1.302 | 3.1055 | 19691.8909 | 0.84498 | 4739.0291
323 | E-SOR-TOU-CC-ET-WC-R60 | 37 | 0.95 | 403.2649 | 0.27334 | 0.53263 | 0.67278 | 0.27311 | #NAME? | 542.425 | 542.425 | 1048.625 | 794.45 | 14.0608 | 15544.9445 | 724.9174 | 1238.6247 | 9.5052 | 85.6404 | 0.029004 | 1.2583 | 3.1062 | 19667.7776 | 0.84637 | 4680.4217
324 | E-SOR-TOU-CC-ET-WC-R60 | 30.5 | 0.75 | 441.5144 | 0.29927 | 0.53498 | 0.6078 | 0.22305 | #NAME? | 545.375 | 545.375 | 1048.625 | 684.9 | 14.0848 | 16918.4879 | 738.2872 | 1238.5791 | 9.4031 | 85.9546 | 0.028474 | 1.2089 | 3.1061 | 19629.5271 | 0.84647 | 4664.9076
325 | E-SOR-TOU-CC-ET-WC-R60 | 24 | 0.6 | 489.4398 | 0.33176 | 0.53753 | 0.51732 | 0.16816 | #NAME? | 548.175 | 548.175 | 1048.625 | 555.9 | 14.1106 | 18561.0686 | 756.5323 | 1238.5441 | 9.2821 | 86.4525 | 0.027779 | 1.1549 | 3.1046 | 19579.4964 | 0.84592 | 4669.8939
326 | E-SOR-TOU-CC-ET-WC-R60 | 17.5 | 0.45 | 552.9693 | 0.37482 | 0.54021 | 0.39299 | 0.11551 | #NAME? | 552.125 | 552.125 | 1048.625 | 399.55 | 14.1569 | 20399.1465 | 780.5991 | 1238.5271 | 9.1481 | 86.972 | 0.026899 | 1.0974 | 3.105 | 19502.9358 | 0.8489 | 4544.4199
327 | E-SOR-TOU-CC-FP-HC-R100 | 31 | 2.3 | 413.863 | 0.27918 | 0.49477 | 0.71051 | 0.2803 | #NAME? | 358.35 | 358.35 | 850.5 | 335 | 0 | 14733.4481 | 826.8922 | 788.6032 | 4.461 | 80.2616 | 0.024155 | 1.3355 | 3.0964 | 19767.176 | 0.84834 | 4180.129
328 | E-SOR-TOU-CC-FP-HC-R100 | 26.5 | 2 | 446.2241 | 0.30101 | 0.49668 | 0.65654 | 0.24066 | #NAME? | 360.15 | 360.15 | 850.5 | 276.275 | 0 | 15715.3719 | 836.6021 | 788.5927 | 4.4276 | 80.9264 | 0.02388 | 1.3 | 3.0971 | 19753.1371 | 0.84806 | 4184.4475
329 | E-SOR-TOU-CC-FP-HC-R100 | 21.5 | 1.6 | 488.4529 | 0.3295 | 0.49937 | 0.581 | 0.18878 | #NAME? | 363.025 | 363.025 | 850.5 | 210.3 | 0 | 17017.7933 | 851.9647 | 788.6048 | 4.3772 | 81.895 | 0.023456 | 1.2551 | 3.098 | 19731.2104 | 0.84724 | 4203.9353
330 | E-SOR-TOU-CC-FP-HC-R100 | 17 | 1.3 | 536.4299 | 0.36186 | 0.50094 | 0.49859 | 0.14196 | #NAME? | 364.525 | 364.525 | 850.5 | 137.925 | 0 | 18257.0869 | 868.1275 | 788.5747 | 4.3336 | 82.6424 | 0.023025 | 1.2117 | 3.0961 | 19708.9833 | 0.85036 | 4096.6448
331 | E-SOR-TOU-CC-FP-HC-R100 | 12.5 | 0.95 | 594.8412 | 0.40127 | 0.50223 | 0.39721 | 0.085557 | #NAME? | 366.425 | 366.425 | 850.5 | 66.7 | 0 | 19757.0331 | 888.0747 | 788.5967 | 4.2852 | 84.7827 | 0.022513 | 1.164 | 3.0953 | 19680.2948 | 0.85469 | 3951.4223
332 | E-SOR-TOU-CC-FP-HC-R100 | 31 | 1.55 | 396.6278 | 0.26756 | 0.49536 | 0.68422 | 0.25072 | #NAME? | 358.525 | 358.525 | 850.5 | 361.15 | 0 | 15407.8521 | 826.3857 | 788.6037 | 4.4564 | 82.1683 | 0.024168 | 1.3288 | 3.0966 | 19766.6472 | 0.84389 | 4324.8369
333 | E-SOR-TOU-CC-FP-HC-R100 | 26.5 | 1.35 | 428.2564 | 0.28889 | 0.49711 | 0.63497 | 0.21682 | #NAME? | 360.625 | 360.625 | 850.5 | 302.025 | 0 | 16260.1894 | 837.6928 | 788.5803 | 4.4197 | 82.2437 | 0.02385 | 1.2903 | 3.0976 | 19752.3429 | 0.84583 | 4256.5766
334 | E-SOR-TOU-CC-FP-HC-R100 | 21.5 | 1.1 | 468.5092 | 0.31605 | 0.49907 | 0.56482 | 0.17223 | #NAME? | 362.425 | 362.425 | 850.5 | 234.8 | 0 | 17404.3045 | 853.1241 | 788.5803 | 4.3773 | 82.4563 | 0.023427 | 1.2422 | 3.097 | 19732.5577 | 0.84862 | 4159.4934
335 | E-SOR-TOU-CC-FP-HC-R100 | 17 | 0.85 | 511.4578 | 0.34502 | 0.50059 | 0.47816 | 0.12211 | #NAME? | 364.175 | 364.175 | 850.5 | 164.825 | 0 | 18727.308 | 869.4588 | 788.5917 | 4.335 | 83.8743 | 0.022996 | 1.1987 | 3.0958 | 19712.3943 | 0.84915 | 4136.7306
336 | E-SOR-TOU-CC-FP-HC-R10 | 12.5 | 0.65 | 564.9728 | 0.38112 | 0.50191 | 0.36922 | 0.063503 | #NAME? | 366.75 | 366.75 | 850.5 | 93.225 | 0 | 20302.6522 | 888.9746 | 788.5723 | 4.2908 | 87.4193 | 0.022493 | 1.1538 | 3.098 | 19680.2259 | 0.8495 | 4118.5338
337 | E-SOR-TOU-CC-FP-HC-R10 | 31 | 0.8 | 355.4544 | 0.23978 | 0.49485 | 0.62319 | 0.19578 | #NAME? | 358.7 | 358.7 | 850.5 | 427.45 | 0 | 16713.6713 | 833.9352 | 788.5969 | 4.4441 | 83.8117 | 0.023949 | 1.28 | 3.098 | 19751.2411 | 0.84263 | 4364.4246
338 | E-SOR-TOU-CC-FP-HC-R10 | 26.5 | 0.65 | 375.8385 | 0.25353 | 0.49622 | 0.57011 | 0.14973 | #NAME? | 359.925 | 359.925 | 850.5 | 383.525 | 0 | 17807.3771 | 844.3182 | 788.5863 | 4.4166 | 85.1724 | 0.023657 | 1.2406 | 3.0973 | 19735.1726 | 0.84061 | 4425.7551
339 | E-SOR-TOU-CC-FP-HC-R10 | 21.5 | 0.55 | 408.3315 | 0.27545 | 0.49774 | 0.50251 | 0.10173 | #NAME? | 361.7 | 361.7 | 850.5 | 311.45 | 0 | 19004.4455 | 859.0644 | 788.5891 | 4.3797 | 86.7492 | 0.023262 | 1.1974 | 3.0976 | 19718.4936 | 0.83913 | 4469.6088
340 | E-SOR-TOU-CC-FP-HC-R10 | 17 | 0.45 | 454.4977 | 0.30659 | 0.49947 | 0.41273 | 0.065544 | #NAME? | 363.475 | 363.475 | 850.5 | 243.275 | 0 | 20084.1329 | 875.5649 | 788.5765 | 4.3475 | 88.3911 | 0.022834 | 1.1606 | 3.0971 | 19699.6553 | 0.83717 | 4528.4837
341 | E-SOR-TOU-CC-FP-HC-R10 | 12.5 | 0.3 | 455.5012 | 0.30727 | 0.50056 | 0.26083 | -0.022288 | #NAME? | 364.8 | 364.8 | 850.5 | 205.125 | 0 | 22397.7984 | 897.8511 | 788.5869 | 4.3331 | 99.5911 | 0.022268 | 1.0974 | 3.0961 | 19663.4196 | 0.82719 | 4854.6125
342 | E-SOR-TOU-CC-FP-HC-R600 | 31 | 2.3 | 398.2172 | 0.26992 | 0.50157 | 0.68055 | 0.33882 | #NAME? | 458.775 | 458.775 | 1048.625 | 324.575 | 0 | 10502.5344 | 889.2073 | 929.1937 | 4.4692 | 63.1282 | 0.017515 | 1.3014 | 3.1387 | 14401.4466 | 0.8329 | 3817.8318
343 | E-SOR-TOU-CC-FP-HC-R600 | 26.5 | 2 | 429.9928 | 0.29146 | 0.50325 | 0.6217 | 0.29478 | #NAME? | 461.2 | 461.2 | 1048.625 | 270.075 | 0 | 11415.0505 | 900.1656 | 929.185 | 4.4322 | 63.4695 | 0.0173 | 1.2641 | 3.138 | 14386.2922 | 0.83288 | 3812.0045
344 | E-SOR-TOU-CC-FP-HC-R600 | 21.5 | 1.6 | 472.4834 | 0.32026 | 0.50478 | 0.54025 | 0.23939 | #NAME? | 463.375 | 463.375 | 1048.625 | 197.3 | 0 | 12602.8407 | 915.0446 | 929.1702 | 4.3942 | 63.9162 | 0.017015 | 1.2183 | 3.139 | 14362.8754 | 0.83307 | 3799.4485
345 | E-SOR-TOU-CC-FP-HC-R600 | 17 | 1.3 | 523.6996 | 0.35498 | 0.50609 | 0.45376 | 0.19052 | #NAME? | 465 | 465 | 1048.625 | 125.45 | 0 | 13722.8577 | 931.0559 | 929.1764 | 4.3574 | 64.1949 | 0.016705 | 1.1763 | 3.1376 | 14327.6088 | 0.83589 | 3713.1572
346 | E-SOR-TOU-CC-FP-HC-R600 | 12.5 | 0.95 | 582.838 | 0.39506 | 0.50741 | 0.34748 | 0.13085 | #NAME? | 467.025 | 467.025 | 1048.625 | 60.7 | 0 | 15078.8212 | 950.0861 | 929.1702 | 4.322 | 64.9635 | 0.016336 | 1.1276 | 3.1385 | 14270.3939 | 0.84262 | 3519.6413
347 | E-SOR-TOU-CC-FP-HC-R600 | 31 | 1.55 | 380.4829 | 0.2579 | 0.5013 | 0.64822 | 0.30004 | #NAME? | 458.775 | 458.775 | 1048.625 | 358.45 | 0 | 11201.156 | 890.4451 | 929.1965 | 4.4684 | 64.417 | 0.01749 | 1.2856 | 3.1395 | 14398.4276 | 0.82754 | 3965.9188
348 | E-SOR-TOU-CC-FP-HC-R600 | 26.5 | 1.35 | 412.1303 | 0.27935 | 0.50284 | 0.59387 | 0.26041 | #NAME? | 460.65 | 460.65 | 1048.625 | 297 | 0 | 12028.4382 | 900.6142 | 929.1656 | 4.4366 | 64.7075 | 0.017289 | 1.2514 | 3.1383 | 14383.1789 | 0.82784 | 3951.0565
349 | E-SOR-TOU-CC-FP-HC-R600 | 21.5 | 1.1 | 454.9037 | 0.30835 | 0.50425 | 0.51589 | 0.2146 | #NAME? | 462.5 | 462.5 | 1048.625 | 222.525 | 0 | 13070.7175 | 915.0956 | 929.1815 | 4.4025 | 64.8927 | 0.01701 | 1.208 | 3.1396 | 14358.1567 | 0.82984 | 3888.2844
350 | E-SOR-TOU-CC-FP-HC-R600 | 17 | 0.85 | 500.9243 | 0.33954 | 0.50561 | 0.43149 | 0.16639 | #NAME? | 464.8 | 464.8 | 1048.625 | 153.275 | 0 | 14166.2892 | 930.7727 | 929.1947 | 4.3632 | 65.2922 | 0.016703 | 1.166 | 3.1385 | 14319.8409 | 0.83373 | 3771.3631
351 | E-SOR-TOU-CC-FP-HC-R60 | 12.5 | 0.65 | 557.4047 | 0.37782 | 0.50701 | 0.32297 | 0.10627 | #NAME? | 466.65 | 466.65 | 1048.625 | 81.875 | 0 | 15540.1197 | 949.9482 | 929.1593 | 4.3313 | 66.6295 | 0.016334 | 1.1192 | 3.1375 | 14266.2723 | 0.83717 | 3664.967
352 | E-SOR-TOU-CC-FP-HC-R60 | 31 | 0.8 | 343.0009 | 0.2325 | 0.50035 | 0.5756 | 0.23782 | #NAME? | 457.275 | 457.275 | 1048.625 | 422.725 | 0 | 12438.4364 | 894.8122 | 929.1885 | 4.4717 | 65.8708 | 0.017388 | 1.2405 | 3.1385 | 14377.1777 | 0.82423 | 4055.2856
353 | E-SOR-TOU-CC-FP-HC-R60 | 26.5 | 0.65 | 366.8033 | 0.24863 | 0.5015 | 0.52359 | 0.19535 | #NAME? | 458.95 | 458.95 | 1048.625 | 374.175 | 0 | 13279.4857 | 904.4591 | 929.1647 | 4.4457 | 66.3165 | 0.017187 | 1.2057 | 3.1388 | 14350.3002 | 0.82518 | 4020.709
354 | E-SOR-TOU-CC-FP-HC-R60 | 21.5 | 0.55 | 401.7956 | 0.27235 | 0.50334 | 0.45099 | 0.14516 | #NAME? | 460.5 | 460.5 | 1048.625 | 300.225 | 0 | 14337.1666 | 917.8081 | 929.1541 | 4.418 | 67.0735 | 0.016926 | 1.1645 | 3.138 | 14323.4645 | 0.82409 | 4041.7772
355 | E-SOR-TOU-CC-FP-HC-R60 | 17 | 0.45 | 450.641 | 0.30546 | 0.50467 | 0.36686 | 0.11196 | #NAME? | 463.275 | 463.275 | 1048.625 | 227.15 | 0 | 15239.4534 | 935.6277 | 929.1626 | 4.3818 | 67.392 | 0.016592 | 1.1289 | 3.1392 | 14289.6389 | 0.82487 | 4010.5888
356 | E-SOR-TOU-CC-FP-HC-R60 | 12.5 | 0.3 | 451.4547 | 0.30601 | 0.50563 | 0.22801 | -0.0030196 | #NAME? | 465.025 | 465.025 | 1048.625 | 185.5 | 0 | 17493.7341 | 956.7529 | 929.1511 | 4.3727 | 74.7448 | 0.016192 | 1.0642 | 3.1376 | 14232.8644 | 0.8135 | 4315.0718
357 | E-SOR-TOU-CC-FP-WC-R100 | 43.5 | 3.25 | 387.6012 | 0.26147 | 0.53187 | 0.75487 | 0.30067 | #NAME? | 416.975 | 416.975 | 850.5 | 404.325 | 10.7003 | 19518.8897 | 715.1509 | 1030.3476 | 9.518 | 100.567 | 0.038231 | 1.3278 | 3.064 | 27335.5466 | 0.88117 | 4322.8551
358 | E-SOR-TOU-CC-FP-WC-R100 | 37 | 2.8 | 420.6783 | 0.28378 | 0.53394 | 0.71172 | 0.25997 | #NAME? | 419.375 | 419.375 | 850.5 | 339.125 | 10.7238 | 20818.236 | 719.2666 | 1030.331 | 9.4611 | 102.4677 | 0.038001 | 1.2901 | 3.0636 | 27312.4979 | 0.87992 | 4368.8859
359 | E-SOR-TOU-CC-FP-WC-R100 | 30.5 | 2.3 | 459.4276 | 0.30992 | 0.5363 | 0.65055 | 0.21328 | #NAME? | 421.65 | 421.65 | 850.5 | 271.525 | 10.7461 | 22373.2991 | 726.514 | 1030.3293 | 9.3824 | 104.5757 | 0.03761 | 1.2506 | 3.0633 | 27278.8592 | 0.87836 | 4426.0758
360 | E-SOR-TOU-CC-FP-WC-R100 | 24 | 1.8 | 505.5407 | 0.34103 | 0.53877 | 0.56311 | 0.16498 | #NAME? | 424.6 | 424.6 | 850.5 | 197.275 | 10.7821 | 24127.081 | 739.5248 | 1030.3267 | 9.2713 | 106.0639 | 0.036955 | 1.2019 | 3.0638 | 27239.8887 | 0.87976 | 4360.0369
361 | E-SOR-TOU-CC-FP-WC-R100 | 17.5 | 1.3 | 566.0491 | 0.38184 | 0.54073 | 0.46396 | 0.10962 | #NAME? | 426.6 | 426.6 | 850.5 | 108.1 | 10.8021 | 26127.5888 | 756.5174 | 1030.2893 | 9.1364 | 108.3522 | 0.03614 | 1.1508 | 3.0625 | 27199.2094 | 0.88363 | 4193.1159
362 | E-SOR-TOU-CC-FP-WC-R100 | 43.5 | 2.2 | 371.7347 | 0.25076 | 0.53241 | 0.73185 | 0.27165 | #NAME? | 417.75 | 417.75 | 850.5 | 435.7 | 10.7099 | 20409.7109 | 714.0314 | 1030.3524 | 9.4956 | 103.157 | 0.038285 | 1.3197 | 3.0632 | 27334.9239 | 0.87616 | 4530.2495
363 | E-SOR-TOU-CC-FP-WC-R100 | 37 | 1.85 | 402.4747 | 0.2715 | 0.53421 | 0.68602 | 0.23554 | #NAME? | 419.75 | 419.75 | 850.5 | 367.025 | 10.7283 | 21605.8996 | 719.2915 | 1030.3435 | 9.4389 | 104.5004 | 0.037995 | 1.2813 | 3.063 | 27309.2853 | 0.877 | 4489.3402
364 | E-SOR-TOU-CC-FP-WC-R100 | 30.5 | 1.55 | 439.5114 | 0.29648 | 0.53645 | 0.62143 | 0.19578 | #NAME? | 422.125 | 422.125 | 850.5 | 298.8 | 10.753 | 23008.5595 | 727.6738 | 1030.341 | 9.3677 | 105.8235 | 0.037557 | 1.2381 | 3.0636 | 27280.1802 | 0.8777 | 4453.3544
365 | E-SOR-TOU-CC-FP-WC-R100 | 24 | 1.2 | 483.2114 | 0.32596 | 0.53841 | 0.53982 | 0.14968 | #NAME? | 424.175 | 424.175 | 850.5 | 224.975 | 10.7747 | 24673.5243 | 739.7205 | 1030.3076 | 9.2718 | 107.3817 | 0.036953 | 1.192 | 3.0636 | 27245.8029 | 0.87974 | 4361.955
366 | E-SOR-TOU-CC-FP-WC-R10 | 17.5 | 0.9 | 541.3575 | 0.36519 | 0.54072 | 0.43953 | 0.093787 | #NAME? | 426.65 | 426.65 | 850.5 | 133.75 | 10.8063 | 26684.4828 | 755.47 | 1030.304 | 9.1503 | 110.8661 | 0.036181 | 1.1448 | 3.0624 | 27195.6154 | 0.88048 | 4321.5975
367 | E-SOR-TOU-CC-FP-WC-R10 | 43.5 | 1.1 | 332.572 | 0.22435 | 0.5327 | 0.67074 | 0.21643 | #NAME? | 419.075 | 419.075 | 850.5 | 507.1 | 10.7363 | 22199.6305 | 718.2224 | 1030.3903 | 9.4424 | 106.5397 | 0.038045 | 1.2784 | 3.0646 | 27306.767 | 0.87332 | 4644.9156
368 | E-SOR-TOU-CC-FP-WC-R10 | 37 | 0.95 | 360.0355 | 0.24287 | 0.53412 | 0.62562 | 0.18401 | #NAME? | 420.2 | 420.2 | 850.5 | 437.675 | 10.7436 | 23298.1207 | 723.0369 | 1030.3419 | 9.4064 | 107.9963 | 0.037785 | 1.2431 | 3.0632 | 27285.5619 | 0.87346 | 4633.9843
369 | E-SOR-TOU-CC-FP-WC-R10 | 30.5 | 0.75 | 386.5612 | 0.26077 | 0.53599 | 0.56617 | 0.13713 | #NAME? | 421.725 | 421.725 | 850.5 | 384.525 | 10.7484 | 24847.623 | 730.6056 | 1030.3152 | 9.3472 | 110.7986 | 0.037387 | 1.2009 | 3.0622 | 27256.0542 | 0.87172 | 4699.8529
370 | E-SOR-TOU-CC-FP-WC-R10 | 24 | 0.6 | 418.8948 | 0.28258 | 0.53793 | 0.48573 | 0.084764 | #NAME? | 423.55 | 423.55 | 850.5 | 307.875 | 10.7718 | 26661.3171 | 743.1262 | 1030.3061 | 9.2729 | 114.6111 | 0.036764 | 1.1533 | 3.0629 | 27219.79 | 0.86847 | 4829.0623
371 | E-SOR-TOU-CC-FP-WC-R10 | 17.5 | 0.45 | 471.2271 | 0.31788 | 0.53987 | 0.36971 | 0.045722 | #NAME? | 425.7 | 425.7 | 850.5 | 227.125 | 10.7925 | 28339.4237 | 759.5685 | 1030.2958 | 9.2056 | 117.8758 | 0.035973 | 1.1087 | 3.0627 | 27171.1857 | 0.86974 | 4765.8334
372 | E-SOR-TOU-CC-FP-WC-R600 | 43.5 | 3.25 | 370.1143 | 0.25087 | 0.53437 | 0.72962 | 0.35719 | #NAME? | 544.175 | 544.175 | 1048.625 | 404.325 | 14.0667 | 13587.1564 | 740.1682 | 1238.6062 | 9.3475 | 78.9176 | 0.028457 | 1.2922 | 3.1063 | 19669.2853 | 0.86795 | 3920.0973
373 | E-SOR-TOU-CC-FP-WC-R600 | 37 | 2.8 | 402.1718 | 0.2726 | 0.53629 | 0.67589 | 0.31285 | #NAME? | 546.575 | 546.575 | 1048.625 | 335.6 | 14.0883 | 14785.1464 | 747.7618 | 1238.5594 | 9.285 | 79.6327 | 0.028166 | 1.2472 | 3.1047 | 19650.275 | 0.86709 | 3942.7437
374 | E-SOR-TOU-CC-FP-WC-R600 | 30.5 | 2.3 | 438.8018 | 0.29743 | 0.53833 | 0.60154 | 0.26265 | #NAME? | 549.4 | 549.4 | 1048.625 | 264.35 | 14.119 | 16240.519 | 757.6461 | 1238.5436 | 9.2073 | 80.5791 | 0.027792 | 1.2008 | 3.1046 | 19621.5746 | 0.86655 | 3953.1798
375 | E-SOR-TOU-CC-FP-WC-R600 | 24 | 1.8 | 487.6882 | 0.33057 | 0.5401 | 0.51364 | 0.2106 | #NAME? | 551.975 | 551.975 | 1048.625 | 186.75 | 14.1525 | 17820.0815 | 769.707 | 1238.5502 | 9.1228 | 81.5942 | 0.027338 | 1.1564 | 3.1049 | 19577.3454 | 0.86732 | 3917.2728
376 | E-SOR-TOU-CC-FP-WC-R600 | 17.5 | 1.3 | 551.305 | 0.37369 | 0.54201 | 0.40752 | 0.15342 | #NAME? | 554.925 | 554.925 | 1048.625 | 100.3 | 14.1922 | 19598.0855 | 786.0041 | 1238.5286 | 9.0196 | 82.5755 | 0.026724 | 1.1077 | 3.1049 | 19499.3823 | 0.87219 | 3737.992
377 | E-SOR-TOU-CC-FP-WC-R600 | 43.5 | 2.2 | 354.2852 | 0.24014 | 0.53446 | 0.70111 | 0.32145 | #NAME? | 544.7 | 544.7 | 1048.625 | 431.925 | 14.0745 | 14450.281 | 741.8859 | 1238.6199 | 9.3298 | 80.46 | 0.028395 | 1.2755 | 3.1062 | 19668.426 | 0.86281 | 4096.7967
378 | E-SOR-TOU-CC-FP-WC-R600 | 37 | 1.85 | 383.411 | 0.25989 | 0.53604 | 0.64366 | 0.2784 | #NAME? | 546.825 | 546.825 | 1048.625 | 366.875 | 14.0993 | 15652.6868 | 747.531 | 1238.5705 | 9.2822 | 81.5973 | 0.028168 | 1.2355 | 3.1057 | 19644.59 | 0.86203 | 4116.8157
379 | E-SOR-TOU-CC-FP-WC-R600 | 30.5 | 1.55 | 421.0583 | 0.2854 | 0.53786 | 0.57582 | 0.23582 | #NAME? | 549.025 | 549.025 | 1048.625 | 294.325 | 14.12 | 16922.5449 | 755.4064 | 1238.5624 | 9.2214 | 82.5523 | 0.027865 | 1.1962 | 3.1053 | 19618.5715 | 0.86258 | 4090.3904
380 | E-SOR-TOU-CC-FP-WC-R600 | 24 | 1.2 | 468.5129 | 0.31757 | 0.53978 | 0.48802 | 0.1915 | #NAME? | 551.725 | 551.725 | 1048.625 | 215.05 | 14.154 | 18358.094 | 768.0518 | 1238.5651 | 9.1386 | 83.1325 | 0.027382 | 1.1516 | 3.1053 | 19568.0676 | 0.86488 | 3999.9622
381 | E-SOR-TOU-CC-FP-WC-R60 | 17.5 | 0.9 | 530.837 | 0.35982 | 0.54181 | 0.39108 | 0.13875 | #NAME? | 554.65 | 554.65 | 1048.625 | 122.375 | 14.1907 | 19982.5366 | 784.7328 | 1238.5314 | 9.0333 | 83.799 | 0.026755 | 1.1027 | 3.105 | 19492.0594 | 0.87124 | 3769.0264
382 | E-SOR-TOU-CC-FP-WC-R60 | 43.5 | 1.1 | 317.1109 | 0.21495 | 0.53414 | 0.62463 | 0.26045 | #NAME? | 544.825 | 544.825 | 1048.625 | 502.575 | 14.0884 | 16133.2961 | 746.3114 | 1238.6257 | 9.3006 | 82.7398 | 0.028209 | 1.2306 | 3.1058 | 19643.7213 | 0.86018 | 4184.4855
383 | E-SOR-TOU-CC-FP-WC-R60 | 37 | 0.95 | 345.9203 | 0.23447 | 0.53549 | 0.57892 | 0.22759 | #NAME? | 546.475 | 546.475 | 1048.625 | 434.425 | 14.1024 | 17053.909 | 750.1739 | 1238.5994 | 9.2723 | 83.651 | 0.028038 | 1.1991 | 3.1055 | 19613.0859 | 0.86076 | 4156.6332
384 | E-SOR-TOU-CC-FP-WC-R60 | 30.5 | 0.75 | 376.1251 | 0.25495 | 0.53725 | 0.51587 | 0.18483 | #NAME? | 548.35 | 548.35 | 1048.625 | 374.2 | 14.1149 | 18270.7139 | 758.6239 | 1238.554 | 9.219 | 84.5065 | 0.027695 | 1.158 | 3.1047 | 19568.3655 | 0.86173 | 4112.4742
385 | E-SOR-TOU-CC-FP-WC-R60 | 24 | 0.6 | 412.9668 | 0.27992 | 0.53901 | 0.4362 | 0.13066 | #NAME? | 550.55 | 550.55 | 1048.625 | 296.95 | 14.1415 | 19809.9894 | 770.1479 | 1238.5642 | 9.1599 | 86.3402 | 0.027252 | 1.1145 | 3.105 | 19516.7058 | 0.85996 | 4162.136
386 | E-SOR-TOU-CC-FP-WC-R60 | 17.5 | 0.45 | 469.001 | 0.3179 | 0.54108 | 0.32088 | 0.085518 | #NAME? | 553.6 | 553.6 | 1048.625 | 209.35 | 14.1736 | 21440.9936 | 787.5227 | 1238.5517 | 9.1047 | 88.1515 | 0.026612 | 1.0708 | 3.1052 | 19443.9889 | 0.85885 | 4184.7931
387 | E-SOR-TOU-FC-ET-HC-OFF0 | 13 | 1 | 575.2286 | 0.38991 | 0.36406 | 0.59012 | 0.45972 | 1 | 620.925 | 620.925 | 1821 | 257.9 | 0 | 2647.2856 | 897.4624 | 784.5306 | 2.4763 | 43.3703 | 0.003311 | 1.6054 | 2.8281 | 1192.337 | 0.60041 | 4045.9712
388 | E-SOR-TOU-FC-ET-HC-OFF0 | 11 | 0.85 | 608.8984 | 0.41273 | 0.36624 | 0.48125 | 0.33609 | 1 | 627.225 | 627.225 | 1821 | 194.4 | 0 | 3312.0682 | 917.4439 | 784.724 | 2.4565 | 44.8124 | 0.0032393 | 1.5345 | 2.8277 | 1192.337 | 0.60451 | 3958.847
389 | E-SOR-TOU-FC-ET-HC-OFF0 | 9 | 0.7 | 642.4672 | 0.43548 | 0.36808 | 0.35453 | 0.1708 | 1 | 633.65 | 633.65 | 1821 | 134.85 | 0 | 4108.2911 | 939.3974 | 784.677 | 2.4448 | 48.3838 | 0.003163 | 1.4544 | 2.8271 | 1192.337 | 0.60921 | 3865.0659
390 | E-SOR-TOU-FC-ET-HC-OFF0 | 7 | 0.55 | 674.4852 | 0.45718 | 0.36939 | 0.20031 | -0.03962 | 1 | 636.975 | 636.975 | 1821 | 78.55 | 0 | 5086.0069 | 960.8058 | 784.7412 | 2.4598 | 60.0596 | 0.0030902 | 1.368 | 2.8233 | 1192.337 | 0.61201 | 3805.1396
391 | E-SOR-TOU-FC-ET-HC-OFF0 | 5 | 0.4 | 709.7723 | 0.4811 | 0.3699 | 0.046534 | -0.2462 | 1 | 638.25 | 638.25 | 1821 | 16.475 | 0 | 6064.0711 | 980.5069 | 784.798 | 2.5091 | 112.2147 | 0.0030275 | 1.2898 | 2.822 | 1192.337 | 0.62353 | 3618.973
392 | E-SOR-TOU-FC-ET-HC-OFF0 | 13 | 0.65 | 562.0527 | 0.38097 | 0.36305 | 0.56214 | 0.36786 | 1 | 619 | 619 | 1821 | 287.5 | 0 | 2900.1233 | 899.0949 | 784.5839 | 2.488 | 44.0032 | 0.0033055 | 1.5686 | 2.8286 | 1192.337 | 0.59709 | 4112.4383
393 | E-SOR-TOU-FC-ET-HC-OFF0 | 11 | 0.55 | 594.4272 | 0.40292 | 0.36538 | 0.45559 | 0.21379 | 1 | 624.625 | 624.625 | 1821 | 220.3 | 0 | 3587.0142 | 919.356 | 784.7118 | 2.47 | 46.3548 | 0.0032312 | 1.4941 | 2.8259 | 1192.337 | 0.5984 | 4066.4368
394 | E-SOR-TOU-FC-ET-HC-OFF0 | 9 | 0.45 | 628.4009 | 0.42595 | 0.36693 | 0.32861 | 0.076417 | 1 | 629.975 | 629.975 | 1821 | 166.275 | 0 | 4354.7042 | 940.0233 | 784.5745 | 2.4618 | 51.1213 | 0.00316 | 1.4222 | 2.8262 | 1192.337 | 0.6032 | 3972.0922
395 | E-SOR-TOU-FC-ET-HC-OFF0 | 7 | 0.35 | 659.9238 | 0.44731 | 0.36807 | 0.18237 | -0.15724 | 1 | 632.75 | 632.75 | 1821 | 104.95 | 0 | 5327.4026 | 963.5507 | 784.7666 | 2.4765 | 68.2344 | 0.0030817 | 1.3309 | 2.8237 | 1192.337 | 0.60526 | 3926.4268
396 | E-SOR-TOU-FC-ET-HC-OFF | 5 | 0.25 | 659.1169 | 0.44677 | 0.36815 | -0.00075997 | -0.62197 | 1 | 633.675 | 633.675 | 1821 | 32.175 | 0 | 6769.1951 | 992.0629 | 784.7435 | 2.5456 | -445.8493 | 0.0029949 | 1.202 | 2.8265 | 1192.337 | 0.59852 | 4040.8543
397 | E-SOR-TOU-FC-ET-HC-OFF | 13 | 0.35 | 529.1123 | 0.35865 | 0.36177 | 0.50056 | 0.13853 | 1 | 613.25 | 613.25 | 1821 | 364.175 | 0 | 3483.9211 | 904.835 | 784.6587 | 2.5113 | 45.5984 | 0.0032845 | 1.4773 | 2.8281 | 1192.337 | 0.58977 | 4250.9727
398 | E-SOR-TOU-FC-ET-HC-OFF | 11 | 0.3 | 558.9226 | 0.37885 | 0.36353 | 0.3963 | -0.041215 | 1 | 618.1 | 618.1 | 1821 | 299.2 | 0 | 4196.6205 | 926.4179 | 784.6681 | 2.496 | 50.4836 | 0.0032079 | 1.4045 | 2.828 | 1192.337 | 0.58845 | 4257.3631
399 | E-SOR-TOU-FC-ET-HC-OFF | 7 | 0.2 | 739.8262 | 0.50147 | 0.36479 | 0.27025 | -0.37171 | 1 | 622.725 | 622.725 | 1821 | 236.4 | 0 | 5196.1619 | 951.4809 | 784.8695 | 2.4937 | 69.3771 | 0.0031238 | 1.3071 | 2.8277 | 1192.337 | 0.58521 | 4303.4022
400 | E-SOR-TOU-FC-ET-HC-R100 | 13 | 1 | 569.0744 | 0.38388 | 0.363 | 0.61486 | 0.2088 | #NAME? | 278.4 | 278.4 | 1024.225 | 337.2 | 0 | 6970.0719 | 695.8979 | 488.7376 | 2.4532 | 44.5973 | 0.011647 | 1.4326 | 2.8254 | 8083.3659 | 0.71314 | 4121.588
401 | E-SOR-TOU-FC-ET-HC-R100 | 11 | 0.85 | 608.5346 | 0.4105 | 0.36503 | 0.53609 | 0.15701 | #NAME? | 281.125 | 281.125 | 1024.225 | 253.85 | 0 | 7569.1837 | 714.9528 | 488.7316 | 2.4129 | 44.7673 | 0.011361 | 1.385 | 2.8212 | 8083.3762 | 0.71732 | 4031.883
402 | E-SOR-TOU-FC-ET-HC-R100 | 9 | 0.7 | 651.062 | 0.43919 | 0.36642 | 0.44056 | 0.092042 | #NAME? | 282.35 | 282.35 | 1024.225 | 169.225 | 0 | 8312.3871 | 735.0181 | 488.6785 | 2.3849 | 45.7617 | 0.011075 | 1.334 | 2.8189 | 8082.5035 | 0.72114 | 3951.9961
403 | E-SOR-TOU-FC-ET-HC-R100 | 7 | 0.55 | 696.3752 | 0.46976 | 0.36694 | 0.32243 | 0.016659 | #NAME? | 284.65 | 284.65 | 1024.225 | 85.65 | 0 | 9200.0267 | 760.3732 | 488.6548 | 2.3556 | 48.1326 | 0.010735 | 1.2747 | 2.8217 | 8081.8547 | 0.726 | 3856.4153
404 | E-SOR-TOU-FC-ET-HC-R100 | 5 | 0.4 | 740.4156 | 0.49947 | 0.3676 | 0.15919 | -0.057495 | #NAME? | 285.2 | 285.2 | 1024.225 | 18.65 | 0 | 10200.5533 | 783.6989 | 488.6515 | 2.3635 | 54.1171 | 0.010439 | 1.2152 | 2.8214 | 8081.0415 | 0.73463 | 3689.3465
405 | E-SOR-TOU-FC-ET-HC-R100 | 13 | 0.65 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
406 | E-SOR-TOU-FC-ET-HC-R600 | 13 | 1 | 558.5142 | 0.37858 | 0.36812 | 0.61028 | 0.2436 | #NAME? | 335.25 | 335.25 | 1166.025 | 340.775 | 0 | 5119.3157 | 707.2515 | 527.1811 | 2.469 | 37.0246 | 0.0087732 | 1.4455 | 2.8647 | 5812.7991 | 0.68172 | 3940.2912
407 | E-SOR-TOU-FC-ET-HC-R600 | 11 | 0.85 | 599.3875 | 0.40628 | 0.37002 | 0.52381 | 0.17861 | #NAME? | 337.425 | 337.425 | 1166.025 | 255.1 | 0 | 5731.1819 | 725.755 | 527.0752 | 2.4354 | 37.3357 | 0.0085638 | 1.3915 | 2.8566 | 5812.4453 | 0.683 | 3906.863
408 | E-SOR-TOU-FC-ET-HC-R600 | 9 | 0.7 | 645.1777 | 0.43732 | 0.37164 | 0.43619 | 0.10725 | #NAME? | 338.925 | 338.925 | 1166.025 | 165.025 | 0 | 6378.3441 | 744.7946 | 527.1532 | 2.4067 | 38.0246 | 0.0083599 | 1.3404 | 2.8514 | 5811.8277 | 0.6895 | 3783.3864
409 | E-SOR-TOU-FC-ET-HC-R600 | 7 | 0.55 | 691.549 | 0.46875 | 0.37262 | 0.31642 | 0.022767 | #NAME? | 340.55 | 340.55 | 1166.025 | 79.9 | 0 | 7201.7301 | 766.9287 | 527.1027 | 2.3856 | 39.9439 | 0.0081354 | 1.2806 | 2.8501 | 5810.5433 | 0.69685 | 3650.716
410 | E-SOR-TOU-FC-ET-HC-R600 | 13 | 0.65 | 282.6165 | 0.19157 | 0.37234 | 0.15424 | -0.057798 | #NAME? | 341.325 | 341.325 | 1166.025 | 15.175 | 0 | 8160.4584 | 787.7663 | 527.1558 | 2.3973 | 44.8825 | 0.007936 | 1.2231 | 2.8586 | 5806.918 | 0.70965 | 3436.1941
411 | E-SOR-TOU-FC-ET-WC-OFF0 | 25.5 | 1.9 | 523.1272 | 0.35459 | 0.39479 | 0.81 | 0.79939 | 1 | 906.875 | 906.875 | 1821 | 617.775 | 38.4864 | 2154.0599 | 1029.2584 | 1422.0886 | 3.9711 | 65.4483 | 0.0056759 | 1.6539 | 2.7625 | 2342.7972 | 0.72327 | 4287.6157
412 | E-SOR-TOU-FC-ET-WC-OFF0 | 21.5 | 1.6 | 569.6088 | 0.3861 | 0.39814 | 0.73785 | 0.6988 | 1 | 921.825 | 921.825 | 1821 | 517 | 38.9089 | 3009.6941 | 1059.6321 | 1422.5392 | 3.8965 | 61.9392 | 0.0055133 | 1.5492 | 2.7616 | 2342.7972 | 0.72966 | 4124.4478
413 | E-SOR-TOU-FC-ET-WC-OFF0 | 18 | 1.35 | 614.6135 | 0.4166 | 0.40123 | 0.63425 | 0.61129 | 1 | 935.95 | 935.95 | 1821 | 417.825 | 39.352 | 4099.7963 | 1091.1267 | 1422.6153 | 3.8296 | 60.856 | 0.0053535 | 1.4486 | 2.7608 | 2342.7972 | 0.72957 | 4100.5613
414 | E-SOR-TOU-FC-ET-WC-OFF0 | 14 | 1.05 | 668.9567 | 0.45344 | 0.40422 | 0.49976 | 0.49122 | 1 | 949.2 | 949.2 | 1821 | 302.05 | 39.7426 | 5522.0614 | 1128.2484 | 1422.3979 | 3.7659 | 58.911 | 0.0051777 | 1.3325 | 2.7616 | 2342.7972 | 0.73879 | 3888.6829
415 | E-SOR-TOU-FC-ET-WC-OFF0 | 10 | 0.75 | 728.387 | 0.49372 | 0.40668 | 0.32924 | 0.32288 | 1 | 959.475 | 959.475 | 1821 | 189.8 | 40.0601 | 7357.4085 | 1169.0798 | 1422.6735 | 3.7282 | 58.3295 | 0.0049969 | 1.2112 | 2.7611 | 2342.7972 | 0.74766 | 3694.6485
416 | E-SOR-TOU-FC-ET-WC-OFF0 | 25.5 | 1.3 | 513.0228 | 0.34774 | 0.39466 | 0.79266 | 0.7504 | 1 | 907.425 | 907.425 | 1821 | 639.225 | 38.5155 | 2422.9561 | 1033.9868 | 1422.1098 | 3.97 | 63.8049 | 0.0056497 | 1.6137 | 2.7622 | 2342.7972 | 0.72289 | 4296.5333
417 | E-SOR-TOU-FC-ET-WC-OFF0 | 21.5 | 1.1 | 558.817 | 0.37878 | 0.39773 | 0.72014 | 0.65544 | 1 | 920.8 | 920.8 | 1821 | 540.65 | 38.8966 | 3268.7631 | 1063.0108 | 1422.3929 | 3.8989 | 61.2359 | 0.0054948 | 1.5145 | 2.7611 | 2342.7972 | 0.72879 | 4144.984
418 | E-SOR-TOU-FC-ET-WC-OFF0 | 18 | 0.9 | 601.5823 | 0.40777 | 0.40041 | 0.62196 | 0.56678 | 1 | 932.85 | 932.85 | 1821 | 445.7 | 39.264 | 4318.3866 | 1093.5401 | 1422.5725 | 3.837 | 60.088 | 0.0053421 | 1.4136 | 2.7613 | 2342.7972 | 0.73158 | 4065.6466
419 | E-SOR-TOU-FC-ET-WC-OFF0 | 14 | 0.7 | 655.5533 | 0.44435 | 0.40337 | 0.48134 | 0.43774 | 1 | 945.475 | 945.475 | 1821 | 326.35 | 39.6448 | 5816.2706 | 1130.981 | 1422.4279 | 3.7785 | 59.1442 | 0.0051652 | 1.3005 | 2.7616 | 2342.7972 | 0.73477 | 3976.8899
420 | E-SOR-TOU-FC-ET-WC-OFF | 10 | 0.5 | 716.6734 | 0.48578 | 0.40606 | 0.31646 | 0.28123 | 1 | 956.375 | 956.375 | 1821 | 214.875 | 39.977 | 7573.1385 | 1171.5496 | 1422.7654 | 3.7384 | 59.2048 | 0.004986 | 1.1886 | 2.7605 | 2342.7972 | 0.74346 | 3781.3231
421 | E-SOR-TOU-FC-ET-WC-OFF | 25.5 | 0.65 | 484.5488 | 0.32844 | 0.39377 | 0.73603 | 0.63127 | 1 | 904.7 | 904.7 | 1821 | 705.05 | 38.4547 | 3208.9561 | 1043.8583 | 1422.1636 | 3.9782 | 61.8132 | 0.0055957 | 1.5081 | 2.7616 | 2342.7972 | 0.72129 | 4338.1712
422 | E-SOR-TOU-FC-ET-WC-OFF | 21.5 | 0.55 | 528.1482 | 0.35799 | 0.39633 | 0.67504 | 0.52765 | 1 | 915.1 | 915.1 | 1821 | 612.525 | 38.7425 | 3975.1476 | 1070.4117 | 1422.3033 | 3.917 | 59.4355 | 0.0054571 | 1.4222 | 2.7615 | 2342.7972 | 0.72862 | 4160.296
423 | E-SOR-TOU-FC-ET-WC-OFF | 18 | 0.45 | 568.7416 | 0.38551 | 0.39888 | 0.5915 | 0.44461 | 1 | 925.675 | 925.675 | 1821 | 521.275 | 39.0524 | 4884.561 | 1098.9578 | 1422.1675 | 3.8559 | 58.5947 | 0.0053157 | 1.3366 | 2.7622 | 2342.7972 | 0.73502 | 4007.0548
424 | E-SOR-TOU-FC-ET-WC-OFF | 14 | 0.35 | 619.9229 | 0.4202 | 0.40185 | 0.46453 | 0.31378 | 1 | 937.975 | 937.975 | 1821 | 402.225 | 39.4388 | 6270.1061 | 1138.5691 | 1422.407 | 3.7897 | 58.2507 | 0.0051308 | 1.2278 | 2.7616 | 2342.7972 | 0.73917 | 3899.1165
425 | E-SOR-TOU-FC-ET-WC-OFF | 10 | 0.25 | 658.5441 | 0.44638 | 0.40423 | 0.29926 | -0.023415 | 1 | 947.1 | 947.1 | 1821 | 290.875 | 39.7187 | 8462.986 | 1185.2181 | 1422.5839 | 3.7593 | 67.3736 | 0.0049288 | 1.0983 | 2.7612 | 2342.7972 | 0.73087 | 4049.9869
426 | E-SOR-TOU-FC-ET-WC-R100 | 25.5 | 1.9 | 484.5426 | 0.32686 | 0.39518 | 0.72566 | 0.29353 | #NAME? | 411.575 | 411.575 | 1024.225 | 570.55 | 9.2649 | 11660.2774 | 657.8836 | 769.9366 | 5.9345 | 71.0775 | 0.023903 | 1.3767 | 2.7745 | 15740.821 | 0.81888 | 4349.8922
427 | E-SOR-TOU-FC-ET-WC-R100 | 21.5 | 1.6 | 524.9211 | 0.3541 | 0.39722 | 0.66796 | 0.23977 | #NAME? | 415.5 | 415.5 | 1024.225 | 465.7 | 9.3225 | 12729.3588 | 675.4901 | 770.0033 | 5.8281 | 71.1539 | 0.023332 | 1.328 | 2.776 | 15737.1231 | 0.81802 | 4370.2133
428 | E-SOR-TOU-FC-ET-WC-R100 | 18 | 1.35 | 566.2153 | 0.38196 | 0.39961 | 0.60426 | 0.19435 | #NAME? | 420 | 420 | 1024.225 | 366.225 | 9.3826 | 13698.8702 | 692.2391 | 770.0652 | 5.7131 | 71.3289 | 0.022803 | 1.2871 | 2.775 | 15727.5457 | 0.82086 | 4279.7946
429 | E-SOR-TOU-FC-ET-WC-R100 | 14 | 1.05 | 619.3828 | 0.41782 | 0.40168 | 0.50672 | 0.13587 | #NAME? | 424.3 | 424.3 | 1024.225 | 244.25 | 9.4501 | 15022.759 | 715.6036 | 770.1874 | 5.5833 | 71.9028 | 0.0221 | 1.2318 | 2.775 | 15711.2354 | 0.82618 | 4118.5417
430 | E-SOR-TOU-FC-ET-WC-R100 | 10 | 0.75 | 685.3236 | 0.4623 | 0.4038 | 0.39054 | 0.064762 | #NAME? | 428.275 | 428.275 | 1024.225 | 116.45 | 9.5079 | 16617.9341 | 743.1751 | 770.0964 | 5.4525 | 74.5137 | 0.021326 | 1.1733 | 2.7749 | 15694.9706 | 0.83243 | 3932.9585
431 | E-SOR-TOU-FC-ET-WC-R100 | 25.5 | 1.3 | 471.1485 | 0.31783 | 0.39562 | 0.70302 | 0.2675 | #NAME? | 413.225 | 413.225 | 1024.225 | 608.025 | 9.2933 | 12157.0871 | 656.9286 | 770.0848 | 5.9252 | 72.7214 | 0.023942 | 1.3715 | 2.7765 | 15744.3421 | 0.81374 | 4502.1815
432 | E-SOR-TOU-FC-ET-WC-R100 | 21.5 | 1.1 | 511.6664 | 0.34516 | 0.39771 | 0.64871 | 0.22473 | #NAME? | 416.675 | 416.675 | 1024.225 | 501.625 | 9.3407 | 13045.1802 | 673.975 | 770.0128 | 5.8197 | 72.2591 | 0.02338 | 1.325 | 2.7761 | 15737.0403 | 0.81678 | 4405.7072
433 | E-SOR-TOU-FC-ET-WC-R100 | 18 | 0.9 | 549.4937 | 0.37068 | 0.39975 | 0.58148 | 0.1787 | #NAME? | 420.525 | 420.525 | 1024.225 | 410.475 | 9.396 | 14041.7258 | 691.8902 | 770.0446 | 5.7128 | 72.2912 | 0.022813 | 1.2785 | 2.7756 | 15726.8434 | 0.81937 | 4323.0315
434 | E-SOR-TOU-FC-ET-WC-R100 | 14 | 0.7 | 601.7446 | 0.40592 | 0.40152 | 0.48217 | 0.1177 | #NAME? | 423.85 | 423.85 | 1024.225 | 285.5 | 9.4447 | 15415.2465 | 715.2239 | 770.1438 | 5.5977 | 73.366 | 0.022116 | 1.224 | 2.7746 | 15715.4507 | 0.82134 | 4259.272
435 | E-SOR-TOU-FC-ET-WC-R10 | 10 | 0.5 | 668.2666 | 0.4508 | 0.40343 | 0.34725 | 0.04587 | #NAME? | 427.425 | 427.425 | 1024.225 | 156.325 | 9.4969 | 17117.4776 | 744.5252 | 770.0818 | 5.4983 | 76.839 | 0.021296 | 1.1621 | 2.7743 | 15699.6149 | 0.82123 | 4254.7039
436 | E-SOR-TOU-FC-ET-WC-R10 | 25.5 | 0.65 | 433.6397 | 0.29252 | 0.39508 | 0.64156 | 0.21642 | #NAME? | 412.45 | 412.45 | 1024.225 | 710.9 | 9.2912 | 13210.53 | 662.5034 | 769.8949 | 5.9157 | 74.0373 | 0.023746 | 1.323 | 2.7752 | 15736.4054 | 0.81025 | 4604.9275
437 | E-SOR-TOU-FC-ET-WC-R10 | 21.5 | 0.55 | 465.3951 | 0.31395 | 0.39704 | 0.584 | 0.16223 | #NAME? | 415.65 | 415.65 | 1024.225 | 620.05 | 9.3281 | 14278.5183 | 681.1337 | 770.0162 | 5.8207 | 74.1974 | 0.023142 | 1.2717 | 2.7742 | 15727.9664 | 0.80854 | 4649.5009
438 | E-SOR-TOU-FC-ET-WC-R10 | 18 | 0.45 | 498.9709 | 0.33659 | 0.39867 | 0.5136 | 0.11588 | #NAME? | 418.5 | 418.5 | 1024.225 | 534.65 | 9.3688 | 15298.607 | 699.3097 | 770.0408 | 5.7358 | 74.7301 | 0.022582 | 1.2262 | 2.7749 | 15719.8877 | 0.80774 | 4667.9944
439 | E-SOR-TOU-FC-ET-WC-R10 | 14 | 0.35 | 539.8691 | 0.36418 | 0.40033 | 0.41041 | 0.042409 | #NAME? | 421.6 | 421.6 | 1024.225 | 420.725 | 9.4129 | 16872.8438 | 722.8083 | 770.0289 | 5.6444 | 78.201 | 0.021895 | 1.1737 | 2.7748 | 15708.7714 | 0.80163 | 4846.3366
440 | E-SOR-TOU-FC-ET-WC-R10 | 10 | 0.25 | 558.3658 | 0.37666 | 0.40147 | 0.24386 | -0.0616 | #NAME? | 423.625 | 423.625 | 1024.225 | 315.7 | 9.4422 | 19212.287 | 759.4585 | 770.0573 | 5.6048 | 88.7072 | 0.020909 | 1.0883 | 2.7751 | 15697.7068 | 0.78897 | 5232.6714
441 | E-SOR-TOU-FC-ET-WC-R600 | 25.5 | 1.9 | 473.1579 | 0.32072 | 0.39663 | 0.71945 | 0.34874 | #NAME? | 510.05 | 510.05 | 1166.025 | 579.45 | 11.6151 | 8066.4227 | 668.0398 | 868.467 | 5.7776 | 56.5591 | 0.017894 | 1.3599 | 2.8076 | 11220.3211 | 0.79603 | 4106.2517
442 | E-SOR-TOU-FC-ET-WC-R600 | 21.5 | 1.6 | 512.8404 | 0.34762 | 0.39919 | 0.66042 | 0.29034 | #NAME? | 516.025 | 516.025 | 1166.025 | 475.375 | 11.6999 | 8988.8941 | 685.5424 | 868.5697 | 5.6605 | 56.4926 | 0.017462 | 1.3105 | 2.8073 | 11209.5623 | 0.79862 | 4030.6374
443 | E-SOR-TOU-FC-ET-WC-R600 | 18 | 1.35 | 553.4076 | 0.37511 | 0.40084 | 0.58993 | 0.23214 | #NAME? | 520.075 | 520.075 | 1166.025 | 374.75 | 11.7595 | 9983.4939 | 702.9911 | 868.6619 | 5.562 | 56.8062 | 0.017055 | 1.2636 | 2.8075 | 11200.4461 | 0.80003 | 3988.4162
444 | E-SOR-TOU-FC-ET-WC-R600 | 14 | 1.05 | 611.3989 | 0.41442 | 0.40292 | 0.49042 | 0.16394 | #NAME? | 524.7 | 524.7 | 1166.025 | 240.8 | 11.8323 | 11245.6228 | 725.1425 | 868.6878 | 5.4446 | 57.6787 | 0.016557 | 1.212 | 2.8057 | 11186.3067 | 0.80357 | 3890.3639
445 | E-SOR-TOU-FC-ET-WC-R600 | 10 | 0.75 | 678.1457 | 0.45967 | 0.40456 | 0.36489 | 0.087197 | #NAME? | 529.15 | 529.15 | 1166.025 | 112.875 | 11.9048 | 12736.5082 | 752.4702 | 868.7466 | 5.3348 | 59.3304 | 0.015963 | 1.1499 | 2.8074 | 11151.3261 | 0.81279 | 3653.9565
446 | E-SOR-TOU-FC-ET-WC-R600 | 25.5 | 1.3 | 458.9001 | 0.31106 | 0.39665 | 0.69245 | 0.31322 | #NAME? | 510.825 | 510.825 | 1166.025 | 617.725 | 11.634 | 8581.6708 | 667.613 | 868.4307 | 5.7763 | 57.9096 | 0.017904 | 1.3497 | 2.8083 | 11219.9735 | 0.79009 | 4257.6541
447 | E-SOR-TOU-FC-ET-WC-R600 | 21.5 | 1.1 | 498.2235 | 0.33771 | 0.39887 | 0.63365 | 0.25771 | #NAME? | 515.6 | 515.6 | 1166.025 | 512.975 | 11.6919 | 9476.2558 | 684.438 | 868.4692 | 5.6716 | 57.8846 | 0.01749 | 1.3021 | 2.8076 | 11211.1628 | 0.79203 | 4198.5668
448 | E-SOR-TOU-FC-ET-WC-R600 | 18 | 0.9 | 538.1596 | 0.36478 | 0.40073 | 0.5665 | 0.20483 | #NAME? | 519.75 | 519.75 | 1166.025 | 414.1 | 11.7579 | 10396.8675 | 702.2867 | 868.5321 | 5.5736 | 57.9867 | 0.017072 | 1.255 | 2.8076 | 11201.9398 | 0.7946 | 4125.2834
449 | E-SOR-TOU-FC-ET-WC-R600 | 14 | 0.7 | 594.8179 | 0.40318 | 0.40265 | 0.46747 | 0.14019 | #NAME? | 524 | 524 | 1166.025 | 279 | 11.8191 | 11621.7539 | 724.7919 | 868.6823 | 5.4633 | 58.86 | 0.016565 | 1.203 | 2.8061 | 11186.2882 | 0.79796 | 4030.5296
450 | E-SOR-TOU-FC-ET-WC-R60 | 10 | 0.5 | 662.3678 | 0.44897 | 0.40412 | 0.33215 | 0.072061 | #NAME? | 527.95 | 527.95 | 1166.025 | 150.275 | 11.8812 | 13091.5447 | 754.0313 | 868.6203 | 5.3673 | 60.3533 | 0.015932 | 1.1374 | 2.8077 | 11151.0056 | 0.80488 | 3846.8454
451 | E-SOR-TOU-FC-ET-WC-R60 | 25.5 | 0.65 | 423.6065 | 0.28713 | 0.3959 | 0.62257 | 0.24844 | #NAME? | 509.675 | 509.675 | 1166.025 | 714.675 | 11.6237 | 9653.9821 | 670.428 | 868.5036 | 5.777 | 59.7664 | 0.01783 | 1.3075 | 2.8082 | 11215.6057 | 0.78368 | 4425.0123
452 | E-SOR-TOU-FC-ET-WC-R60 | 21.5 | 0.55 | 458.4795 | 0.31077 | 0.39778 | 0.56897 | 0.19265 | #NAME? | 513.325 | 513.325 | 1166.025 | 619.2 | 11.671 | 10515.627 | 687.8657 | 868.4075 | 5.686 | 59.5532 | 0.017401 | 1.2586 | 2.8073 | 11204.4291 | 0.78511 | 4377.964
453 | E-SOR-TOU-FC-ET-WC-R60 | 18 | 0.45 | 495.0771 | 0.33558 | 0.39941 | 0.49534 | 0.14471 | #NAME? | 516.575 | 516.575 | 1166.025 | 529.775 | 11.713 | 11424.922 | 707.4904 | 868.6104 | 5.5996 | 59.5346 | 0.016939 | 1.2074 | 2.8062 | 11189.1549 | 0.78478 | 4376.725
454 | E-SOR-TOU-FC-ET-WC-R60 | 14 | 0.35 | 539.1445 | 0.36545 | 0.40113 | 0.39289 | 0.064476 | #NAME? | 520.725 | 520.725 | 1166.025 | 409.4 | 11.7735 | 12814.765 | 731.1264 | 868.481 | 5.512 | 61.6024 | 0.016406 | 1.1532 | 2.8075 | 11163.7698 | 0.78157 | 4447.7716
455 | E-SOR-TOU-FC-ET-WC-R60 | 10 | 0.25 | 555.1996 | 0.37633 | 0.40215 | 0.22659 | -0.066057 | #NAME? | 522.775 | 522.775 | 1166.025 | 309.175 | 11.8055 | 15084.7626 | 767.1118 | 868.5659 | 5.4792 | 69.0418 | 0.015665 | 1.0618 | 2.8064 | 11137.9774 | 0.76931 | 4760.7812
456 | E-SOR-TOU-FC-FP-HC-OFF0 | 13 | 1 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
457 | E-SOR-TOU-FC-FP-HC-OFF0 | 11 | 0.85 | 481.2887 | 0.32623 | 0.36817 | 0.34417 | 0.22583 | 1 | 633.025 | 633.025 | 1821 | 73.05 | 0 | 4085.0278 | 910.2844 | 784.7657 | 2.4618 | 48.7471 | 0.0032599 | 1.468 | 2.8205 | 1192.337 | 0.64117 | 3365.528
458 | E-SOR-TOU-FC-FP-HC-OFF0 | 9 | 0.7 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
459 | E-SOR-TOU-FC-FP-HC-R100 | 13 | 1 | 497.8714 | 0.33585 | 0.36465 | 0.51597 | 0.17955 | #NAME? | 281.4 | 281.4 | 1024.225 | 149.125 | 0 | 7463.4665 | 703.1232 | 488.7086 | 2.4175 | 44.9316 | 0.011541 | 1.3981 | 2.835 | 8083.4297 | 0.73507 | 3692.0206
460 | E-SOR-TOU-FC-FP-HC-R100 | 11 | 0.85 | 532.2702 | 0.35906 | 0.36606 | 0.43977 | 0.13098 | #NAME? | 282.5 | 282.5 | 1024.225 | 109.575 | 0 | 8030.2466 | 717.4635 | 488.7391 | 2.3958 | 45.4333 | 0.011327 | 1.3573 | 2.828 | 8082.7969 | 0.73674 | 3655.4556
461 | E-SOR-TOU-FC-FP-HC-R100 | 9 | 0.7 | 568.1468 | 0.38326 | 0.36725 | 0.35646 | 0.070303 | #NAME? | 283.625 | 283.625 | 1024.225 | 73.5 | 0 | 8706.8913 | 734.3271 | 488.8091 | 2.3764 | 46.62 | 0.011085 | 1.3111 | 2.8234 | 8082.0018 | 0.73943 | 3601.1135
462 | E-SOR-TOU-FC-FP-HC-R100 | 7 | 0.55 | 607.7849 | 0.41 | 0.36776 | 0.25756 | -0.0037823 | #NAME? | 284.775 | 284.775 | 1024.225 | 39.675 | 0 | 9532.0762 | 755.0358 | 488.7078 | 2.3641 | 49.517 | 0.010807 | 1.257 | 2.8273 | 8081.8824 | 0.74117 | 3568.4306
463 | E-SOR-TOU-FC-FP-HC-R100 | 5 | 0.4 | 666.8596 | 0.44985 | 0.36774 | 0.1153 | -0.064575 | #NAME? | 285.675 | 285.675 | 1024.225 | 6.9 | 0 | 10378.8964 | 776.8219 | 488.7334 | 2.3768 | 55.4995 | 0.010526 | 1.2079 | 2.8281 | 8080.7789 | 0.74512 | 3495.243
464 | E-SOR-TOU-FC-FP-HC-R100 | 13 | 0.65 | 472.7706 | 0.31892 | 0.36441 | 0.48155 | 0.13351 | #NAME? | 281 | 281 | 1024.225 | 182.675 | 0 | 7901.4048 | 707.3621 | 488.6412 | 2.4189 | 45.8732 | 0.011476 | 1.37 | 2.8315 | 8083.1002 | 0.72908 | 3805.7353
465 | E-SOR-TOU-FC-FP-HC-R100 | 11 | 0.55 | 500.2695 | 0.33747 | 0.36584 | 0.41308 | 0.074308 | #NAME? | 281.65 | 281.65 | 1024.225 | 144.075 | 0 | 8527.4315 | 722.9743 | 488.7878 | 2.403 | 46.7522 | 0.011248 | 1.3238 | 2.828 | 8082.7294 | 0.72923 | 3799.045
466 | E-SOR-TOU-FC-FP-HC-R100 | 9 | 0.45 | 549.4872 | 0.37067 | 0.36653 | 0.32479 | 0.039253 | #NAME? | 282.55 | 282.55 | 1024.225 | 105.8 | 0 | 9032.4084 | 742.1261 | 488.7787 | 2.3861 | 47.2773 | 0.010981 | 1.2811 | 2.8301 | 8082.4703 | 0.73177 | 3749.2561
467 | E-SOR-TOU-FC-FP-HC-R100 | 7 | 0.35 | 574.8133 | 0.38776 | 0.36711 | 0.19384 | -0.046574 | #NAME? | 283.6 | 283.6 | 1024.225 | 62.65 | 0 | 10032.9585 | 762.4694 | 488.762 | 2.3866 | 52.3169 | 0.010711 | 1.2281 | 2.8309 | 8081.8591 | 0.72742 | 3831.599
468 | E-SOR-TOU-FC-FP-HC-R10 | 5 | 0.25 | 500.2459 | 0.33745 | 0.36661 | -0.033294 | -0.20163 | #NAME? | 284.35 | 284.35 | 1024.225 | 25.625 | 0 | 11819.4105 | 777.339 | 488.6894 | 2.4568 | 77.7464 | 0.010521 | 1.1347 | 2.8292 | 8081.4241 | 0.71405 | 4094.9418
469 | E-SOR-TOU-FC-FP-HC-R10 | 13 | 0.35 | 418.1133 | 0.28205 | 0.3638 | 0.38433 | 0.031865 | #NAME? | 278.925 | 278.925 | 1024.225 | 259.75 | 0 | 8932.3144 | 723.1465 | 488.6642 | 2.4334 | 47.8339 | 0.011246 | 1.2923 | 2.8316 | 8082.9471 | 0.71308 | 4122.3646
470 | E-SOR-TOU-FC-FP-HC-R10 | 11 | 0.3 | 432.66 | 0.29186 | 0.36413 | 0.30106 | -0.047601 | #NAME? | 280.475 | 280.475 | 1024.225 | 221.35 | 0 | 9758.1716 | 740.6672 | 488.7409 | 2.4202 | 50.9711 | 0.011003 | 1.2467 | 2.836 | 8082.6277 | 0.70585 | 4270.3394
471 | E-SOR-TOU-FC-FP-HC-R10 | 7 | 0.2 | 506.3901 | 0.3416 | 0.36487 | 0.13694 | -0.15293 | #NAME? | 280.85 | 280.85 | 1024.225 | 196.475 | 0 | 10995.4002 | 750.1857 | 488.725 | 2.4329 | 57.7468 | 0.010873 | 1.1744 | 2.832 | 8082.4247 | 0.70421 | 4300.8738
472 | E-SOR-TOU-FC-FP-HC-R600 | 13 | 1 | 482.2764 | 0.3269 | 0.36981 | 0.50671 | 0.20294 | #NAME? | 337.075 | 337.075 | 1166.025 | 144.725 | 0 | 5674.0309 | 712.5253 | 527.1784 | 2.4423 | 37.6657 | 0.0087142 | 1.4016 | 2.8664 | 5812.5846 | 0.70573 | 3514.6858
473 | E-SOR-TOU-FC-FP-HC-R600 | 11 | 0.85 | 518.0577 | 0.35115 | 0.37073 | 0.4385 | 0.14664 | #NAME? | 339.55 | 339.55 | 1166.025 | 104.45 | 0 | 6183.4441 | 727.9298 | 527.1338 | 2.4151 | 37.983 | 0.0085427 | 1.3583 | 2.863 | 5812.0191 | 0.7085 | 3463.6607
474 | E-SOR-TOU-FC-FP-HC-R600 | 9 | 0.7 | 557.1692 | 0.37766 | 0.37182 | 0.36007 | 0.079007 | #NAME? | 340.425 | 340.425 | 1166.025 | 67.875 | 0 | 6782.1941 | 743.6653 | 527.0806 | 2.3977 | 38.8459 | 0.0083739 | 1.3121 | 2.8602 | 5811.007 | 0.71264 | 3389.9091
475 | E-SOR-TOU-FC-FP-HC-R600 | 7 | 0.55 | 599.2383 | 0.40618 | 0.3725 | 0.26184 | 0.00038514 | #NAME? | 341.6 | 341.6 | 1166.025 | 35.6 | 0 | 7503.347 | 760.5276 | 527.066 | 2.3864 | 41.0434 | 0.0081997 | 1.2623 | 2.8578 | 5809.0971 | 0.71789 | 3300.0892
476 | E-SOR-TOU-FC-FP-HC-R600 | 5 | 0.4 | 658.2499 | 0.44618 | 0.3726 | 0.11834 | -0.065917 | #NAME? | 341.1 | 341.1 | 1166.025 | 5.175 | 0 | 8320.6507 | 778.4015 | 527.113 | 2.409 | 46.0203 | 0.008023 | 1.2163 | 2.8584 | 5806.204 | 0.72299 | 3216.6363
477 | E-SOR-TOU-FC-FP-HC-R600 | 13 | 0.65 | 459.6372 | 0.31155 | 0.36914 | 0.47684 | 0.14422 | #NAME? | 337 | 337 | 1166.025 | 176.775 | 0 | 6073.5119 | 717.7946 | 527.1227 | 2.4451 | 38.1871 | 0.0086568 | 1.368 | 2.8686 | 5812.941 | 0.70013 | 3613.1074
478 | E-SOR-TOU-FC-FP-HC-R600 | 11 | 0.55 | 489.5904 | 0.33186 | 0.37029 | 0.40865 | 0.081042 | #NAME? | 338.1 | 338.1 | 1166.025 | 138.65 | 0 | 6615.4746 | 732.2641 | 527.1247 | 2.4258 | 38.7706 | 0.0084965 | 1.3227 | 2.8637 | 5812.0316 | 0.70179 | 3578.8433
479 | E-SOR-TOU-FC-FP-HC-R600 | 9 | 0.45 | 539.1015 | 0.36542 | 0.37146 | 0.31523 | 0.050082 | #NAME? | 339.15 | 339.15 | 1166.025 | 102.55 | 0 | 7080.1975 | 747.2438 | 527.1486 | 2.4091 | 39.6035 | 0.0083358 | 1.2899 | 2.8578 | 5810.5491 | 0.70459 | 3524.8174
480 | E-SOR-TOU-FC-FP-HC-R600 | 7 | 0.35 | 565.2245 | 0.38312 | 0.37172 | 0.18988 | -0.049995 | #NAME? | 340.4 | 340.4 | 1166.025 | 59.85 | 0 | 8006.7615 | 767.3616 | 527.162 | 2.4093 | 43.4146 | 0.0081335 | 1.2316 | 2.8603 | 5808.921 | 0.70266 | 3557.1351
481 | E-SOR-TOU-FC-FP-HC-R60 | 5 | 0.25 | 494.512 | 0.33519 | 0.37163 | -0.025026 | -0.23866 | #NAME? | 340.05 | 340.05 | 1166.025 | 24.025 | 0 | 9683.1133 | 780.2479 | 527.0673 | 2.486 | 62.9183 | 0.0080087 | 1.1307 | 2.863 | 5807.4873 | 0.69162 | 3748.5467
482 | E-SOR-TOU-FC-FP-HC-R60 | 13 | 0.35 | 410.4654 | 0.27822 | 0.36818 | 0.37727 | 0.036552 | #NAME? | 335.375 | 335.375 | 1166.025 | 251.775 | 0 | 6954.3704 | 729.0434 | 527.1165 | 2.453 | 39.7358 | 0.0085308 | 1.2993 | 2.8633 | 5812.0467 | 0.68645 | 3853.6806
483 | E-SOR-TOU-FC-FP-HC-R60 | 11 | 0.3 | 426.015 | 0.28876 | 0.36891 | 0.2906 | -0.050637 | #NAME? | 336.2 | 336.2 | 1166.025 | 214.6 | 0 | 7682.9529 | 743.9052 | 527.0965 | 2.4455 | 41.9627 | 0.0083727 | 1.2533 | 2.8626 | 5811.1069 | 0.68152 | 3939.3742
484 | E-SOR-TOU-FC-FP-HC-R60 | 7 | 0.2 | 503.6638 | 0.3414 | 0.36949 | 0.13959 | -0.1817 | #NAME? | 336.075 | 336.075 | 1166.025 | 183.6 | 0 | 8853.0089 | 753.4695 | 527.1111 | 2.4622 | 46.9503 | 0.0082744 | 1.1737 | 2.8637 | 5810.331 | 0.68069 | 3952.6885
485 | E-SOR-TOU-FC-FP-WC-OFF0 | 25.5 | 1.9 | 391.8045 | 0.26558 | 0.39958 | 0.5918 | 0.61237 | 1 | 1341.125 | 931.625 | 1821 | 219.3 | 23.6743 | 4482.6084 | 779.7742 | 1422.5344 | 5.7419 | 61.3117 | 0.0074916 | 1.4335 | 2.7614 | 2342.7972 | 0.76688 | 3374.1229
486 | E-SOR-TOU-FC-FP-WC-OFF0 | 21.5 | 1.6 | 418.0926 | 0.28339 | 0.40127 | 0.51631 | 0.53529 | 1 | 1422.4 | 939.15 | 1821 | 177.25 | 23.8114 | 5306.3931 | 796.158 | 1422.5881 | 5.6905 | 60.122 | 0.0073375 | 1.3616 | 2.7613 | 2342.7972 | 0.77386 | 3232.7059
487 | E-SOR-TOU-FC-FP-WC-OFF0 | 18 | 1.35 | 444.0489 | 0.30099 | 0.40261 | 0.43262 | 0.46807 | 1 | 1511.3 | 945.525 | 1821 | 136.65 | 23.9237 | 6177.1996 | 813.7476 | 1422.516 | 5.6488 | 59.0367 | 0.0071788 | 1.2936 | 2.7614 | 2342.7972 | 0.77865 | 3136.5264
488 | E-SOR-TOU-FC-FP-WC-OFF0 | 14 | 1.05 | 477.4291 | 0.32361 | 0.40407 | 0.33596 | 0.37066 | 1 | 1605.95 | 951.775 | 1821 | 89.925 | 24.0353 | 7224.2751 | 835.2252 | 1422.613 | 5.6035 | 57.6321 | 0.006994 | 1.2181 | 2.761 | 2342.7972 | 0.79102 | 2906.5652
489 | E-SOR-TOU-FC-FP-WC-OFF0 | 10 | 0.75 | 516.8873 | 0.35036 | 0.40527 | 0.21949 | 0.22294 | 1 | 1701.075 | 956.725 | 1821 | 45.95 | 24.1243 | 8559.3678 | 860.2255 | 1422.7027 | 5.5983 | 58.8107 | 0.0067911 | 1.138 | 2.7611 | 2342.7972 | 0.79957 | 2751.4976
490 | E-SOR-TOU-FC-FP-WC-OFF0 | 25.5 | 1.3 | 379.7579 | 0.25741 | 0.39886 | 0.56857 | 0.5708 | 1 | 1363.475 | 929.175 | 1821 | 238.65 | 23.6488 | 4790.1772 | 784.4161 | 1422.4876 | 5.7447 | 60.8315 | 0.0074472 | 1.3968 | 2.7615 | 2342.7972 | 0.76793 | 3358.9524
491 | E-SOR-TOU-FC-FP-WC-OFF0 | 21.5 | 1.1 | 405.6368 | 0.27495 | 0.40063 | 0.49228 | 0.49221 | 1 | 1436.55 | 936.525 | 1821 | 195.975 | 23.7704 | 5623.9101 | 800.3031 | 1422.3786 | 5.7005 | 60.1067 | 0.0072995 | 1.3311 | 2.7617 | 2342.7972 | 0.77214 | 3268.6968
492 | E-SOR-TOU-FC-FP-WC-OFF0 | 18 | 0.9 | 429.9141 | 0.29141 | 0.40199 | 0.41879 | 0.42318 | 1 | 1516.475 | 942.575 | 1821 | 156.75 | 23.8787 | 6410.2814 | 817.7629 | 1422.609 | 5.6509 | 58.9006 | 0.0071436 | 1.266 | 2.7612 | 2342.7972 | 0.78077 | 3101.8822
493 | E-SOR-TOU-FC-FP-WC-OFF0 | 14 | 0.7 | 461.9111 | 0.3131 | 0.40355 | 0.32254 | 0.30585 | 1 | 1611.225 | 949.35 | 1821 | 107.2 | 23.9957 | 7500.2519 | 840.0974 | 1422.6524 | 5.6101 | 58.6734 | 0.0069537 | 1.1906 | 2.7611 | 2342.7972 | 0.78853 | 2953.6343
494 | E-SOR-TOU-FC-FP-WC-OFF | 10 | 0.5 | 506.9016 | 0.34359 | 0.40489 | 0.20462 | 0.18245 | 1 | 1703.725 | 954.875 | 1821 | 64.225 | 24.0946 | 8788.991 | 866.0116 | 1422.5151 | 5.6112 | 60.3245 | 0.0067457 | 1.1184 | 2.7615 | 2342.7972 | 0.79266 | 2873.2523
495 | E-SOR-TOU-FC-FP-WC-OFF | 25.5 | 0.65 | 349.3393 | 0.23679 | 0.39743 | 0.50864 | 0.43364 | 1 | 1393.9 | 923.2 | 1821 | 290.8 | 23.5597 | 5652.7444 | 795.6237 | 1422.1882 | 5.7656 | 60.5425 | 0.0073423 | 1.3129 | 2.7621 | 2342.7972 | 0.76552 | 3414.2478
496 | E-SOR-TOU-FC-FP-WC-OFF | 21.5 | 0.55 | 372.6891 | 0.25262 | 0.39924 | 0.44322 | 0.34447 | 1 | 1468.675 | 930.625 | 1821 | 247.825 | 23.6815 | 6415.4185 | 812.4501 | 1422.3049 | 5.7156 | 60.3021 | 0.0071903 | 1.2504 | 2.7619 | 2342.7972 | 0.7698 | 3321.3607
497 | E-SOR-TOU-FC-FP-WC-OFF | 18 | 0.45 | 398.8405 | 0.27034 | 0.4007 | 0.36958 | 0.29374 | 1 | 1540.775 | 936.8 | 1821 | 206.275 | 23.7855 | 7159.3927 | 828.8935 | 1422.418 | 5.6775 | 60.2749 | 0.0070475 | 1.2023 | 2.7615 | 2342.7972 | 0.77237 | 3263.8755
498 | E-SOR-TOU-FC-FP-WC-OFF | 14 | 0.35 | 424.8771 | 0.28799 | 0.4023 | 0.28156 | 0.17302 | 1 | 1624.6 | 943.125 | 1821 | 152.975 | 23.8995 | 8185.9924 | 853.3918 | 1422.5294 | 5.6295 | 61.1641 | 0.0068453 | 1.1247 | 2.7613 | 2342.7972 | 0.78109 | 3094.0988
499 | E-SOR-TOU-FC-FP-WC-OFF | 10 | 0.25 | 415.0329 | 0.28132 | 0.40366 | 0.16217 | -0.10786 | 1 | 1705.075 | 948.625 | 1821 | 108.6 | 23.9966 | 9857.523 | 875.8302 | 1422.7466 | 5.6541 | 78.6916 | 0.0066698 | 1.0277 | 2.7608 | 2342.7972 | 0.78602 | 2997.4394
500 | E-SOR-TOU-FC-FP-WC-R100 | 25.5 | 1.9 | 434.532 | 0.29313 | 0.39788 | 0.64721 | 0.26349 | #NAME? | 417.25 | 417.25 | 1024.225 | 283.675 | 9.3483 | 12489.1826 | 674.4926 | 770.0195 | 5.7865 | 70.1096 | 0.023361 | 1.3366 | 2.7769 | 15734.6066 | 0.83316 | 3932.48
501 | E-SOR-TOU-FC-FP-WC-R100 | 21.5 | 1.6 | 468.1707 | 0.31582 | 0.39986 | 0.58744 | 0.21676 | #NAME? | 420.625 | 420.625 | 1024.225 | 230.05 | 9.3939 | 13458.8449 | 687.3213 | 770.0287 | 5.7056 | 70.6117 | 0.02295 | 1.2958 | 2.7755 | 15726.1183 | 0.83349 | 3917.021
502 | E-SOR-TOU-FC-FP-WC-R100 | 18 | 1.35 | 503.5625 | 0.33969 | 0.40143 | 0.52702 | 0.17327 | #NAME? | 423.95 | 423.95 | 1024.225 | 174.95 | 9.4435 | 14382.6716 | 700.4517 | 770.0937 | 5.6277 | 71.2369 | 0.022543 | 1.2595 | 2.7758 | 15715.0285 | 0.83517 | 3864.6526
503 | E-SOR-TOU-FC-FP-WC-R100 | 14 | 1.05 | 550.8485 | 0.37159 | 0.4028 | 0.44358 | 0.11923 | #NAME? | 426.225 | 426.225 | 1024.225 | 106.675 | 9.4744 | 15571.5168 | 719.1078 | 770.1924 | 5.5383 | 72.1278 | 0.021989 | 1.2107 | 2.7738 | 15701.7745 | 0.83981 | 3729.7816
504 | E-SOR-TOU-FC-FP-WC-R100 | 10 | 0.75 | 609.7094 | 0.4113 | 0.4043 | 0.34265 | 0.052543 | #NAME? | 429.275 | 429.275 | 1024.225 | 51.175 | 9.5222 | 17025.9266 | 740.6942 | 770.1606 | 5.4458 | 75.3993 | 0.021379 | 1.1593 | 2.7739 | 15684.8241 | 0.84428 | 3600.6912
505 | E-SOR-TOU-FC-FP-WC-R100 | 25.5 | 1.3 | 417.4234 | 0.28158 | 0.39817 | 0.62279 | 0.23497 | #NAME? | 418 | 418 | 1024.225 | 310.525 | 9.355 | 13026.7906 | 674.6678 | 770.0045 | 5.7742 | 71.6122 | 0.023354 | 1.3291 | 2.7762 | 15734.3019 | 0.82941 | 4038.09
506 | E-SOR-TOU-FC-FP-WC-R100 | 21.5 | 1.1 | 449.9989 | 0.30356 | 0.39991 | 0.56467 | 0.19437 | #NAME? | 421.1 | 421.1 | 1024.225 | 252.725 | 9.4026 | 13899.3337 | 688.1985 | 770.0585 | 5.6988 | 71.7248 | 0.022922 | 1.2863 | 2.7765 | 15724.5954 | 0.83172 | 3967.1043
507 | E-SOR-TOU-FC-FP-WC-R100 | 18 | 0.9 | 480.7307 | 0.32429 | 0.40108 | 0.50377 | 0.15103 | #NAME? | 423.25 | 423.25 | 1024.225 | 199.1 | 9.4379 | 14826.4424 | 702.5958 | 770.0561 | 5.629 | 72.1171 | 0.022481 | 1.2437 | 2.7763 | 15715.9839 | 0.83421 | 3892.5722
508 | E-SOR-TOU-FC-FP-WC-R100 | 14 | 0.7 | 524.277 | 0.35367 | 0.40255 | 0.41918 | 0.091384 | #NAME? | 425.8 | 425.8 | 1024.225 | 134.2 | 9.4688 | 16103.4226 | 721.0542 | 769.9715 | 5.5473 | 74.0444 | 0.021939 | 1.1962 | 2.7753 | 15705.0285 | 0.83435 | 3883.4201
509 | E-SOR-TOU-FC-FP-WC-R10 | 10 | 0.5 | 588.6628 | 0.3971 | 0.40392 | 0.29248 | 0.031224 | #NAME? | 428.575 | 428.575 | 1024.225 | 74.075 | 9.5125 | 17597.1448 | 743.7462 | 770.1837 | 5.4981 | 78.1849 | 0.021305 | 1.1461 | 2.7744 | 15690.119 | 0.83173 | 3951.6814
510 | E-SOR-TOU-FC-FP-WC-R10 | 25.5 | 0.65 | 368.7213 | 0.24873 | 0.39771 | 0.55541 | 0.16578 | #NAME? | 417.375 | 417.375 | 1024.225 | 387.5 | 9.35 | 14369.362 | 684.5525 | 770.0757 | 5.7545 | 73.3657 | 0.023032 | 1.2697 | 2.7751 | 15724.2338 | 0.82562 | 4145.2443
511 | E-SOR-TOU-FC-FP-WC-R10 | 21.5 | 0.55 | 392.8464 | 0.26501 | 0.39902 | 0.50399 | 0.11367 | #NAME? | 419.3 | 419.3 | 1024.225 | 329.8 | 9.3783 | 15375.955 | 697.4992 | 770.0151 | 5.6964 | 74.6927 | 0.022632 | 1.2283 | 2.7743 | 15717.4915 | 0.82299 | 4216.7257
512 | E-SOR-TOU-FC-FP-WC-R10 | 18 | 0.45 | 425.1427 | 0.28679 | 0.40018 | 0.43079 | 0.079351 | #NAME? | 421.5 | 421.5 | 1024.225 | 283.575 | 9.4082 | 16236.4772 | 712.7473 | 770.0845 | 5.6436 | 75.6858 | 0.02218 | 1.1924 | 2.775 | 15710.1826 | 0.81997 | 4300.8601
513 | E-SOR-TOU-FC-FP-WC-R10 | 14 | 0.35 | 449.9296 | 0.30351 | 0.40152 | 0.33076 | 0.014448 | #NAME? | 424.025 | 424.025 | 1024.225 | 224.975 | 9.4453 | 17668.7097 | 731.261 | 770.0683 | 5.5883 | 80.1665 | 0.02165 | 1.1451 | 2.7751 | 15698.2543 | 0.81624 | 4404.3046
514 | E-SOR-TOU-FC-FP-WC-R10 | 10 | 0.25 | 410.2536 | 0.27675 | 0.40251 | 0.16163 | -0.094021 | #NAME? | 425.75 | 425.75 | 1024.225 | 174.45 | 9.47 | 20078.153 | 745.003 | 770.024 | 5.6458 | 97.1796 | 0.021264 | 1.0669 | 2.7757 | 15683.0572 | 0.80805 | 4641.44
515 | E-SOR-TOU-FC-FP-WC-R600 | 25.5 | 1.9 | 416.4094 | 0.28225 | 0.39959 | 0.63288 | 0.30774 | #NAME? | 517.2 | 517.2 | 1166.025 | 281.075 | 11.7198 | 8994.3155 | 684.014 | 868.5618 | 5.6205 | 56.4112 | 0.017496 | 1.3127 | 2.8065 | 11208.4205 | 0.81462 | 3635.8174
516 | E-SOR-TOU-FC-FP-WC-R600 | 21.5 | 1.6 | 450.0556 | 0.30506 | 0.40106 | 0.57483 | 0.25562 | #NAME? | 520.575 | 520.575 | 1166.025 | 223.225 | 11.7686 | 9851.2761 | 697.085 | 868.6344 | 5.5482 | 56.6172 | 0.017184 | 1.2703 | 2.8067 | 11199.0154 | 0.81684 | 3576.556
517 | E-SOR-TOU-FC-FP-WC-R600 | 18 | 1.35 | 485.4859 | 0.32908 | 0.40241 | 0.51074 | 0.20416 | #NAME? | 523.8 | 523.8 | 1166.025 | 169.525 | 11.8142 | 10735.7698 | 710.4513 | 868.7655 | 5.4813 | 57.1397 | 0.016873 | 1.2313 | 2.8064 | 11186.968 | 0.81765 | 3551.2193
518 | E-SOR-TOU-FC-FP-WC-R600 | 14 | 1.05 | 536.2204 | 0.36346 | 0.40374 | 0.42811 | 0.14272 | #NAME? | 526.75 | 526.75 | 1166.025 | 99.775 | 11.8593 | 11822.1127 | 727.4798 | 868.6382 | 5.4017 | 58.0833 | 0.016483 | 1.1881 | 2.8059 | 11165.8816 | 0.8218 | 3444.4098
519 | E-SOR-TOU-FC-FP-WC-R600 | 10 | 0.75 | 597.2685 | 0.40484 | 0.40489 | 0.32185 | 0.070533 | #NAME? | 529.775 | 529.775 | 1166.025 | 47.225 | 11.9126 | 13145.4988 | 748.2358 | 868.7473 | 5.3303 | 60.1908 | 0.016018 | 1.1351 | 2.8067 | 11129.1598 | 0.82837 | 3281.3357
520 | E-SOR-TOU-FC-FP-WC-R600 | 25.5 | 1.3 | 398.9156 | 0.2704 | 0.39932 | 0.6069 | 0.26606 | #NAME? | 517.225 | 517.225 | 1166.025 | 311.8 | 11.7227 | 9562.3897 | 685.9974 | 868.4643 | 5.6208 | 57.4345 | 0.017449 | 1.2952 | 2.8078 | 11207.73 | 0.80978 | 3753.8604
521 | E-SOR-TOU-FC-FP-WC-R600 | 21.5 | 1.1 | 432.7583 | 0.29334 | 0.40085 | 0.55148 | 0.21905 | #NAME? | 520.2 | 520.2 | 1166.025 | 251.075 | 11.7604 | 10351.6939 | 698.3949 | 868.6719 | 5.5534 | 57.7008 | 0.017152 | 1.2567 | 2.8062 | 11197.6834 | 0.81153 | 3704.5408
522 | E-SOR-TOU-FC-FP-WC-R600 | 18 | 0.9 | 465.9511 | 0.31583 | 0.40212 | 0.48952 | 0.17159 | #NAME? | 523.175 | 523.175 | 1166.025 | 194.7 | 11.8047 | 11184.6895 | 711.4628 | 868.6284 | 5.4889 | 58.2217 | 0.016849 | 1.2192 | 2.8069 | 11185.4734 | 0.81367 | 3646.7688
523 | E-SOR-TOU-FC-FP-WC-R600 | 14 | 0.7 | 511.9128 | 0.34699 | 0.40339 | 0.40254 | 0.11101 | #NAME? | 526.25 | 526.25 | 1166.025 | 129.45 | 11.8523 | 12289.2068 | 728.4171 | 868.681 | 5.418 | 59.4761 | 0.01646 | 1.1737 | 2.8069 | 11162.1845 | 0.81657 | 3568.7506
524 | E-SOR-TOU-FC-FP-WC-R60 | 10 | 0.5 | 578.3048 | 0.39199 | 0.40449 | 0.28234 | 0.054395 | #NAME? | 528.6 | 528.6 | 1166.025 | 71.325 | 11.8892 | 13551.3655 | 751.5019 | 868.7829 | 5.3652 | 61.3753 | 0.015954 | 1.1211 | 2.8058 | 11129.3889 | 0.81929 | 3493.8935
525 | E-SOR-TOU-FC-FP-WC-R60 | 25.5 | 0.65 | 356.2494 | 0.24148 | 0.39854 | 0.53597 | 0.18746 | #NAME? | 515.575 | 515.575 | 1166.025 | 383.625 | 11.6999 | 10766.2163 | 692.5105 | 868.4821 | 5.6191 | 59.0407 | 0.017283 | 1.2429 | 2.8071 | 11195.696 | 0.80487 | 3873.4248
526 | E-SOR-TOU-FC-FP-WC-R60 | 21.5 | 0.55 | 382.901 | 0.25954 | 0.39978 | 0.48249 | 0.13632 | #NAME? | 517.825 | 517.825 | 1166.025 | 322.175 | 11.7301 | 11578.9769 | 703.7981 | 868.4693 | 5.5677 | 59.7699 | 0.01701 | 1.2061 | 2.8066 | 11180.9631 | 0.80493 | 3864.6979
527 | E-SOR-TOU-FC-FP-WC-R60 | 18 | 0.45 | 417.9596 | 0.2833 | 0.40085 | 0.40851 | 0.10439 | #NAME? | 520.35 | 520.35 | 1166.025 | 274.025 | 11.7705 | 12336.5868 | 719.6036 | 868.5649 | 5.5146 | 60.2942 | 0.016649 | 1.1703 | 2.8074 | 11165.6572 | 0.80165 | 3939.1944
528 | E-SOR-TOU-FC-FP-WC-R60 | 14 | 0.35 | 444.1888 | 0.30108 | 0.4023 | 0.31245 | 0.029424 | #NAME? | 523.625 | 523.625 | 1166.025 | 213.175 | 11.8128 | 13631.5926 | 737.3135 | 868.684 | 5.4641 | 63.2814 | 0.016252 | 1.1227 | 2.8068 | 11141.5601 | 0.79996 | 3970.8503
529 | E-SOR-TOU-FC-FP-WC-R60 | 10 | 0.25 | 404.8431 | 0.27441 | 0.40319 | 0.14758 | -0.10437 | #NAME? | 525.425 | 525.425 | 1166.025 | 168.4 | 11.8435 | 15916.1296 | 750.9835 | 868.5713 | 5.5188 | 74.8955 | 0.015946 | 1.0387 | 2.8065 | 11115.1096 | 0.79346 | 4123.469
530 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
531 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
532 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
533 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
534 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
535 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
536 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
537 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
538 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
539 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
540 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
541 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
542 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
543 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
544 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
545 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
546 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
547 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
548 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
549 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
550 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
551 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
552 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
553 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
554 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
555 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
556 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
557 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
558 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
559 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
560 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
561 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
562 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
563 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
564 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
565 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
566 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
567 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
568 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
569 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
570 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
571 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
572 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
573 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
574 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
575 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
576 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
577 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
578 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
579 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
580 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
581 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
582 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
583 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
584 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
585 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
586 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
587 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
588 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
589 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
590 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
591 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
592 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
593 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
594 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
595 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
596 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
597 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
598 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
599 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
600 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
601 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
602 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
603 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
604 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
605 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
606 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
607 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
608 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
609 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
610 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
611 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
612 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
613 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
614 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
615 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
616 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
617 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
618 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
619 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
620 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
621 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
622 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
623 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
624 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
625 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
626 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
627 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
628 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
629 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
630 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
631 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
632 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
633 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
634 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
635 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
636 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
637 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
638 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
639 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
640 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
641 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
642 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
643 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
644 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
645 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
646 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
647 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
648 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
649 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
650 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
651 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
652 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
653 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
654 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
655 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
656 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
657 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
658 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
659 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
660 | ------ | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0
Note on S1: bnienbor: with electricity for pumps in solar circuit (weightened), with electricity for boiler (weightened), without cold water pump
Note on T1: bnienbor: with electricity for pumps in solar circuit (weightened), with electricity for boiler (weightened), without cold water pump

## Yearly Data
CODE | SYSTEM | CHILLER | LOCATION | COLD | COLLECTOR | HEAT | BUILDING | F_SCAL | A_COLLECTOR | V_STORAGE | TIME | PS1/2 | PB | PELBOILER | PDHW | PH | PC | PHR | PCW | PELCHILLER | PELCT | TIME | Q_IRR | Q_COLL | Q_AUX_SUMMER | Q_AUX_WINTER | Q_AUX_DHW | Q_AUX_HEAT | Q_AUX_COOL | Q_LOSS_STORE | Q_SOLAR_COOL | Q_LOSS_PIPES | TIME | Q_COLD | Q_COLD_AUX | Q_COLD_SOLAR | Q_COLD_DEMAND | Q_HEAT_DEMAND | Q_DHW_DEMAND | Q_HR | Q_CHILLER_TOT | Q_DHW_SUMMER | Q_SOLARTOSYSTEM | TIME | V_WATER | SOLARCOOLINGTIME | AUXCOOLINGTIME | COOLINGDEMANDTIME | PELREFCHILLER | PELREFBOILER | STAGNATION TIME
| SCHEME |  |  | DISTRIBUTION | TYPE | REJECTION
1 | E | SOR | NAP | CC | ET | HC | R100 | 2.2447 | 31 | 2.3 | 8760 | 196617.2046 | 79658.1 | 123091.5497 | 65533.1035 | 92407.6909 | 95440 | 267232 | 133616 | 8589.6 | 565097.8973 | 8760 | 1720.1251 | 17388.1774 | 2894.7608 | 3877.0473 | 0 | 0 | 0 | -1479.8803 | 0 | 2858.8438 | 8760 | 4791.7807 | 0 | 0 | 4791.7033 | 6547.1955 | 3465.3091 | 13091.6088 | 9663.5983 | 1255.9932 | 15149.437 | 8760 | 0 | 954.4 | 0 | 1854.725 | 1553763.9416 | 178372.614 | 745.35 | -1350.1696
2 | E | SOR | NAP | CC | ET | HC | R100 | 2.2447 | 26.5 | 2 | 8760 | 193672.4469 | 95635.35 | 131967.208 | 65533.1035 | 92407.6909 | 96055 | 268954 | 134477 | 8644.95 | 568710.5751 | 8760 | 1720.1251 | 15896.319 | 3853.1648 | 4467.5798 | 0 | 0 | 0 | -1446.7233 | 0 | 2840.7688 | 8760 | 4791.9358 | 0 | 0 | 4791.7033 | 6547.1955 | 3452.6241 | 13080.0651 | 9626.8711 | 1255.7218 | 13734.9286 | 8760 | 0 | 960.55 | 0 | 1854.725 | 1553763.2106 | 178372.614 | 636.7 | -1332.614
3 | E | SOR | NAP | CC | ET | HC | R100 | 2.2447 | 21.5 | 1.6 | 8760 | 190317.1721 | 116527.95 | 143573.4342 | 65533.1035 | 92407.6909 | 96640 | 270592 | 135296 | 8697.6 | 572168.5236 | 8760 | 1720.1251 | 13888.3032 | 5273.0893 | 5225.3546 | 0 | 0 | 0 | -1410.5106 | 0 | 2815.9812 | 8760 | 4792.2692 | 0 | 0 | 4791.7033 | 6547.1955 | 3445.6059 | 13074.236 | 9592.2062 | 1254.8781 | 11820.573 | 8760 | 0 | 966.4 | 0 | 1854.725 | 1553744.2927 | 178372.614 | 514.25 | -1322.7074
4 | E | SOR | NAP | CC | ET | HC | R100 | 2.2447 | 17 | 1.3 | 8760 | 188910.9805 | 132884.55 | 152659.8284 | 65533.1035 | 92407.6909 | 97230 | 272244 | 136122 | 8750.7 | 575647.0941 | 8760 | 1720.1251 | 11875.8521 | 6387.5158 | 5938.2478 | 0 | 0 | 0 | -1369.1901 | 0 | 2763.5532 | 8760 | 4792.2905 | 0 | 0 | 4791.7033 | 6547.1955 | 3436.6378 | 13073.7748 | 9558.47 | 1254.1552 | 9927.5325 | 8760 | 0 | 972.3 | 0 | 1854.725 | 1553764.3896 | 178372.614 | 383.425 | -1306.8548
5 | E | SOR | NAP | CC | ET | HC | R100 | 2.2447 | 12.5 | 0.95 | 8760 | 189267.8303 | 149418 | 161844.466 | 65533.1035 | 92407.6909 | 97792.5 | 273819 | 136909.5 | 8801.325 | 578937.5115 | 8760 | 1720.1251 | 9593.8993 | 7492.3098 | 6735.0863 | 0 | 0 | 0 | -1312.8713 | 0 | 2663.4388 | 8760 | 4792.5571 | 0 | 0 | 4791.7033 | 6547.1955 | 3417.4632 | 13056.9326 | 9529.803 | 1252.3967 | 7823.561 | 8760 | 0 | 977.925 | 0 | 1854.725 | 1553749.3289 | 178372.614 | 235.375 | -1303.6518
6 | E | SOR | NAP | CC | ET | HC | R100 | 2.2447 | 31 | 1.55 | 8760 | 189684.4065 | 87403.05 | 127394.0129 | 65533.1035 | 92407.6909 | 95222.5 | 266623 | 133311.5 | 8570.025 | 563859.0971 | 8760 | 1720.1251 | 16589.1415 | 3441.5985 | 4368.1719 | 0 | 0 | 0 | -1491.014 | 0 | 2907.7967 | 8760 | 4791.8134 | 0 | 0 | 4791.7033 | 6547.1955 | 3476.1642 | 13121.0346 | 9685.7571 | 1255.9833 | 14293.8879 | 8760 | 0 | 952.225 | 0 | 1854.725 | 1553771.6386 | 178372.614 | 801.875 | -1366.2397
7 | E | SOR | NAP | CC | ET | HC | R100 | 2.2447 | 26.5 | 1.35 | 8760 | 188226.2058 | 99685.35 | 134217.058 | 65533.1035 | 92407.6909 | 95852.5 | 268387 | 134193.5 | 8626.725 | 567544.2788 | 8760 | 1720.1251 | 15329.5005 | 4189.5549 | 4818.976 | 0 | 0 | 0 | -1461.561 | 0 | 2887.7224 | 8760 | 4792.2579 | 0 | 0 | 4791.7033 | 6547.1955 | 3466.4992 | 13103.7902 | 9643.2833 | 1255.6827 | 13112.1116 | 8760 | 0 | 958.525 | 0 | 1854.725 | 1553756.7558 | 178372.614 | 688.025 | -1346.7652
8 | E | SOR | NAP | CC | ET | HC | R100 | 2.2447 | 21.5 | 1.1 | 8760 | 186697.0046 | 118006.2 | 144394.6294 | 65533.1035 | 92407.6909 | 96500 | 270200 | 135100 | 8685 | 571347.9657 | 8760 | 1720.1251 | 13548.8722 | 5420.2956 | 5434.8195 | 0 | 0 | 0 | -1426.0979 | 0 | 2859.7462 | 8760 | 4792.3292 | 0 | 0 | 4791.7033 | 6547.1955 | 3455.6374 | 13089.4077 | 9603.9232 | 1254.7744 | 11433.6235 | 8760 | 0 | 965 | 0 | 1854.725 | 1553730.9259 | 178372.614 | 552.025 | -1327.1649
9 | E | SOR | NAP | CC | ET | HC | R100 | 2.2447 | 17 | 0.85 | 8760 | 185871.5481 | 135210.6 | 153951.9922 | 65533.1035 | 92407.6909 | 97105 | 271894 | 135947 | 8739.45 | 574895.3268 | 8760 | 1720.1251 | 11630.4222 | 6648.3372 | 6142.6965 | 0 | 0 | 0 | -1390.0264 | 0 | 2813.8584 | 8760 | 4792.2529 | 0 | 0 | 4791.7033 | 6547.1955 | 3442.4837 | 13076.9586 | 9571.3649 | 1253.9746 | 9632.4703 | 8760 | 0 | 971.05 | 0 | 1854.725 | 1553744.6237 | 178372.614 | 421.15 | -1320.3527
10 | E | SOR | NAP | CC | ET | HC | R10 | 2.2447 | 12.5 | 0.65 | 8760 | 186331.7223 | 151559.1 | 163033.8867 | 65533.1035 | 92407.6909 | 97692.5 | 273539 | 136769.5 | 8792.325 | 578363.0061 | 8760 | 1720.1251 | 9392.7067 | 7717.0672 | 6961.4862 | 0 | 0 | 0 | -1341.6686 | 0 | 2725.0665 | 8760 | 4791.9286 | 0 | 0 | 4791.7033 | 6547.1955 | 3420.4056 | 13070.2289 | 9533.9268 | 1251.3079 | 7561.9492 | 8760 | 0 | 976.925 | 0 | 1854.725 | 1553736.5794 | 178372.614 | 271.65 | -1300.8634
11 | E | SOR | NAP | CC | ET | HC | R10 | 2.2447 | 31 | 0.8 | 8760 | 178063.3962 | 98528.4 | 133574.3508 | 65533.1035 | 92407.6909 | 95020 | 266056 | 133028 | 8551.8 | 562686.6262 | 8760 | 1720.1251 | 15299.0257 | 4150.8035 | 4954.6329 | 0 | 0 | 0 | -1495.1562 | 0 | 2999.9326 | 8760 | 4792.3512 | 0 | 0 | 4791.7033 | 6547.1955 | 3478.2145 | 13172.282 | 9721.6189 | 1256.0786 | 12931.2111 | 8760 | 0 | 950.2 | 0 | 1854.725 | 1553782.2851 | 178372.614 | 887.775 | -1365.0538
12 | E | SOR | NAP | CC | ET | HC | R10 | 2.2447 | 26.5 | 0.65 | 8760 | 176475.5838 | 110565 | 140260.905 | 65533.1035 | 92407.6909 | 95475 | 267330 | 133665 | 8592.75 | 565358.0605 | 8760 | 1720.1251 | 14121.7243 | 4738.9771 | 5480.8006 | 0 | 0 | 0 | -1475.184 | 0 | 2996.697 | 8760 | 4792.4089 | 0 | 0 | 4791.7033 | 6547.1955 | 3467.389 | 13153.1781 | 9679.3597 | 1255.3235 | 11811.3634 | 8760 | 0 | 954.75 | 0 | 1854.725 | 1553776.4607 | 178372.614 | 797.2 | -1353.0426
13 | E | SOR | NAP | CC | ET | HC | R10 | 2.2447 | 21.5 | 0.55 | 8760 | 176642.7312 | 127483.2 | 149659.2784 | 65533.1035 | 92407.6909 | 96230 | 269444 | 134722 | 8660.7 | 569774.5488 | 8760 | 1720.1251 | 12621.981 | 5694.8723 | 6141.3852 | 0 | 0 | 0 | -1453.2545 | 0 | 2976.8244 | 8760 | 4792.257 | 0 | 0 | 4791.7033 | 6547.1955 | 3453.9543 | 13118.5235 | 9623.5924 | 1253.793 | 10408.1946 | 8760 | 0 | 962.3 | 0 | 1854.725 | 1553758.014 | 178372.614 | 662.975 | -1335.6467
14 | E | SOR | NAP | CC | ET | HC | R10 | 2.2447 | 17 | 0.45 | 8760 | 176592.4696 | 146101.05 | 160001.8389 | 65533.1035 | 92407.6909 | 96782.5 | 270991 | 135495.5 | 8710.425 | 573021.715 | 8760 | 1720.1251 | 10892.1252 | 6931.5792 | 6801.7251 | 0 | 0 | 0 | -1448.7274 | 0 | 2917.08 | 8760 | 4792.4452 | 0 | 0 | 4791.7033 | 6547.1955 | 3437.8002 | 13104.303 | 9590.4948 | 1251.9768 | 8805.6484 | 8760 | 0 | 967.825 | 0 | 1854.725 | 1553755.7401 | 178372.614 | 527.525 | -1326.7174
15 | E | SOR | NAP | CC | ET | HC | R10 | 2.2447 | 12.5 | 0.3 | 8760 | 173037.7303 | 167516.1 | 171898.2957 | 65533.1035 | 92407.6909 | 97300 | 272440 | 136220 | 8757 | 576051.9457 | 8760 | 1720.1251 | 8452.0559 | 7971.3823 | 8014.7157 | 0 | 0 | 0 | -1474.5786 | 0 | 2960.7728 | 8760 | 4791.9824 | 0 | 0 | 4791.7033 | 6547.1955 | 3404.02 | 13095.7884 | 9559.8591 | 1244.9509 | 6395.1203 | 8760 | 0 | 973 | 0 | 1854.725 | 1553741.8674 | 178372.614 | 417.475 | -1315.1722
16 | E | SOR | NAP | CC | ET | HC | R600 | 2.6378 | 31 | 2.3 | 8760 | 198148.2969 | 58777.65 | 111492.0731 | 65533.1035 | 55495.4426 | 106320 | 297696 | 148848 | 9568.8 | 630206.1091 | 8760 | 1720.1251 | 17372.8514 | 3399.9395 | 1784.5374 | 0 | 0 | 0 | -1569.8039 | 0 | 2854.0848 | 8760 | 5360.3601 | 0 | 0 | 5359.9812 | 3337.1316 | 4023.6529 | 14998.5257 | 10765.8479 | 1489.5629 | 15033.571 | 8760 | 0 | 1063.2 | 0 | 2104.7 | 1725346.2474 | 155104.6654 | 730.25 | -1367.6608
17 | E | SOR | NAP | CC | ET | HC | R600 | 2.6378 | 26.5 | 2 | 8760 | 196511.0561 | 72030.6 | 118854.3322 | 65533.1035 | 55495.4426 | 107057.5 | 299761 | 149880.5 | 9635.175 | 634530.9038 | 8760 | 1720.1251 | 16015.3657 | 4296.2345 | 2121.909 | 0 | 0 | 0 | -1537.9924 | 0 | 2829.567 | 8760 | 5360.4117 | 0 | 0 | 5359.9812 | 3337.1316 | 4009.5373 | 14980.2543 | 10718.6534 | 1489.0658 | 13760.9401 | 8760 | 0 | 1070.575 | 0 | 2104.7 | 1725336.8374 | 155104.6654 | 607.925 | -1354.8828
18 | E | SOR | NAP | CC | ET | HC | R600 | 2.6378 | 21.5 | 1.6 | 8760 | 193923.9285 | 92556 | 130256.572 | 65533.1035 | 55495.4426 | 107757.5 | 301721 | 150860.5 | 9698.175 | 638661.2123 | 8760 | 1720.1251 | 14082.5337 | 5838.8215 | 2608.9855 | 0 | 0 | 0 | -1487.7876 | 0 | 2788.3925 | 8760 | 5360.4728 | 0 | 0 | 5359.9812 | 3337.1316 | 3986.4772 | 14986.0339 | 10681.825 | 1486.1306 | 11940.4429 | 8760 | 0 | 1077.575 | 0 | 2104.7 | 1725305.1331 | 155104.6654 | 477.25 | -1335.7728
19 | E | SOR | NAP | CC | ET | HC | R600 | 2.6378 | 17 | 1.3 | 8760 | 192822.6985 | 109393.2 | 139609.9484 | 65533.1035 | 55495.4426 | 108347.5 | 303373 | 151686.5 | 9751.275 | 642147.7292 | 8760 | 1720.1251 | 12098.5269 | 7133.2935 | 3118.5343 | 0 | 0 | 0 | -1434.399 | 0 | 2717.8553 | 8760 | 5359.9817 | 0 | 0 | 5359.9812 | 3337.1316 | 3960.209 | 14973.542 | 10642.7636 | 1484.0469 | 10096.2609 | 8760 | 0 | 1083.475 | 0 | 2104.7 | 1725329.2584 | 155104.6654 | 344.45 | -1333.5188
20 | E | SOR | NAP | CC | ET | HC | R600 | 2.6378 | 12.5 | 0.95 | 8760 | 192874.9505 | 127834.2 | 149854.2654 | 65533.1035 | 55495.4426 | 108942.5 | 305039 | 152519.5 | 9804.825 | 645659.2649 | 8760 | 1720.1251 | 9775.6464 | 8400.3432 | 3744.4266 | 0 | 0 | 0 | -1365.7054 | 0 | 2608.51 | 8760 | 5360.8171 | 0 | 0 | 5359.9812 | 3337.1316 | 3930.67 | 14975.3048 | 10610.8851 | 1480.6079 | 7964.5284 | 8760 | 0 | 1089.425 | 0 | 2104.7 | 1725307.2256 | 155104.6654 | 197.175 | -1325.897
21 | E | SOR | NAP | CC | ET | HC | R600 | 2.6378 | 31 | 1.55 | 8760 | 190274.6561 | 66777.75 | 115936.2768 | 65533.1035 | 55495.4426 | 106132.5 | 297171 | 148585.5 | 9551.925 | 629143.4468 | 8760 | 1720.1251 | 16508.4496 | 4007.4296 | 2115.6969 | 0 | 0 | 0 | -1566.3762 | 0 | 2886.994 | 8760 | 5360.4239 | 0 | 0 | 5359.9812 | 3337.1316 | 4023.1284 | 15044.6635 | 10788.2018 | 1488.6187 | 14129.7043 | 8760 | 0 | 1061.325 | 0 | 2104.7 | 1725366.02 | 155104.6654 | 790.15 | -1375.5376
22 | E | SOR | NAP | CC | ET | HC | R600 | 2.6378 | 26.5 | 1.35 | 8760 | 189893.3845 | 78165 | 122262.105 | 65533.1035 | 55495.4426 | 106805 | 299054 | 149527 | 9612.45 | 633085.853 | 8760 | 1720.1251 | 15352.5363 | 4771.305 | 2461.4514 | 0 | 0 | 0 | -1538.6531 | 0 | 2869.2099 | 8760 | 5360.3755 | 0 | 0 | 5359.9812 | 3337.1316 | 4014.0958 | 15020.726 | 10739.0052 | 1487.7445 | 13048.7065 | 8760 | 0 | 1068.05 | 0 | 2104.7 | 1725334.4356 | 155104.6654 | 671.35 | -1358.2506
23 | E | SOR | NAP | CC | ET | HC | R600 | 2.6378 | 21.5 | 1.1 | 8760 | 189589.8357 | 95065.65 | 131650.7291 | 65533.1035 | 55495.4426 | 107575 | 301210 | 150605 | 9681.75 | 637608.5433 | 8760 | 1720.1251 | 13689.0584 | 6011.3824 | 2880.6987 | 0 | 0 | 0 | -1499.6442 | 0 | 2830.4633 | 8760 | 5360.7209 | 0 | 0 | 5359.9812 | 3337.1316 | 3997.0277 | 15004.7606 | 10690.8986 | 1484.9167 | 11501.2125 | 8760 | 0 | 1075.75 | 0 | 2104.7 | 1725322.7019 | 155104.6654 | 519.8 | -1343.0001
24 | E | SOR | NAP | CC | ET | HC | R600 | 2.6378 | 17 | 0.85 | 8760 | 188700.9059 | 113131.35 | 141686.56 | 65533.1035 | 55495.4426 | 108185 | 302918 | 151459 | 9736.65 | 641200.8771 | 8760 | 1720.1251 | 11781.3086 | 7359.4748 | 3350.6807 | 0 | 0 | 0 | -1450.8497 | 0 | 2770.9712 | 8760 | 5360.3565 | 0 | 0 | 5359.9812 | 3337.1316 | 3971.5004 | 14991.6562 | 10655.137 | 1483.3217 | 9727.6966 | 8760 | 0 | 1081.85 | 0 | 2104.7 | 1725321.5106 | 155104.6654 | 390.925 | -1336.9733
25 | E | SOR | NAP | CC | ET | HC | R60 | 2.6378 | 12.5 | 0.65 | 8760 | 189620.7933 | 130029.3 | 151073.6841 | 65533.1035 | 55495.4426 | 108847.5 | 304773 | 152386.5 | 9796.275 | 645108.0034 | 8760 | 1720.1251 | 9558.8591 | 8649.7446 | 3898.786 | 0 | 0 | 0 | -1388.6239 | 0 | 2664.4981 | 8760 | 5360.6895 | 0 | 0 | 5359.9812 | 3337.1316 | 3935.5893 | 14985.4594 | 10617.1716 | 1478.8137 | 7694.3625 | 8760 | 0 | 1088.475 | 0 | 2104.7 | 1725315.1748 | 155104.6654 | 235.85 | -1320.7906
26 | E | SOR | NAP | CC | ET | HC | R60 | 2.6378 | 31 | 0.8 | 8760 | 178245.5618 | 80030.7 | 123298.5359 | 65533.1035 | 55495.4426 | 105885 | 296478 | 148239 | 9529.65 | 627708.8688 | 8760 | 1720.1251 | 15211.3626 | 4873.7513 | 2648.1647 | 0 | 0 | 0 | -1562.1672 | 0 | 2956.6837 | 8760 | 5360.0203 | 0 | 0 | 5359.9812 | 3337.1316 | 4023.2339 | 15096.6562 | 10824.7384 | 1486.0331 | 12785.0541 | 8760 | 0 | 1058.85 | 0 | 2104.7 | 1725357.4715 | 155104.6654 | 881.45 | -1388.1851
27 | E | SOR | NAP | CC | ET | HC | R60 | 2.6378 | 26.5 | 0.65 | 8760 | 177749.3826 | 89926.2 | 128795.6694 | 65533.1035 | 55495.4426 | 106412.5 | 297955 | 148977.5 | 9577.125 | 630811.3501 | 8760 | 1720.1251 | 14165.3042 | 5454.0378 | 3013.347 | 0 | 0 | 0 | -1535.9619 | 0 | 2950.4743 | 8760 | 5360.4093 | 0 | 0 | 5359.9812 | 3337.1316 | 4005.7093 | 15084.6801 | 10780.9355 | 1483.9217 | 11799.9374 | 8760 | 0 | 1064.125 | 0 | 2104.7 | 1725358.0574 | 155104.6654 | 784.45 | -1367.0234
28 | E | SOR | NAP | CC | ET | HC | R60 | 2.6378 | 21.5 | 0.55 | 8760 | 178433.6194 | 104760 | 137036.12 | 65533.1035 | 55495.4426 | 107217.5 | 300209 | 150104.5 | 9649.575 | 635530.0801 | 8760 | 1720.1251 | 12718.7184 | 6468.0421 | 3410.0389 | 0 | 0 | 0 | -1505.8431 | 0 | 2921.9026 | 8760 | 5360.6988 | 0 | 0 | 5359.9812 | 3337.1316 | 3984.3986 | 15042.8824 | 10716.6395 | 1480.5445 | 10463.4812 | 8760 | 0 | 1072.175 | 0 | 2104.7 | 1725333.09 | 155104.6654 | 643.65 | -1354.305
29 | E | SOR | NAP | CC | ET | HC | R60 | 2.6378 | 17 | 0.45 | 8760 | 178857.1784 | 123952.95 | 147698.1592 | 65533.1035 | 55495.4426 | 107845 | 301966 | 150983 | 9706.05 | 639218.3786 | 8760 | 1720.1251 | 11019.1014 | 7801.9954 | 3832.7103 | 0 | 0 | 0 | -1487.0273 | 0 | 2865.7494 | 8760 | 5360.1205 | 0 | 0 | 5359.9812 | 3337.1316 | 3957.7542 | 15028.226 | 10677.4514 | 1477.4264 | 8891.2398 | 8760 | 0 | 1078.45 | 0 | 2104.7 | 1725309.578 | 155104.6654 | 504 | -1340.249
30 | E | SOR | NAP | CC | ET | HC | R60 | 2.6378 | 12.5 | 0.3 | 8760 | 175168.9719 | 144813.15 | 159286.3866 | 65533.1035 | 55495.4426 | 108402.5 | 303527 | 151763.5 | 9756.225 | 642492.5742 | 8760 | 1720.1251 | 8564.3813 | 9094.8846 | 4792.666 | 0 | 0 | 0 | -1494.3535 | 0 | 2903.4257 | 8760 | 5360.2575 | 0 | 0 | 5359.9812 | 3337.1316 | 3901.9073 | 15019.8331 | 10644.4789 | 1467.2565 | 6474.0772 | 8760 | 0 | 1084.025 | 0 | 2104.7 | 1725293.6892 | 155104.6654 | 395.85 | -1324.7453
31 | E | SOR | NAP | CC | ET | WC | R100 | 3.1512 | 43.5 | 3.25 | 8760 | 226067.4756 | 78833.25 | 122633.3303 | 65533.1035 | 105813.8734 | 113362.5 | 391100.625 | 158707.5 | 10202.625 | 52430.1562 | 8760 | 1720.1251 | 22908.2229 | 3122.1326 | 5085.2107 | 0 | 0 | 0 | -1488.8808 | 0 | 2829.3318 | 8760 | 6724.32 | 0 | 0 | 6726.6505 | 9191.0315 | 4605.9156 | 20825.797 | 12748.1634 | 1704.1469 | 20608.9463 | 8760 | 25650.9679 | 1133.625 | 0 | 1854.725 | 2206375.0483 | 178372.614 | 865.275
32 | E | SOR | NAP | CC | ET | WC | R100 | 3.1512 | 37 | 2.8 | 8760 | 217703.801 | 94246.2 | 131195.5094 | 65533.1035 | 105813.8734 | 113957.5 | 393153.375 | 159540.5 | 10256.175 | 52705.3438 | 8760 | 1720.1251 | 21051.2468 | 4221.2148 | 5876.6974 | 0 | 0 | 0 | -1452.8279 | 0 | 2825.7832 | 8760 | 6724.4002 | 0 | 0 | 6726.6505 | 9191.0315 | 4578.8503 | 20804.9669 | 12689.7759 | 1701.321 | 18816.4451 | 8760 | 25638.1038 | 1139.575 | 0 | 1854.725 | 2206326.8921 | 178372.614 | 746.05
33 | E | SOR | NAP | CC | ET | WC | R100 | 3.1512 | 30.5 | 2.3 | 8760 | 208673.8024 | 114967.35 | 142706.492 | 65533.1035 | 105813.8734 | 114547.5 | 395188.875 | 160366.5 | 10309.275 | 52978.2188 | 8760 | 1720.1251 | 18629.4633 | 5940.3563 | 6813.9544 | 0 | 0 | 0 | -1416.8643 | 0 | 2814.315 | 8760 | 6722.4358 | 0 | 0 | 6726.6505 | 9191.0315 | 4563.903 | 20784.3667 | 12628.5755 | 1699.4984 | 16482.5091 | 8760 | 25639.8984 | 1145.475 | 0 | 1854.725 | 2206251.9458 | 178372.614 | 623.575
34 | E | SOR | NAP | CC | ET | WC | R100 | 3.1512 | 24 | 1.8 | 8760 | 201034.0938 | 136695.6 | 154776.9372 | 65533.1035 | 105813.8734 | 115122.5 | 397172.625 | 161171.5 | 10361.025 | 53244.1562 | 8760 | 1720.1251 | 15846.4892 | 7966.9462 | 7803.8584 | 0 | 0 | 0 | -1377.4313 | 0 | 2785.3683 | 8760 | 6721.9311 | 0 | 0 | 6726.6505 | 9191.0315 | 4548.2334 | 20776.5006 | 12575.0861 | 1696.1994 | 13806.4932 | 8760 | 25649.6726 | 1151.225 | 0 | 1854.725 | 2206240.3726 | 178372.614 | 490.475
35 | E | SOR | NAP | CC | ET | WC | R100 | 3.1512 | 17.5 | 1.3 | 8760 | 196443.7658 | 155479.5 | 165211.7415 | 65533.1035 | 105813.8734 | 115700 | 399165 | 161980 | 10413 | 53511.25 | 8760 | 1720.1251 | 12754.3947 | 9372.8271 | 8925.0499 | 0 | 0 | 0 | -1320.1727 | 0 | 2707.2779 | 8760 | 6721.6386 | 0 | 0 | 6726.6505 | 9191.0315 | 4514.4873 | 20764.0908 | 12518.6893 | 1691.5688 | 10880.6327 | 8760 | 25656.3955 | 1157 | 0 | 1854.725 | 2206188.6148 | 178372.614 | 326.175
36 | E | SOR | NAP | CC | ET | WC | R100 | 3.1512 | 43.5 | 2.2 | 8760 | 216972.967 | 87795.9 | 127612.2483 | 65533.1035 | 105813.8734 | 113552.5 | 391756.125 | 158973.5 | 10219.725 | 52518.0312 | 8760 | 1720.1251 | 21683.4165 | 3947.8948 | 5728.0941 | 0 | 0 | 0 | -1497.1839 | 0 | 2877.3022 | 8760 | 6725.2771 | 0 | 0 | 6726.6505 | 9191.0315 | 4623.1082 | 20876.8575 | 12758.8326 | 1702.812 | 19329.3896 | 8760 | 25694.6705 | 1135.525 | 0 | 1854.725 | 2206385.1696 | 178372.614 | 918.675
37 | E | SOR | NAP | CC | ET | WC | R100 | 3.1512 | 37 | 1.85 | 8760 | 209154.9107 | 101036.7 | 134967.7579 | 65533.1035 | 105813.8734 | 113932.5 | 393067.125 | 159505.5 | 10253.925 | 52693.7812 | 8760 | 1720.1251 | 20001.073 | 4866.7979 | 6423.0469 | 0 | 0 | 0 | -1466.1479 | 0 | 2872.5946 | 8760 | 6724.7423 | 0 | 0 | 6726.6505 | 9191.0315 | 4601.5105 | 20859.741 | 12714.1536 | 1700.4128 | 17707.2415 | 8760 | 25693.5397 | 1139.325 | 0 | 1854.725 | 2206380.084 | 178372.614 | 810.225
38 | E | SOR | NAP | CC | ET | WC | R100 | 3.1512 | 30.5 | 1.55 | 8760 | 202914.8308 | 117953.55 | 144365.3814 | 65533.1035 | 105813.8734 | 114452.5 | 394861.125 | 160233.5 | 10300.725 | 52934.2812 | 8760 | 1720.1251 | 17981.2646 | 6317.2837 | 7144.9891 | 0 | 0 | 0 | -1431.0139 | 0 | 2857.9416 | 8760 | 6723.609 | 0 | 0 | 6726.6505 | 9191.0315 | 4582.7421 | 20825.2401 | 12650.3157 | 1698.8214 | 15776.6016 | 8760 | 25672.5686 | 1144.525 | 0 | 1854.725 | 2206302.6141 | 178372.614 | 675.275
39 | E | SOR | NAP | CC | ET | WC | R100 | 3.1512 | 24 | 1.2 | 8760 | 197366.1673 | 138330.45 | 155685.1267 | 65533.1035 | 105813.8734 | 114982.5 | 396689.625 | 160975.5 | 10348.425 | 53179.4062 | 8760 | 1720.1251 | 15476.711 | 8213.3024 | 8068.7551 | 0 | 0 | 0 | -1391.9605 | 0 | 2829.8183 | 8760 | 6722.9865 | 0 | 0 | 6726.6505 | 9191.0315 | 4557.2881 | 20800.6552 | 12594.6212 | 1694.934 | 13384.2131 | 8760 | 25663.305 | 1149.825 | 0 | 1854.725 | 2206265.5748 | 178372.614 | 527.825
40 | E | SOR | NAP | CC | ET | WC | R10 | 3.1512 | 17.5 | 0.9 | 8760 | 193563.8178 | 156370.5 | 165706.7085 | 65533.1035 | 105813.8734 | 115647.5 | 398983.875 | 161906.5 | 10408.275 | 53486.9688 | 8760 | 1720.1251 | 12514.1232 | 9615.7899 | 9145.9546 | 0 | 0 | 0 | -1338.486 | 0 | 2755.284 | 8760 | 6722.5201 | 0 | 0 | 6726.6505 | 9191.0315 | 4516.9157 | 20779.2975 | 12527.4633 | 1689.6365 | 10589.7435 | 8760 | 25664.2242 | 1156.475 | 0 | 1854.725 | 2206214.5677 | 178372.614 | 360.9
41 | E | SOR | NAP | CC | ET | WC | R10 | 3.1512 | 43.5 | 1.1 | 8760 | 200964.0508 | 101413.35 | 135176.994 | 65533.1035 | 105813.8734 | 113585 | 391868.25 | 159019 | 10222.65 | 52533.0625 | 8760 | 1720.1251 | 19648.6177 | 5126.2487 | 6552.758 | 0 | 0 | 0 | -1489.2301 | 0 | 2957.7064 | 8760 | 6725.3604 | 0 | 0 | 6726.6505 | 9191.0315 | 4619.1774 | 20935.6572 | 12789.0854 | 1700.9228 | 17242.1513 | 8760 | 25756.3636 | 1135.85 | 0 | 1854.725 | 2206423.8689 | 178372.614 | 1009.05
42 | E | SOR | NAP | CC | ET | WC | R10 | 3.1512 | 37 | 0.95 | 8760 | 196218.8113 | 112207.95 | 141173.5942 | 65533.1035 | 105813.8734 | 113847.5 | 392773.875 | 159386.5 | 10246.275 | 52654.4688 | 8760 | 1720.1251 | 18406.4111 | 5708.7809 | 7146.1735 | 0 | 0 | 0 | -1467.8088 | 0 | 2962.4441 | 8760 | 6725.1774 | 0 | 0 | 6726.6505 | 9191.0315 | 4600.3495 | 20915.7205 | 12750.5268 | 1698.7584 | 16034.3682 | 8760 | 25743.4468 | 1138.475 | 0 | 1854.725 | 2206395.1744 | 178372.614 | 897.05
43 | E | SOR | NAP | CC | ET | WC | R10 | 3.1512 | 30.5 | 0.75 | 8760 | 190731.3169 | 127788.3 | 149828.7671 | 65533.1035 | 105813.8734 | 114275 | 394248.75 | 159985 | 10284.75 | 52852.1875 | 8760 | 1720.1251 | 16626.7243 | 6742.0751 | 7980.7985 | 0 | 0 | 0 | -1441.8685 | 0 | 2962.689 | 8760 | 6722.9122 | 0 | 0 | 6726.6505 | 9191.0315 | 4574.0941 | 20872.2275 | 12685.8398 | 1695.0947 | 14325.8433 | 8760 | 25711.2908 | 1142.75 | 0 | 1854.725 | 2206297.4831 | 178372.614 | 787.25
44 | E | SOR | NAP | CC | ET | WC | R10 | 3.1512 | 24 | 0.6 | 8760 | 186196.2523 | 149153.4 | 161697.4758 | 65533.1035 | 105813.8734 | 114827.5 | 396154.875 | 160758.5 | 10334.475 | 53107.7188 | 8760 | 1720.1251 | 14380.2028 | 8445.3631 | 8944.0309 | 0 | 0 | 0 | -1416.7977 | 0 | 2950.0583 | 8760 | 6722.7703 | 0 | 0 | 6726.6505 | 9191.0315 | 4541.1461 | 20837.4583 | 12619.8557 | 1689.3556 | 12180.5407 | 8760 | 25693.8935 | 1148.275 | 0 | 1854.725 | 2206280.7995 | 178372.614 | 643.925
45 | E | SOR | NAP | CC | ET | WC | R10 | 3.1512 | 17.5 | 0.45 | 8760 | 182883.8552 | 167259.6 | 171755.8052 | 65533.1035 | 105813.8734 | 115480 | 398406 | 161672 | 10393.2 | 53409.5 | 8760 | 1720.1251 | 11636.7586 | 10078.0911 | 9931.8443 | 0 | 0 | 0 | -1408.8148 | 0 | 2869.6217 | 8760 | 6721.5684 | 0 | 0 | 6726.6505 | 9191.0315 | 4493.3359 | 20798.6297 | 12548.4369 | 1678.1975 | 9610.3867 | 8760 | 25677.9049 | 1154.8 | 0 | 1854.725 | 2206207.4964 | 178372.614 | 481.45
46 | E | SOR | NAP | CC | ET | WC | R600 | 3.703 | 43.5 | 3.25 | 8760 | 226555.2736 | 57296.7 | 110669.3779 | 65533.1035 | 62307.5625 | 127655 | 440409.75 | 178717 | 11488.95 | 59040.4375 | 8760 | 1720.1251 | 22721.2113 | 3727.9268 | 2231.26 | 0 | 0 | 0 | -1584.7799 | 0 | 2838.8868 | 8760 | 7523.9472 | 0 | 0 | 7524.4058 | 4684.7054 | 5281.9958 | 23627.2035 | 14255.373 | 1979.3651 | 20302.1105 | 8760 | 28908.0156 | 1276.55 | 0 | 2104.7 | 2449136.2903 | 155104.6654 | 857.675
47 | E | SOR | NAP | CC | ET | WC | R600 | 3.703 | 37 | 2.8 | 8760 | 219554.3449 | 71567.55 | 118597.0994 | 65533.1035 | 62307.5625 | 128275 | 442548.75 | 179585 | 11544.75 | 59327.1875 | 8760 | 1720.1251 | 21022.7762 | 4869.7162 | 2701.1721 | 0 | 0 | 0 | -1550.2288 | 0 | 2822.0187 | 8760 | 7523.2657 | 0 | 0 | 7524.4058 | 4684.7054 | 5249.1479 | 23607.1459 | 14192.9481 | 1975.6132 | 18682.7203 | 8760 | 28908.1703 | 1282.75 | 0 | 2104.7 | 2449096.04 | 155104.6654 | 731.225
48 | E | SOR | NAP | CC | ET | WC | R600 | 3.703 | 30.5 | 2.3 | 8760 | 211916.7134 | 90641.7 | 129193.1429 | 65533.1035 | 62307.5625 | 128985 | 444998.25 | 180579 | 11608.65 | 59655.5625 | 8760 | 1720.1251 | 18785.8615 | 6675.8213 | 3251.6941 | 0 | 0 | 0 | -1507.7984 | 0 | 2802.6417 | 8760 | 7521.0004 | 0 | 0 | 7524.4058 | 4684.7054 | 5218.8807 | 23594.0323 | 14119.7621 | 1970.4853 | 16541.6936 | 8760 | 28909.2317 | 1289.85 | 0 | 2104.7 | 2449033.0058 | 155104.6654 | 596.675
49 | E | SOR | NAP | CC | ET | WC | R600 | 3.703 | 24 | 1.8 | 8760 | 204901.3446 | 112860 | 141535.82 | 65533.1035 | 62307.5625 | 129662.5 | 447335.625 | 181527.5 | 11669.625 | 59968.9062 | 8760 | 1720.1251 | 16088.1697 | 8663.7246 | 3939.7997 | 0 | 0 | 0 | -1452.6164 | 0 | 2753.6111 | 8760 | 7522.2471 | 0 | 0 | 7524.4058 | 4684.7054 | 5174.428 | 23595.6093 | 14064.2898 | 1963.5396 | 13973.9907 | 8760 | 28932.5003 | 1296.625 | 0 | 2104.7 | 2449019.3591 | 155104.6654 | 454
50 | E | SOR | NAP | CC | ET | WC | R600 | 3.703 | 17.5 | 1.3 | 8760 | 200296.1486 | 133388.1 | 152939.5597 | 65533.1035 | 62307.5625 | 130335 | 449655.75 | 182469 | 11730.15 | 60279.9375 | 8760 | 1720.1251 | 12982.9105 | 10468.1253 | 4797.7716 | 0 | 0 | 0 | -1384.9298 | 0 | 2663.6309 | 8760 | 7521.9716 | 0 | 0 | 7524.4058 | 4684.7054 | 5126.1272 | 23591.0854 | 14001.9728 | 1955.3016 | 11054.0248 | 8760 | 28951.6042 | 1303.35 | 0 | 2104.7 | 2448990.8963 | 155104.6654 | 285.775
51 | E | SOR | NAP | CC | ET | WC | R600 | 3.703 | 43.5 | 2.2 | 8760 | 216246.1987 | 67230 | 116187.51 | 65533.1035 | 62307.5625 | 127817.5 | 440970.375 | 178944.5 | 11503.575 | 59115.5938 | 8760 | 1720.1251 | 21393.0373 | 4672.1658 | 2638.1054 | 0 | 0 | 0 | -1576.2703 | 0 | 2869.0863 | 8760 | 7524.2456 | 0 | 0 | 7524.4058 | 4684.7054 | 5271.1383 | 23686.3748 | 14268.6905 | 1976.5787 | 18938.8743 | 8760 | 28968.2789 | 1278.175 | 0 | 2104.7 | 2449146.8649 | 155104.6654 | 917.85
52 | E | SOR | NAP | CC | ET | WC | R600 | 3.703 | 37 | 1.85 | 8760 | 209864.3398 | 79798.5 | 123169.5445 | 65533.1035 | 62307.5625 | 128290 | 442600.5 | 179606 | 11546.1 | 59334.125 | 8760 | 1720.1251 | 19872.5667 | 5663.6463 | 3146.5975 | 0 | 0 | 0 | -1548.0306 | 0 | 2864.1626 | 8760 | 7524.358 | 0 | 0 | 7524.4058 | 4684.7054 | 5252.8997 | 23672.7383 | 14217.8313 | 1972.7372 | 17478.7773 | 8760 | 28967.9773 | 1282.9 | 0 | 2104.7 | 2449100.3667 | 155104.6654 | 798.45
53 | E | SOR | NAP | CC | ET | WC | R600 | 3.703 | 30.5 | 1.55 | 8760 | 205255.5358 | 95692.05 | 131998.7059 | 65533.1035 | 62307.5625 | 128885 | 444653.25 | 180439 | 11599.65 | 59609.3125 | 8760 | 1720.1251 | 18056.7435 | 7006.2381 | 3676.0579 | 0 | 0 | 0 | -1513.767 | 0 | 2844.7293 | 8760 | 7521.4835 | 0 | 0 | 7524.4058 | 4684.7054 | 5232.2793 | 23633.8219 | 14141.2978 | 1968.7435 | 15757.2091 | 8760 | 28946.7883 | 1288.85 | 0 | 2104.7 | 2449029.3657 | 155104.6654 | 652.125
54 | E | SOR | NAP | CC | ET | WC | R600 | 3.703 | 24 | 1.2 | 8760 | 200200.1804 | 117024.75 | 143849.4158 | 65533.1035 | 62307.5625 | 129550 | 446947.5 | 181370 | 11659.5 | 59916.875 | 8760 | 1720.1251 | 15627.8738 | 8998.1293 | 4289.2479 | 0 | 0 | 0 | -1465.5653 | 0 | 2801.8055 | 8760 | 7522.5037 | 0 | 0 | 7524.4058 | 4684.7054 | 5191.2198 | 23621.848 | 14080.6299 | 1961.6711 | 13459.0207 | 8760 | 28953.1843 | 1295.5 | 0 | 2104.7 | 2449018.8488 | 155104.6654 | 502.275
55 | E | SOR | NAP | CC | ET | WC | R60 | 3.703 | 17.5 | 0.9 | 8760 | 196694.5941 | 135930.15 | 154351.7156 | 65533.1035 | 62307.5625 | 130257.5 | 449388.375 | 182360.5 | 11723.175 | 60244.0938 | 8760 | 1720.1251 | 12696.3282 | 10685.1506 | 4974.5205 | 0 | 0 | 0 | -1398.2645 | 0 | 2707.8975 | 8760 | 7520.8131 | 0 | 0 | 7524.4058 | 4684.7054 | 5133.5954 | 23603.01 | 14006.6265 | 1950.9688 | 10720.4536 | 8760 | 28953.275 | 1302.575 | 0 | 2104.7 | 2448947.3366 | 155104.6654 | 329.45
56 | E | SOR | NAP | CC | ET | WC | R60 | 3.703 | 43.5 | 1.1 | 8760 | 200006.5181 | 82629.45 | 124742.1897 | 65533.1035 | 62307.5625 | 127922.5 | 441332.625 | 179091.5 | 11513.025 | 59164.1562 | 8760 | 1720.1251 | 19401.6347 | 5982.0141 | 3387.9465 | 0 | 0 | 0 | -1565.1282 | 0 | 2929.14 | 8760 | 7524.8024 | 0 | 0 | 7524.4058 | 4684.7054 | 5271.4609 | 23763.1624 | 14298.6821 | 1970.0528 | 16923.7241 | 8760 | 29044.2095 | 1279.225 | 0 | 2104.7 | 2449138.0973 | 155104.6654 | 1008.725
57 | E | SOR | NAP | CC | ET | WC | R60 | 3.703 | 37 | 0.95 | 8760 | 196596.8879 | 91596.15 | 129723.3576 | 65533.1035 | 62307.5625 | 128240 | 442428 | 179536 | 11541.6 | 59311 | 8760 | 1720.1251 | 18323.0695 | 6570.8143 | 3789.1989 | 0 | 0 | 0 | -1540.3402 | 0 | 2929.7411 | 8760 | 7524.0856 | 0 | 0 | 7524.4058 | 4684.7054 | 5247.4266 | 23740.3548 | 14253.5786 | 1967.0508 | 15878.3602 | 8760 | 29029.1106 | 1282.4 | 0 | 2104.7 | 2449139.7153 | 155104.6654 | 889.675
58 | E | SOR | NAP | CC | ET | WC | R60 | 3.703 | 30.5 | 0.75 | 8760 | 192162.6617 | 105871.05 | 137653.3289 | 65533.1035 | 62307.5625 | 128762.5 | 444230.625 | 180267.5 | 11588.625 | 59552.6562 | 8760 | 1720.1251 | 16675.2303 | 7635.8077 | 4283.7041 | 0 | 0 | 0 | -1507.3065 | 0 | 2920.2183 | 8760 | 7523.6263 | 0 | 0 | 7524.4058 | 4684.7054 | 5211.047 | 23702.3976 | 14185.5573 | 1960.6943 | 14315.1141 | 8760 | 29005.7893 | 1287.625 | 0 | 2104.7 | 2449075.8051 | 155104.6654 | 770.775
59 | E | SOR | NAP | CC | ET | WC | R60 | 3.703 | 24 | 0.6 | 8760 | 188275.4462 | 126940.5 | 149357.7985 | 65533.1035 | 62307.5625 | 129347.5 | 446248.875 | 181086.5 | 11641.275 | 59823.2188 | 8760 | 1720.1251 | 14506.9811 | 9353.4904 | 4873.96 | 0 | 0 | 0 | -1471.832 | 0 | 2897.3198 | 8760 | 7521.3496 | 0 | 0 | 7524.4058 | 4684.7054 | 5165.9938 | 23654.6749 | 14105.0793 | 1952.0167 | 12263.2956 | 8760 | 28973.1599 | 1293.475 | 0 | 2104.7 | 2449008.4929 | 155104.6654 | 624.15
60 | E | SOR | NAP | CC | ET | WC | R60 | 3.703 | 17.5 | 0.45 | 8760 | 185308.0623 | 146232 | 160074.584 | 65533.1035 | 62307.5625 | 130067.5 | 448732.875 | 182094.5 | 11706.075 | 60156.2188 | 8760 | 1720.1251 | 11784.5688 | 11239.6943 | 5585.3146 | 0 | 0 | 0 | -1445.1286 | 0 | 2820.8562 | 8760 | 7520.9919 | 0 | 0 | 7524.4058 | 4684.7054 | 5093.5868 | 23619.9386 | 14032.0373 | 1936.2758 | 9715.785 | 8760 | 28963.8534 | 1300.675 | 0 | 2104.7 | 2448979.5769 | 155104.6654 | 455.25
61 | E | SOR | NAP | CC | FP | HC | R100 | 2.2447 | 31 | 2.3 | 8760 | 197197.4081 | 92321.1 | 130126.0807 | 65533.1035 | 92407.6909 | 95945 | 268646 | 134323 | 8635.05 | 568062.2005 | 8760 | 1720.1251 | 15791.5673 | 3795.3119 | 4242.7176 | 0 | 0 | 0 | -1447.3052 | 0 | 2441.347 | 8760 | 4792.2505 | 0 | 0 | 4791.7033 | 6547.1955 | 3455.8354 | 13075.3143 | 9643.0943 | 1254.8974 | 13951.1143 | 8760 | 0 | 959.45 | 0 | 1854.725 | 1565109.7087 | 178372.614 | 415.725 | -1346.0301
62 | E | SOR | NAP | CC | FP | HC | R100 | 2.2447 | 26.5 | 2 | 8760 | 192199.3735 | 105922.35 | 137681.827 | 65533.1035 | 92407.6909 | 96455 | 270074 | 135037 | 8680.95 | 571074.4599 | 8760 | 1720.1251 | 14386.0862 | 4732.4713 | 4765.2292 | 0 | 0 | 0 | -1416.4167 | 0 | 2437.1827 | 8760 | 4792.2256 | 0 | 0 | 4791.7033 | 6547.1955 | 3448.6546 | 13073.6854 | 9608.1908 | 1254.9365 | 12604.8372 | 8760 | 0 | 964.55 | 0 | 1854.725 | 1565097.8127 | 178372.614 | 349.975 | -1327.6834
63 | E | SOR | NAP | CC | FP | HC | R100 | 2.2447 | 21.5 | 1.6 | 8760 | 186769.8091 | 124070.4 | 147763.4048 | 65533.1035 | 92407.6909 | 97022.5 | 271663 | 135831.5 | 8732.025 | 574414.6737 | 8760 | 1720.1251 | 12561.2303 | 6014.287 | 5432.0554 | 0 | 0 | 0 | -1377.2272 | 0 | 2426.2287 | 8760 | 4792.3278 | 0 | 0 | 4791.7033 | 6547.1955 | 3440.291 | 13075.8723 | 9576.8816 | 1253.9195 | 10858.5284 | 8760 | 0 | 970.225 | 0 | 1854.725 | 1565107.4209 | 178372.614 | 275.075 | -1311.7729
64 | E | SOR | NAP | CC | FP | HC | R100 | 2.2447 | 17 | 1.3 | 8760 | 183636.402 | 138943.35 | 156025.604 | 65533.1035 | 92407.6909 | 97457.5 | 272881 | 136440.5 | 8771.175 | 576977.3355 | 8760 | 1720.1251 | 10779.383 | 6988.2231 | 6103.651 | 0 | 0 | 0 | -1332.6572 | 0 | 2397.1528 | 8760 | 4792.0899 | 0 | 0 | 4791.7033 | 6547.1955 | 3427.1224 | 13066.0204 | 9547.8975 | 1252.7987 | 9170.2711 | 8760 | 0 | 974.575 | 0 | 1854.725 | 1565067.7977 | 178372.614 | 194.575 | -1309.8573
65 | E | SOR | NAP | CC | FP | HC | R100 | 2.2447 | 12.5 | 0.95 | 8760 | 182231.8925 | 153806.85 | 164282.5535 | 65533.1035 | 92407.6909 | 97890 | 274092 | 137046 | 8810.1 | 579496.2738 | 8760 | 1720.1251 | 8761.3088 | 7858.4241 | 6845.641 | 0 | 0 | 0 | -1274.8852 | 0 | 2340.9353 | 8760 | 4792.22 | 0 | 0 | 4791.7033 | 6547.1955 | 3407.0465 | 13046.7412 | 9525.7706 | 1250.2127 | 7288.1792 | 8760 | 0 | 978.9 | 0 | 1854.725 | 1565065.9642 | 178372.614 | 105.3 | -1312.5046
66 | E | SOR | NAP | CC | FP | HC | R100 | 2.2447 | 31 | 1.55 | 8760 | 191538.439 | 100194.3 | 134499.7891 | 65533.1035 | 92407.6909 | 95770 | 268156 | 134078 | 8619.3 | 567083.1438 | 8760 | 1720.1251 | 14933.8127 | 4340.7829 | 4715.0357 | 0 | 0 | 0 | -1451.4256 | 0 | 2484.0131 | 8760 | 4792.2963 | 0 | 0 | 4791.7033 | 6547.1955 | 3465.8712 | 13109.3352 | 9657.3321 | 1255.1746 | 13047.0874 | 8760 | 0 | 957.7 | 0 | 1854.725 | 1565090.3277 | 178372.614 | 453.15 | -1346.8843
67 | E | SOR | NAP | CC | FP | HC | R100 | 2.2447 | 26.5 | 1.35 | 8760 | 187907.1273 | 111175.2 | 140599.8824 | 65533.1035 | 92407.6909 | 96252.5 | 269507 | 134753.5 | 8662.725 | 569906.1897 | 8760 | 1720.1251 | 13768.4455 | 5024.1614 | 5139.9779 | 0 | 0 | 0 | -1422.3299 | 0 | 2479.2499 | 8760 | 4792.4136 | 0 | 0 | 4791.7033 | 6547.1955 | 3458.5189 | 13097.5535 | 9624.9017 | 1254.5803 | 11940.6064 | 8760 | 0 | 962.525 | 0 | 1854.725 | 1565129.2692 | 178372.614 | 384.35 | -1336.7534
68 | E | SOR | NAP | CC | FP | HC | R100 | 2.2447 | 21.5 | 1.1 | 8760 | 183875.0362 | 127086.3 | 149438.7931 | 65533.1035 | 92407.6909 | 96817.5 | 271089 | 135544.5 | 8713.575 | 573221.9568 | 8760 | 1720.1251 | 12155.8177 | 6191.0462 | 5720.2927 | 0 | 0 | 0 | -1384.9641 | 0 | 2466.0936 | 8760 | 4792.1893 | 0 | 0 | 4791.7033 | 6547.1955 | 3445.0018 | 13086.6082 | 9588.3953 | 1253.579 | 10411.5663 | 8760 | 0 | 968.175 | 0 | 1854.725 | 1565082.3011 | 178372.614 | 298.725 | -1322.6775
69 | E | SOR | NAP | CC | FP | HC | R100 | 2.2447 | 17 | 0.85 | 8760 | 180830.5927 | 142581.6 | 158046.7192 | 65533.1035 | 92407.6909 | 97320 | 272496 | 136248 | 8758.8 | 576172.7684 | 8760 | 1720.1251 | 10434.8141 | 7199.9105 | 6386.4016 | 0 | 0 | 0 | -1346.0833 | 0 | 2443.4576 | 8760 | 4792.278 | 0 | 0 | 4791.7033 | 6547.1955 | 3430.2107 | 13079.2158 | 9558.9163 | 1252.3919 | 8782.9142 | 8760 | 0 | 973.2 | 0 | 1854.725 | 1565084.2709 | 178372.614 | 219.9 | -1316.0053
70 | E | SOR | NAP | CC | FP | HC | R10 | 2.2447 | 12.5 | 0.65 | 8760 | 178753.4717 | 157688.1 | 166438.6597 | 65533.1035 | 92407.6909 | 97757.5 | 273721 | 136860.5 | 8798.175 | 578742.2742 | 8760 | 1720.1251 | 8443.8354 | 8091.956 | 7164.5451 | 0 | 0 | 0 | -1300.3608 | 0 | 2391.7547 | 8760 | 4791.9655 | 0 | 0 | 4791.7033 | 6547.1955 | 3410.2811 | 13063.9666 | 9529.8237 | 1249.0179 | 6920.7811 | 8760 | 0 | 977.575 | 0 | 1854.725 | 1565074.3227 | 178372.614 | 133.375 | -1314.6351
71 | E | SOR | NAP | CC | FP | HC | R10 | 2.2447 | 31 | 0.8 | 8760 | 180257.3699 | 113836.05 | 142078.0339 | 65533.1035 | 92407.6909 | 95680 | 267904 | 133952 | 8611.2 | 566565.2197 | 8760 | 1720.1251 | 13451.9652 | 5020.0474 | 5469.1331 | 0 | 0 | 0 | -1441.3657 | 0 | 2560.3315 | 8760 | 4792.2954 | 0 | 0 | 4791.7033 | 6547.1955 | 3464.8088 | 13152.2106 | 9682.7128 | 1254.5266 | 11512.6303 | 8760 | 0 | 956.8 | 0 | 1854.725 | 1565132.8536 | 178372.614 | 524.975 | -1354.2977
72 | E | SOR | NAP | CC | FP | HC | R10 | 2.2447 | 26.5 | 0.65 | 8760 | 176644.1391 | 124730.55 | 148130.1304 | 65533.1035 | 92407.6909 | 96045 | 268926 | 134463 | 8644.05 | 568704.8893 | 8760 | 1720.1251 | 12357.9856 | 5570.9794 | 6014.8497 | 0 | 0 | 0 | -1420.6955 | 0 | 2566.19 | 8760 | 4792.1903 | 0 | 0 | 4791.7033 | 6547.1955 | 3451.6279 | 13135.944 | 9650.5448 | 1253.117 | 10466.1609 | 8760 | 0 | 960.45 | 0 | 1854.725 | 1565118.0872 | 178372.614 | 468.925 | -1342.8585
73 | E | SOR | NAP | CC | FP | HC | R10 | 2.2447 | 21.5 | 0.55 | 8760 | 173182.2048 | 138956.85 | 156033.1035 | 65533.1035 | 92407.6909 | 96640 | 270592 | 135296 | 8697.6 | 572187.287 | 8760 | 1720.1251 | 10985.3748 | 6448.6508 | 6605.3447 | 0 | 0 | 0 | -1400.3348 | 0 | 2555.4792 | 8760 | 4792.5788 | 0 | 0 | 4791.7033 | 6547.1955 | 3438.1381 | 13111.4604 | 9607.0607 | 1252.1523 | 9174.0631 | 8760 | 0 | 966.4 | 0 | 1854.725 | 1565118.1052 | 178372.614 | 380.9 | -1326.5615
74 | E | SOR | NAP | CC | FP | HC | R10 | 2.2447 | 17 | 0.45 | 8760 | 171750.8166 | 154298.25 | 164555.5353 | 65533.1035 | 92407.6909 | 97147.5 | 272013 | 136006.5 | 8743.275 | 575164.7443 | 8760 | 1720.1251 | 9545.5201 | 7552.8334 | 7099.5622 | 0 | 0 | 0 | -1401.4162 | 0 | 2520.8219 | 8760 | 4792.5196 | 0 | 0 | 4791.7033 | 6547.1955 | 3424.4528 | 13107.1353 | 9576.7368 | 1250.1975 | 7834.8492 | 8760 | 0 | 971.475 | 0 | 1854.725 | 1565057.0384 | 178372.614 | 297.075 | -1312.274
75 | E | SOR | NAP | CC | FP | HC | R10 | 2.2447 | 12.5 | 0.3 | 8760 | 163131.3302 | 175217.85 | 176176.7605 | 65533.1035 | 92407.6909 | 97537.5 | 273105 | 136552.5 | 8778.375 | 577455.7174 | 8760 | 1720.1251 | 7152.2249 | 8508.2273 | 8334.2652 | 0 | 0 | 0 | -1431.0262 | 0 | 2555.5842 | 8760 | 4792.4565 | 0 | 0 | 4791.7033 | 6547.1955 | 3388.5968 | 13088.3509 | 9548.2431 | 1240.9971 | 5472.8323 | 8760 | 0 | 975.375 | 0 | 1854.725 | 1565085.9407 | 178372.614 | 243.05 | -1309.9563
76 | E | SOR | NAP | CC | FP | HC | R600 | 2.6378 | 31 | 2.3 | 8760 | 198148.2969 | 58777.65 | 111492.0731 | 65533.1035 | 55495.4426 | 106320 | 297696 | 148848 | 9568.8 | 630206.1091 | 8760 | 1720.1251 | 17372.8514 | 3399.9395 | 1784.5374 | 0 | 0 | 0 | -1569.8039 | 0 | 2854.0848 | 8760 | 5360.3601 | 0 | 0 | 5359.9812 | 3337.1316 | 4023.6529 | 14998.5257 | 10765.8479 | 1489.5629 | 15033.571 | 8760 | 0 | 1063.2 | 0 | 2104.7 | 1737562.4166 | 155104.6654 | 730.25 | -1367.6608
77 | E | SOR | NAP | CC | FP | HC | R600 | 2.6378 | 26.5 | 2 | 8760 | 196511.0561 | 72030.6 | 118854.3322 | 65533.1035 | 55495.4426 | 107057.5 | 299761 | 149880.5 | 9635.175 | 634530.9038 | 8760 | 1720.1251 | 16015.3657 | 4296.2345 | 2121.909 | 0 | 0 | 0 | -1537.9924 | 0 | 2829.567 | 8760 | 5360.4117 | 0 | 0 | 5359.9812 | 3337.1316 | 4009.5373 | 14980.2543 | 10718.6534 | 1489.0658 | 13760.9401 | 8760 | 0 | 1070.575 | 0 | 2104.7 | 1737547.319 | 155104.6654 | 607.925 | -1354.8828
78 | E | SOR | NAP | CC | FP | HC | R600 | 2.6378 | 21.5 | 1.6 | 8760 | 193923.9285 | 92556 | 130256.572 | 65533.1035 | 55495.4426 | 107757.5 | 301721 | 150860.5 | 9698.175 | 638661.2123 | 8760 | 1720.1251 | 14082.5337 | 5838.8215 | 2608.9855 | 0 | 0 | 0 | -1487.7876 | 0 | 2788.3925 | 8760 | 5360.4728 | 0 | 0 | 5359.9812 | 3337.1316 | 3986.4772 | 14986.0339 | 10681.825 | 1486.1306 | 11940.4429 | 8760 | 0 | 1077.575 | 0 | 2104.7 | 1737504.5171 | 155104.6654 | 477.25 | -1335.7728
79 | E | SOR | NAP | CC | FP | HC | R600 | 2.6378 | 17 | 1.3 | 8760 | 192822.6985 | 109393.2 | 139609.9484 | 65533.1035 | 55495.4426 | 108347.5 | 303373 | 151686.5 | 9751.275 | 642147.7292 | 8760 | 1720.1251 | 12098.5269 | 7133.2935 | 3118.5343 | 0 | 0 | 0 | -1434.399 | 0 | 2717.8553 | 8760 | 5359.9817 | 0 | 0 | 5359.9812 | 3337.1316 | 3960.209 | 14973.542 | 10642.7636 | 1484.0469 | 10096.2609 | 8760 | 0 | 1083.475 | 0 | 2104.7 | 1737532.7778 | 155104.6654 | 344.45 | -1333.5188
80 | E | SOR | NAP | CC | FP | HC | R600 | 2.6378 | 12.5 | 0.95 | 8760 | 192874.9505 | 127834.2 | 149854.2654 | 65533.1035 | 55495.4426 | 108942.5 | 305039 | 152519.5 | 9804.825 | 645659.2649 | 8760 | 1720.1251 | 9775.6464 | 8400.3432 | 3744.4266 | 0 | 0 | 0 | -1365.7054 | 0 | 2608.51 | 8760 | 5360.8171 | 0 | 0 | 5359.9812 | 3337.1316 | 3930.67 | 14975.3048 | 10610.8851 | 1480.6079 | 7964.5284 | 8760 | 0 | 1089.425 | 0 | 2104.7 | 1737502.7901 | 155104.6654 | 197.175 | -1325.897
81 | E | SOR | NAP | CC | FP | HC | R600 | 2.6378 | 31 | 1.55 | 8760 | 190274.6561 | 66777.75 | 115936.2768 | 65533.1035 | 55495.4426 | 106132.5 | 297171 | 148585.5 | 9551.925 | 629143.4468 | 8760 | 1720.1251 | 16508.4496 | 4007.4296 | 2115.6969 | 0 | 0 | 0 | -1566.3762 | 0 | 2886.994 | 8760 | 5360.4239 | 0 | 0 | 5359.9812 | 3337.1316 | 4023.1284 | 15044.6635 | 10788.2018 | 1488.6187 | 14129.7043 | 8760 | 0 | 1061.325 | 0 | 2104.7 | 1737588.7138 | 155104.6654 | 790.15 | -1375.5376
82 | E | SOR | NAP | CC | FP | HC | R600 | 2.6378 | 26.5 | 1.35 | 8760 | 189893.3845 | 78165 | 122262.105 | 65533.1035 | 55495.4426 | 106805 | 299054 | 149527 | 9612.45 | 633085.853 | 8760 | 1720.1251 | 15352.5363 | 4771.305 | 2461.4514 | 0 | 0 | 0 | -1538.6531 | 0 | 2869.2099 | 8760 | 5360.3755 | 0 | 0 | 5359.9812 | 3337.1316 | 4014.0958 | 15020.726 | 10739.0052 | 1487.7445 | 13048.7065 | 8760 | 0 | 1068.05 | 0 | 2104.7 | 1737545.6383 | 155104.6654 | 671.35 | -1358.2506
83 | E | SOR | NAP | CC | FP | HC | R600 | 2.6378 | 21.5 | 1.1 | 8760 | 189589.8357 | 95065.65 | 131650.7291 | 65533.1035 | 55495.4426 | 107575 | 301210 | 150605 | 9681.75 | 637608.5433 | 8760 | 1720.1251 | 13689.0584 | 6011.3824 | 2880.6987 | 0 | 0 | 0 | -1499.6442 | 0 | 2830.4633 | 8760 | 5360.7209 | 0 | 0 | 5359.9812 | 3337.1316 | 3997.0277 | 15004.7606 | 10690.8986 | 1484.9167 | 11501.2125 | 8760 | 0 | 1075.75 | 0 | 2104.7 | 1737527.4793 | 155104.6654 | 519.8 | -1343.0001
84 | E | SOR | NAP | CC | FP | HC | R600 | 2.6378 | 17 | 0.85 | 8760 | 188700.9059 | 113131.35 | 141686.56 | 65533.1035 | 55495.4426 | 108185 | 302918 | 151459 | 9736.65 | 641200.8771 | 8760 | 1720.1251 | 11781.3086 | 7359.4748 | 3350.6807 | 0 | 0 | 0 | -1450.8497 | 0 | 2770.9712 | 8760 | 5360.3565 | 0 | 0 | 5359.9812 | 3337.1316 | 3971.5004 | 14991.6562 | 10655.137 | 1483.3217 | 9727.6966 | 8760 | 0 | 1081.85 | 0 | 2104.7 | 1737523.6624 | 155104.6654 | 390.925 | -1336.9733
85 | E | SOR | NAP | CC | FP | HC | R60 | 2.6378 | 12.5 | 0.65 | 8760 | 189620.7933 | 130029.3 | 151073.6841 | 65533.1035 | 55495.4426 | 108847.5 | 304773 | 152386.5 | 9796.275 | 645108.0034 | 8760 | 1720.1251 | 9558.8591 | 8649.7446 | 3898.786 | 0 | 0 | 0 | -1388.6239 | 0 | 2664.4981 | 8760 | 5360.6895 | 0 | 0 | 5359.9812 | 3337.1316 | 3935.5893 | 14985.4594 | 10617.1716 | 1478.8137 | 7694.3625 | 8760 | 0 | 1088.475 | 0 | 2104.7 | 1737513.1654 | 155104.6654 | 235.85 | -1320.7906
86 | E | SOR | NAP | CC | FP | HC | R60 | 2.6378 | 31 | 0.8 | 8760 | 178245.5618 | 80030.7 | 123298.5359 | 65533.1035 | 55495.4426 | 105885 | 296478 | 148239 | 9529.65 | 627708.8688 | 8760 | 1720.1251 | 15211.3626 | 4873.7513 | 2648.1647 | 0 | 0 | 0 | -1562.1672 | 0 | 2956.6837 | 8760 | 5360.0203 | 0 | 0 | 5359.9812 | 3337.1316 | 4023.2339 | 15096.6562 | 10824.7384 | 1486.0331 | 12785.0541 | 8760 | 0 | 1058.85 | 0 | 2104.7 | 1737580.2261 | 155104.6654 | 881.45 | -1388.1851
87 | E | SOR | NAP | CC | FP | HC | R60 | 2.6378 | 26.5 | 0.65 | 8760 | 177749.3826 | 89926.2 | 128795.6694 | 65533.1035 | 55495.4426 | 106412.5 | 297955 | 148977.5 | 9577.125 | 630811.3501 | 8760 | 1720.1251 | 14165.3042 | 5454.0378 | 3013.347 | 0 | 0 | 0 | -1535.9619 | 0 | 2950.4743 | 8760 | 5360.4093 | 0 | 0 | 5359.9812 | 3337.1316 | 4005.7093 | 15084.6801 | 10780.9355 | 1483.9217 | 11799.9374 | 8760 | 0 | 1064.125 | 0 | 2104.7 | 1737578.3543 | 155104.6654 | 784.45 | -1367.0234
88 | E | SOR | NAP | CC | FP | HC | R60 | 2.6378 | 21.5 | 0.55 | 8760 | 178433.6194 | 104760 | 137036.12 | 65533.1035 | 55495.4426 | 107217.5 | 300209 | 150104.5 | 9649.575 | 635530.0801 | 8760 | 1720.1251 | 12718.7184 | 6468.0421 | 3410.0389 | 0 | 0 | 0 | -1505.8431 | 0 | 2921.9026 | 8760 | 5360.6988 | 0 | 0 | 5359.9812 | 3337.1316 | 3984.3986 | 15042.8824 | 10716.6395 | 1480.5445 | 10463.4812 | 8760 | 0 | 1072.175 | 0 | 2104.7 | 1737542.7135 | 155104.6654 | 643.65 | -1354.305
89 | E | SOR | NAP | CC | FP | HC | R60 | 2.6378 | 17 | 0.45 | 8760 | 178857.1784 | 123952.95 | 147698.1592 | 65533.1035 | 55495.4426 | 107845 | 301966 | 150983 | 9706.05 | 639218.3786 | 8760 | 1720.1251 | 11019.1014 | 7801.9954 | 3832.7103 | 0 | 0 | 0 | -1487.0273 | 0 | 2865.7494 | 8760 | 5360.1205 | 0 | 0 | 5359.9812 | 3337.1316 | 3957.7542 | 15028.226 | 10677.4514 | 1477.4264 | 8891.2398 | 8760 | 0 | 1078.45 | 0 | 2104.7 | 1737510.2174 | 155104.6654 | 504 | -1340.249
90 | E | SOR | NAP | CC | FP | HC | R60 | 2.6378 | 12.5 | 0.3 | 8760 | 175168.9719 | 144813.15 | 159286.3866 | 65533.1035 | 55495.4426 | 108402.5 | 303527 | 151763.5 | 9756.225 | 642492.5742 | 8760 | 1720.1251 | 8564.3813 | 9094.8846 | 4792.666 | 0 | 0 | 0 | -1494.3535 | 0 | 2903.4257 | 8760 | 5360.2575 | 0 | 0 | 5359.9812 | 3337.1316 | 3901.9073 | 15019.8331 | 10644.4789 | 1467.2565 | 6474.0772 | 8760 | 0 | 1084.025 | 0 | 2104.7 | 1737487.9743 | 155104.6654 | 395.85 | -1324.7453
91 | E | SOR | NAP | CC | FP | WC | R100 | 3.1512 | 43.5 | 3.25 | 8760 | 230378.7662 | 90590.4 | 129164.6448 | 65533.1035 | 105813.8734 | 113882.5 | 392894.625 | 159435.5 | 10249.425 | 52670.6562 | 8760 | 1720.1251 | 21056.3901 | 3996.6594 | 5567.4 | 0 | 0 | 0 | -1457.6063 | 0 | 2418.1244 | 8760 | 6725.2655 | 0 | 0 | 6726.6505 | 9191.0315 | 4585.3352 | 20808.9827 | 12701.5519 | 1700.942 | 19145.0079 | 8760 | 25646.5669 | 1138.825 | 0 | 1854.725 | 2206382.7054 | 178372.614 | 489.175
92 | E | SOR | NAP | CC | FP | WC | R100 | 3.1512 | 37 | 2.8 | 8760 | 218647.3583 | 105262.2 | 137315.1014 | 65533.1035 | 105813.8734 | 114405 | 394697.25 | 160167 | 10296.45 | 52912.3125 | 8760 | 1720.1251 | 19197.3095 | 5166.2715 | 6266.8558 | 0 | 0 | 0 | -1423.9132 | 0 | 2426.4467 | 8760 | 6723.5728 | 0 | 0 | 6726.6505 | 9191.0315 | 4565.6485 | 20793.8185 | 12647.3906 | 1698.6081 | 17342.2155 | 8760 | 25647.7126 | 1144.05 | 0 | 1854.725 | 2206321.4721 | 178372.614 | 417.375
93 | E | SOR | NAP | CC | FP | WC | R100 | 3.1512 | 30.5 | 2.3 | 8760 | 207329.6474 | 123593.85 | 147498.6725 | 65533.1035 | 105813.8734 | 114997.5 | 396741.375 | 160996.5 | 10349.775 | 53186.3438 | 8760 | 1720.1251 | 16962.6225 | 6729.8792 | 7112.3035 | 0 | 0 | 0 | -1387.2957 | 0 | 2427.6753 | 8760 | 6723.6236 | 0 | 0 | 6726.6505 | 9191.0315 | 4552.4217 | 20787.0507 | 12594.8447 | 1696.0723 | 15178.1396 | 8760 | 25655.8445 | 1149.975 | 0 | 1854.725 | 2206304.3936 | 178372.614 | 345.125
94 | E | SOR | NAP | CC | FP | WC | R100 | 3.1512 | 24 | 1.8 | 8760 | 197997.3482 | 143440.2 | 158523.6874 | 65533.1035 | 105813.8734 | 115410 | 398164.5 | 161574 | 10386.9 | 53377.125 | 8760 | 1720.1251 | 14454.6216 | 8590.5608 | 8048.0873 | 0 | 0 | 0 | -1343.8954 | 0 | 2414.8893 | 8760 | 6722.8092 | 0 | 0 | 6726.6505 | 9191.0315 | 4531.0919 | 20777.4914 | 12553.4971 | 1693.2971 | 12759.5879 | 8760 | 25660.4792 | 1154.1 | 0 | 1854.725 | 2206240.0299 | 178372.614 | 262.975
95 | E | SOR | NAP | CC | FP | WC | R100 | 3.1512 | 17.5 | 1.3 | 8760 | 191519.5687 | 160569 | 168039.053 | 65533.1035 | 105813.8734 | 115812.5 | 399553.125 | 162137.5 | 10423.125 | 53563.2812 | 8760 | 1720.1251 | 11682.9292 | 9771.4254 | 9086.2653 | 0 | 0 | 0 | -1284.687 | 0 | 2371.9521 | 8760 | 6721.5777 | 0 | 0 | 6726.6505 | 9191.0315 | 4493.6945 | 20761.3275 | 12507.7193 | 1686.1824 | 10116.9004 | 8760 | 25657.7336 | 1158.125 | 0 | 1854.725 | 2206191.4016 | 178372.614 | 159
96 | E | SOR | NAP | CC | FP | WC | R100 | 3.1512 | 43.5 | 2.2 | 8760 | 222871.3479 | 99144 | 133916.328 | 65533.1035 | 105813.8734 | 113990 | 393265.5 | 159586 | 10259.1 | 52720.375 | 8760 | 1720.1251 | 19807.5395 | 4776.8533 | 6201.002 | 0 | 0 | 0 | -1459.9903 | 0 | 2464.9724 | 8760 | 6725.1104 | 0 | 0 | 6726.6505 | 9191.0315 | 4598.9002 | 20850.2524 | 12709.2241 | 1699.8085 | 17844.8332 | 8760 | 25684.8582 | 1139.9 | 0 | 1854.725 | 2206367.872 | 178372.614 | 524.375
97 | E | SOR | NAP | CC | FP | WC | R100 | 3.1512 | 37 | 1.85 | 8760 | 212602.8204 | 111809.7 | 140952.3589 | 65533.1035 | 105813.8734 | 114355 | 394524.75 | 160097 | 10291.95 | 52889.1875 | 8760 | 1720.1251 | 18178.7107 | 5745.4803 | 6799.3236 | 0 | 0 | 0 | -1429.1354 | 0 | 2474.0866 | 8760 | 6724.4651 | 0 | 0 | 6726.6505 | 9191.0315 | 4585.0557 | 20837.9059 | 12669.2896 | 1697.7777 | 16266.3478 | 8760 | 25687.4021 | 1143.55 | 0 | 1854.725 | 2206325.8711 | 178372.614 | 455.175
98 | E | SOR | NAP | CC | FP | WC | R100 | 3.1512 | 30.5 | 1.55 | 8760 | 203342.8432 | 126960.75 | 149369.0478 | 65533.1035 | 105813.8734 | 114812.5 | 396103.125 | 160737.5 | 10333.125 | 53100.7812 | 8760 | 1720.1251 | 16302.9456 | 7040.1827 | 7518.2456 | 0 | 0 | 0 | -1392.7511 | 0 | 2466.0781 | 8760 | 6723.8017 | 0 | 0 | 6726.6505 | 9191.0315 | 4561.7055 | 20812.9229 | 12618.0566 | 1694.4871 | 14469.8713 | 8760 | 25672.6148 | 1148.125 | 0 | 1854.725 | 2206298.6358 | 178372.614 | 378.55
99 | E | SOR | NAP | CC | FP | WC | R100 | 3.1512 | 24 | 1.2 | 8760 | 194920.3084 | 145967.4 | 159927.5938 | 65533.1035 | 105813.8734 | 115260 | 397647 | 161364 | 10373.4 | 53307.75 | 8760 | 1720.1251 | 13973.6163 | 8755.3737 | 8368.3946 | 0 | 0 | 0 | -1350.1792 | 0 | 2453.9583 | 8760 | 6722.2547 | 0 | 0 | 6726.6505 | 9191.0315 | 4534.0378 | 20796.0121 | 12567.7405 | 1691.1578 | 12235.0487 | 8760 | 25667.0279 | 1152.6 | 0 | 1854.725 | 2206245.5622 | 178372.614 | 290.45
100 | E | SOR | NAP | CC | FP | WC | R10 | 3.1512 | 17.5 | 0.9 | 8760 | 188200.4835 | 162787.05 | 169271.2209 | 65533.1035 | 105813.8734 | 115745 | 399320.25 | 162043 | 10417.05 | 53532.0625 | 8760 | 1720.1251 | 11322.5788 | 10034.5512 | 9414.1181 | 0 | 0 | 0 | -1296.8261 | 0 | 2412.5679 | 8760 | 6721.1429 | 0 | 0 | 6726.6505 | 9191.0315 | 4495.6657 | 20771.3681 | 12514.4894 | 1684.1251 | 9713.6695 | 8760 | 25662.1313 | 1157.45 | 0 | 1854.725 | 2206214.5872 | 178372.614 | 184.4
101 | E | SOR | NAP | CC | FP | WC | R10 | 3.1512 | 43.5 | 1.1 | 8760 | 207878.3682 | 115014.6 | 142732.7402 | 65533.1035 | 105813.8734 | 114115 | 393696.75 | 159761 | 10270.35 | 52778.1875 | 8760 | 1720.1251 | 17527.058 | 5977.5394 | 7223.3155 | 0 | 0 | 0 | -1440.1885 | 0 | 2536.8478 | 8760 | 6725.2524 | 0 | 0 | 6726.6505 | 9191.0315 | 4593.7569 | 20910.1168 | 12725.9769 | 1696.5411 | 15527.8789 | 8760 | 25741.6791 | 1141.15 | 0 | 1854.725 | 2206385.0206 | 178372.614 | 598.65
102 | E | SOR | NAP | CC | FP | WC | R10 | 3.1512 | 37 | 0.95 | 8760 | 200328.0435 | 125274.6 | 148432.3602 | 65533.1035 | 105813.8734 | 114380 | 394611 | 160132 | 10294.2 | 52900.75 | 8760 | 1720.1251 | 16351.94 | 6602.8099 | 7753.4248 | 0 | 0 | 0 | -1417.1012 | 0 | 2543.7877 | 8760 | 6725.2424 | 0 | 0 | 6726.6505 | 9191.0315 | 4574.1426 | 20890.3356 | 12693.1238 | 1694.3759 | 14390.9185 | 8760 | 25734.2629 | 1143.8 | 0 | 1854.725 | 2206351.5866 | 178372.614 | 530.7
103 | E | SOR | NAP | CC | FP | WC | R10 | 3.1512 | 30.5 | 0.75 | 8760 | 191290.9221 | 140013.9 | 156620.3143 | 65533.1035 | 105813.8734 | 114730 | 395818.5 | 160622 | 10325.7 | 53062.625 | 8760 | 1720.1251 | 14647.162 | 7609.2639 | 8543.358 | 0 | 0 | 0 | -1388.7258 | 0 | 2551.201 | 8760 | 6724.1904 | 0 | 0 | 6726.6505 | 9191.0315 | 4543.6467 | 20862.8267 | 12645.8492 | 1689.4455 | 12748.0818 | 8760 | 25714.0432 | 1147.3 | 0 | 1854.725 | 2206319.805 | 178372.614 | 466.4
104 | E | SOR | NAP | CC | FP | WC | R10 | 3.1512 | 24 | 0.6 | 8760 | 183213.5354 | 158207.85 | 166727.3905 | 65533.1035 | 105813.8734 | 115137.5 | 397224.375 | 161192.5 | 10362.375 | 53251.0938 | 8760 | 1720.1251 | 12600.1796 | 9037.0811 | 9399.437 | 0 | 0 | 0 | -1364.4276 | 0 | 2546.3282 | 8760 | 6723.1202 | 0 | 0 | 6726.6505 | 9191.0315 | 4512.7347 | 20831.5763 | 12590.7763 | 1683.4272 | 10788.5469 | 8760 | 25691.1084 | 1151.375 | 0 | 1854.725 | 2206264.3336 | 178372.614 | 375.725
105 | E | SOR | NAP | CC | FP | WC | R10 | 3.1512 | 17.5 | 0.45 | 8760 | 177722.9875 | 174424.05 | 175735.7899 | 65533.1035 | 105813.8734 | 115630 | 398923.5 | 161882 | 10406.7 | 53478.875 | 8760 | 1720.1251 | 10267.3396 | 10743.4408 | 10289.059 | 0 | 0 | 0 | -1362.7237 | 0 | 2497.6394 | 8760 | 6721.6199 | 0 | 0 | 6726.6505 | 9191.0315 | 4466.7697 | 20794.1348 | 12533.4648 | 1669.7923 | 8592.303 | 8760 | 25672.835 | 1156.3 | 0 | 1854.725 | 2206209.6639 | 178372.614 | 271.4
106 | E | SOR | NAP | CC | FP | WC | R600 | 3.703 | 43.5 | 3.25 | 8760 | 231078.2016 | 70071.75 | 117766.1548 | 65533.1035 | 62307.5625 | 128297.5 | 442626.375 | 179616.5 | 11546.775 | 59337.5938 | 8760 | 1720.1251 | 20759.3513 | 4743.3135 | 2594.4365 | 0 | 0 | 0 | -1540.9305 | 0 | 2380.9054 | 8760 | 7524.4398 | 0 | 0 | 7524.4058 | 4684.7054 | 5241.3785 | 23620.0477 | 14200.5389 | 1973.0526 | 18772.4853 | 8760 | 28918.7005 | 1282.975 | 0 | 2104.7 | 2449117.2299 | 155104.6654 | 457.225
107 | E | SOR | NAP | CC | FP | WC | R600 | 3.703 | 37 | 2.8 | 8760 | 219663.9748 | 84095.55 | 125556.6354 | 65533.1035 | 62307.5625 | 128902.5 | 444713.625 | 180463.5 | 11601.225 | 59617.4062 | 8760 | 1720.1251 | 18990.1953 | 5990.7005 | 3036.8761 | 0 | 0 | 0 | -1502.6293 | 0 | 2382.2846 | 8760 | 7523.9434 | 0 | 0 | 7524.4058 | 4684.7054 | 5211.3573 | 23615.7974 | 14143.5559 | 1968.1347 | 17067.465 | 8760 | 28924.3456 | 1289.025 | 0 | 2104.7 | 2449087.5997 | 155104.6654 | 389.6
108 | E | SOR | NAP | CC | FP | WC | R600 | 3.703 | 30.5 | 2.3 | 8760 | 209510.0287 | 101869.65 | 135430.4771 | 65533.1035 | 62307.5625 | 129462.5 | 446645.625 | 181247.5 | 11651.625 | 59876.4062 | 8760 | 1720.1251 | 16872.8603 | 7673.1928 | 3563.1606 | 0 | 0 | 0 | -1459.6599 | 0 | 2379.5438 | 8760 | 7523.2302 | 0 | 0 | 7524.4058 | 4684.7054 | 5181.4107 | 23603.8515 | 14089.2352 | 1961.5215 | 15028.5522 | 8760 | 28932.1928 | 1294.625 | 0 | 2104.7 | 2449051.8521 | 155104.6654 | 315.175
109 | E | SOR | NAP | CC | FP | WC | R600 | 3.703 | 24 | 1.8 | 8760 | 200667.9718 | 121790.25 | 146496.7393 | 65533.1035 | 62307.5625 | 129965 | 448379.25 | 181951 | 11696.85 | 60108.8125 | 8760 | 1720.1251 | 14514.4484 | 9576.0793 | 4206.5034 | 0 | 0 | 0 | -1408.4397 | 0 | 2357.2271 | 8760 | 7522.7477 | 0 | 0 | 7524.4058 | 4684.7054 | 5145.1277 | 23601.7054 | 14041.3018 | 1957.3095 | 12771.4545 | 8760 | 28946.4841 | 1299.65 | 0 | 2104.7 | 2449024.0969 | 155104.6654 | 231.25
110 | E | SOR | NAP | CC | FP | WC | R600 | 3.703 | 17.5 | 1.3 | 8760 | 193593.1082 | 140186.7 | 156716.3079 | 65533.1035 | 62307.5625 | 130462.5 | 450095.625 | 182647.5 | 11741.625 | 60338.9062 | 8760 | 1720.1251 | 11765.8281 | 11062.9316 | 4971.8321 | 0 | 0 | 0 | -1339.1454 | 0 | 2304.9074 | 8760 | 7522.2045 | 0 | 0 | 7524.4058 | 4684.7054 | 5095.5768 | 23595.8815 | 13990.8426 | 1949.0461 | 10165.1603 | 8760 | 28959.1279 | 1304.625 | 0 | 2104.7 | 2448980.6001 | 155104.6654 | 130.175
111 | E | SOR | NAP | CC | FP | WC | R600 | 3.703 | 43.5 | 2.2 | 8760 | 222243.9435 | 80462.7 | 123538.5199 | 65533.1035 | 62307.5625 | 128400 | 442980 | 179760 | 11556 | 59385 | 8760 | 1720.1251 | 19419.3434 | 5652.2918 | 3038.3844 | 0 | 0 | 0 | -1531.6375 | 0 | 2417.3146 | 8760 | 7523.7299 | 0 | 0 | 7524.4058 | 4684.7054 | 5241.7107 | 23664.7227 | 14209.5336 | 1969.562 | 17392.5599 | 8760 | 28963.9809 | 1284 | 0 | 2104.7 | 2449138.9429 | 155104.6654 | 504.25
112 | E | SOR | NAP | CC | FP | WC | R600 | 3.703 | 37 | 1.85 | 8760 | 212505.9535 | 92624.85 | 130294.8195 | 65533.1035 | 62307.5625 | 128820 | 444429 | 180348 | 11593.8 | 59579.25 | 8760 | 1720.1251 | 17919.1083 | 6667.6685 | 3521.1409 | 0 | 0 | 0 | -1500.1226 | 0 | 2419.7866 | 8760 | 7524.4916 | 0 | 0 | 7524.4058 | 4684.7054 | 5221.8773 | 23662.1976 | 14168.5628 | 1965.3817 | 15949.8405 | 8760 | 28968.3954 | 1288.2 | 0 | 2104.7 | 2449102.9873 | 155104.6654 | 433.625
113 | E | SOR | NAP | CC | FP | WC | R600 | 3.703 | 30.5 | 1.55 | 8760 | 204339.5213 | 107130.6 | 138353.0322 | 65533.1035 | 62307.5625 | 129297.5 | 446076.375 | 181016.5 | 11636.775 | 59800.0938 | 8760 | 1720.1251 | 16192.3504 | 7981.5075 | 4020.5419 | 0 | 0 | 0 | -1461.1141 | 0 | 2415.1727 | 8760 | 7522.344 | 0 | 0 | 7524.4058 | 4684.7054 | 5192.7697 | 23634.445 | 14109.3888 | 1960.6132 | 14300.6735 | 8760 | 28956.5515 | 1292.975 | 0 | 2104.7 | 2449055.3621 | 155104.6654 | 352.5
114 | E | SOR | NAP | CC | FP | WC | R600 | 3.703 | 24 | 1.2 | 8760 | 196576.1973 | 125986.05 | 148827.5839 | 65533.1035 | 62307.5625 | 129860 | 448017 | 181804 | 11687.4 | 60060.25 | 8760 | 1720.1251 | 13996.4977 | 9808.6329 | 4557.6989 | 0 | 0 | 0 | -1411.1028 | 0 | 2394.4044 | 8760 | 7522.5523 | 0 | 0 | 7524.4058 | 4684.7054 | 5156.0748 | 23621.6574 | 14053.693 | 1956.3417 | 12211.8223 | 8760 | 28962.6789 | 1298.6 | 0 | 2104.7 | 2449013.6841 | 155104.6654 | 262.8
115 | E | SOR | NAP | CC | FP | WC | R60 | 3.703 | 17.5 | 0.9 | 8760 | 190128.6701 | 143376.75 | 158488.4398 | 65533.1035 | 62307.5625 | 130387.5 | 449836.875 | 182542.5 | 11734.875 | 60304.2188 | 8760 | 1720.1251 | 11405.8422 | 11358.542 | 5201.9572 | 0 | 0 | 0 | -1345.7009 | 0 | 2344.8234 | 8760 | 7522.0625 | 0 | 0 | 7524.4058 | 4684.7054 | 5097.4045 | 23604.2073 | 13999.3982 | 1945.4675 | 9765.1863 | 8760 | 28963.9642 | 1303.875 | 0 | 2104.7 | 2449009.803 | 155104.6654 | 157.525
116 | E | SOR | NAP | CC | FP | WC | R60 | 3.703 | 43.5 | 1.1 | 8760 | 206469.9703 | 97498.35 | 133002.139 | 65533.1035 | 62307.5625 | 128557.5 | 443523.375 | 179980.5 | 11570.175 | 59457.8438 | 8760 | 1720.1251 | 17219.6089 | 6977.4261 | 3928.7365 | 0 | 0 | 0 | -1503.6232 | 0 | 2470.4015 | 8760 | 7524.1262 | 0 | 0 | 7524.4058 | 4684.7054 | 5231.166 | 23732.2208 | 14228.3653 | 1963.7541 | 15185.0103 | 8760 | 29033.2653 | 1285.575 | 0 | 2104.7 | 2449143.1687 | 155104.6654 | 587.375
117 | E | SOR | NAP | CC | FP | WC | R60 | 3.703 | 37 | 0.95 | 8760 | 199657.4818 | 106396.2 | 137945.0594 | 65533.1035 | 62307.5625 | 128852.5 | 444541.125 | 180393.5 | 11596.725 | 59594.2812 | 8760 | 1720.1251 | 16164.912 | 7643.3036 | 4255.2312 | 0 | 0 | 0 | -1476.1897 | 0 | 2481.356 | 8760 | 7523.5554 | 0 | 0 | 7524.4058 | 4684.7054 | 5205.7199 | 23712.5557 | 14188.6704 | 1959.4846 | 14160.6886 | 8760 | 29019.8063 | 1288.525 | 0 | 2104.7 | 2449125.129 | 155104.6654 | 514.7
118 | E | SOR | NAP | CC | FP | WC | R60 | 3.703 | 30.5 | 0.75 | 8760 | 191543.4942 | 120290.4 | 145663.5448 | 65533.1035 | 62307.5625 | 129232.5 | 445852.125 | 180925.5 | 11630.925 | 59770.0312 | 8760 | 1720.1251 | 14612.3018 | 8707.002 | 4710.3434 | 0 | 0 | 0 | -1441.255 | 0 | 2481.2233 | 8760 | 7522.7993 | 0 | 0 | 7524.4058 | 4684.7054 | 5165.5098 | 23683.9474 | 14137.4912 | 1950.9645 | 12680.5468 | 8760 | 28999.9279 | 1292.325 | 0 | 2104.7 | 2449086.9337 | 155104.6654 | 447.075
119 | E | SOR | NAP | CC | FP | WC | R60 | 3.703 | 24 | 0.6 | 8760 | 184156.7862 | 137659.5 | 155312.4015 | 65533.1035 | 62307.5625 | 129707.5 | 447490.875 | 181590.5 | 11673.675 | 59989.7188 | 8760 | 1720.1251 | 12681.5519 | 10230.7151 | 5247.6637 | 0 | 0 | 0 | -1408.2065 | 0 | 2469.538 | 8760 | 7523.155 | 0 | 0 | 7524.4058 | 4684.7054 | 5118.4442 | 23651.4733 | 14079.3241 | 1942.3957 | 10846.0947 | 8760 | 28982.3399 | 1297.075 | 0 | 2104.7 | 2449035.6526 | 155104.6654 | 353.8
120 | E | SOR | NAP | CC | FP | WC | R60 | 3.703 | 17.5 | 0.45 | 8760 | 178883.8191 | 153357.3 | 164032.8201 | 65533.1035 | 62307.5625 | 130262.5 | 449405.625 | 182367.5 | 11723.625 | 60246.4062 | 8760 | 1720.1251 | 10327.2699 | 11994.0161 | 5884.2814 | 0 | 0 | 0 | -1391.2067 | 0 | 2427.3607 | 8760 | 7521.622 | 0 | 0 | 7524.4058 | 4684.7054 | 5049.2201 | 23625.1413 | 14016.6985 | 1925.8297 | 8628.0207 | 8760 | 28968.7994 | 1302.625 | 0 | 2104.7 | 2449000.0107 | 155104.6654 | 252.125
121 | E | SOR | NAP | FC | ET | WC | OFF0 | 0.20777 | 25.5 | 1.9 | 8760 | 184813.4186 | 18755.55 | 89259.0554 | 0 | 27899.3122 | 132492.5 | 457099.125 | 185489.5 | 11924.325 | 490222.25 | 8760 | 1720.1251 | 16614.8297 | 2016.3798 | 4.2605 | 0 | 0 | 0 | -1703.0591 | 0 | 3051.3387 | 8760 | 5200.6578 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 32847.7098 | 13177.5081 | 0 | 14077.7239 | 8760 | 45679.127 | 1324.925 | 0 | 2468.675 | 1946603.356 | 110654.3789 | 682.475
122 | E | SOR | NAP | FC | ET | WC | OFF0 | 0.20777 | 21.5 | 1.6 | 8760 | 185661.9557 | 30315.6 | 95680.8772 | 0 | 27899.3122 | 134405 | 463697.25 | 188167 | 12096.45 | 497298.5 | 8760 | 1720.1251 | 15260.041 | 3473.3904 | 5.2493 | 0 | 0 | 0 | -1670.1527 | 0 | 3022.4446 | 8760 | 5200.7045 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33039.1348 | 13055.1184 | 0 | 12804.8031 | 8760 | 46041.9992 | 1344.05 | 0 | 2468.675 | 1946609.0363 | 110654.3789 | 566.6
123 | E | SOR | NAP | FC | ET | WC | OFF0 | 0.20777 | 18 | 1.35 | 8760 | 186557.6147 | 43418.7 | 102959.8919 | 0 | 27899.3122 | 136187.5 | 469846.875 | 190662.5 | 12256.875 | 503893.75 | 8760 | 1720.1251 | 13770.923 | 5233.5504 | 26.0452 | 0 | 0 | 0 | -1635.9698 | 0 | 2987.9797 | 8760 | 5200.7882 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33256.9597 | 12961.1412 | 0 | 11405.0997 | 8760 | 46415.588 | 1361.875 | 0 | 2468.675 | 1946782.3797 | 110654.3789 | 448.2
124 | E | SOR | NAP | FC | ET | WC | OFF0 | 0.20777 | 14 | 1.05 | 8760 | 186954.1017 | 56928.15 | 110464.6416 | 0 | 27899.3122 | 138025 | 476186.25 | 193235 | 12422.25 | 510692.5 | 8760 | 1720.1251 | 11621.1671 | 6897.276 | 92.5575 | 0 | 0 | 0 | -1590.7785 | 0 | 2930.4051 | 8760 | 5200.7103 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33514.2835 | 12853.8524 | 0 | 9390.1635 | 8760 | 46832.9819 | 1380.25 | 0 | 2468.675 | 1947247.316 | 110654.3789 | 317.85
125 | E | SOR | NAP | FC | ET | WC | OFF0 | 0.20777 | 10 | 0.75 | 8760 | 186576.2596 | 72925.65 | 119351.5491 | 0 | 27899.3122 | 139555 | 481464.75 | 195377 | 12559.95 | 516353.5 | 8760 | 1720.1251 | 8991.7003 | 8865.8243 | 199.9656 | 0 | 0 | 0 | -1522.0329 | 0 | 2826.2347 | 8760 | 5200.7862 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33746.1541 | 12758.1517 | 0 | 6943.733 | 8760 | 47211.0414 | 1395.55 | 0 | 2468.675 | 1947055.8424 | 110654.3789 | 190.95
126 | E | SOR | NAP | FC | ET | WC | OFF0 | 0.20777 | 25.5 | 1.3 | 8760 | 181641.8792 | 21628.35 | 90854.949 | 0 | 27899.3122 | 132685 | 457763.25 | 185759 | 11941.65 | 490934.5 | 8760 | 1720.1251 | 16265.2528 | 2317.7802 | 13.4399 | 0 | 0 | 0 | -1684.8936 | 0 | 3058.9176 | 8760 | 5200.6978 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 32900.9722 | 13201.96 | 0 | 13723.6636 | 8760 | 45748.4893 | 1326.85 | 0 | 2468.675 | 1946313.8159 | 110654.3789 | 705.25
127 | E | SOR | NAP | FC | ET | WC | OFF0 | 0.20777 | 21.5 | 1.1 | 8760 | 183046.5451 | 32220.45 | 96739.0567 | 0 | 27899.3122 | 134222.5 | 463067.625 | 187911.5 | 12080.025 | 496623.25 | 8760 | 1720.1251 | 14981.3443 | 3605.5481 | 28.9181 | 0 | 0 | 0 | -1655.2862 | 0 | 3029.4935 | 8760 | 5200.7934 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33068.7591 | 13086.828 | 0 | 12528.3812 | 8760 | 46049.6518 | 1342.225 | 0 | 2468.675 | 1946672.9793 | 110654.3789 | 592.225
128 | E | SOR | NAP | FC | ET | WC | OFF0 | 0.20777 | 18 | 0.9 | 8760 | 183584.8421 | 45180.45 | 103938.5767 | 0 | 27899.3122 | 135755 | 468354.75 | 190057 | 12217.95 | 502293.5 | 8760 | 1720.1251 | 13480.3851 | 5229.8705 | 70.5075 | 0 | 0 | 0 | -1625.6989 | 0 | 3004.148 | 8760 | 5200.8001 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33245.791 | 12989.9994 | 0 | 11118.2805 | 8760 | 46358.6257 | 1357.55 | 0 | 2468.675 | 1946795.0992 | 110654.3789 | 481.675
129 | E | SOR | NAP | FC | ET | WC | OFF0 | 0.20777 | 14 | 0.7 | 8760 | 184522.1284 | 59725.35 | 112018.538 | 0 | 27899.3122 | 137517.5 | 474435.375 | 192524.5 | 12376.575 | 508814.75 | 8760 | 1720.1251 | 11424.8592 | 6968.5185 | 144.0887 | 0 | 0 | 0 | -1584.0387 | 0 | 2954.1899 | 8760 | 5200.7388 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33448.5469 | 12883.4199 | 0 | 9189.8587 | 8760 | 46735.8588 | 1375.175 | 0 | 2468.675 | 1946939.3555 | 110654.3789 | 347.025
130 | E | SOR | NAP | FC | ET | WC | OFF | 0.20777 | 10 | 0.5 | 8760 | 184596.8434 | 76223.7 | 121183.6769 | 0 | 27899.3122 | 139162.5 | 480110.625 | 194827.5 | 12524.625 | 514901.25 | 8760 | 1720.1251 | 8867.0786 | 8879.8446 | 270.8576 | 0 | 0 | 0 | -1534.9399 | 0 | 2862.2113 | 8760 | 5200.9529 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33692.9307 | 12780.2049 | 0 | 6792.2097 | 8760 | 47128.0935 | 1391.625 | 0 | 2468.675 | 1947168.5865 | 110654.3789 | 215.35
131 | E | SOR | NAP | FC | ET | WC | OFF | 0.20777 | 25.5 | 0.65 | 8760 | 174285.1388 | 28254.15 | 94535.7036 | 0 | 27899.3122 | 132417.5 | 456840.375 | 185384.5 | 11917.575 | 489944.75 | 8760 | 1720.1251 | 15463.6196 | 2903.1522 | 80.6563 | 0 | 0 | 0 | -1656.5816 | 0 | 3083.9605 | 8760 | 5200.7358 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 32931.8581 | 13242.5628 | 0 | 12929.6062 | 8760 | 45773.2059 | 1324.175 | 0 | 2468.675 | 1946492.0545 | 110654.3789 | 767.1
132 | E | SOR | NAP | FC | ET | WC | OFF | 0.20777 | 21.5 | 0.55 | 8760 | 176515.8111 | 38048.4 | 99976.5908 | 0 | 27899.3122 | 133667.5 | 461152.875 | 187134.5 | 12030.075 | 494569.75 | 8760 | 1720.1251 | 14329.7715 | 3947.154 | 121.6766 | 0 | 0 | 0 | -1635.5214 | 0 | 3068.412 | 8760 | 5200.7539 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33039.4852 | 13143.1043 | 0 | 11876.4114 | 8760 | 45982.7031 | 1336.675 | 0 | 2468.675 | 1946512.2068 | 110654.3789 | 659.9
133 | E | SOR | NAP | FC | ET | WC | OFF | 0.20777 | 18 | 0.45 | 8760 | 177483.8838 | 50652 | 106978.124 | 0 | 27899.3122 | 134872.5 | 465310.125 | 188821.5 | 12138.525 | 499028.25 | 8760 | 1720.1251 | 12927.887 | 5286.2983 | 183.0807 | 0 | 0 | 0 | -1612.3344 | 0 | 3048.1583 | 8760 | 5200.6932 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33142.9267 | 13041.7869 | 0 | 10569.6425 | 8760 | 46199.5147 | 1348.725 | 0 | 2468.675 | 1946645.734 | 110654.3789 | 553.5
134 | E | SOR | NAP | FC | ET | WC | OFF | 0.20777 | 14 | 0.35 | 8760 | 178628.4854 | 67549.95 | 116365.2482 | 0 | 27899.3122 | 136682.5 | 471554.625 | 191355.5 | 12301.425 | 505725.25 | 8760 | 1720.1251 | 10968.2466 | 6979.6816 | 302.3121 | 0 | 0 | 0 | -1585.5609 | 0 | 3015.7378 | 8760 | 5200.7115 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33359.9209 | 12927.6567 | 0 | 8715.2264 | 8760 | 46584.7707 | 1366.825 | 0 | 2468.675 | 1946792.4123 | 110654.3789 | 418.8
135 | E | SOR | NAP | FC | ET | WC | OFF | 0.20777 | 10 | 0.25 | 8760 | 176396.3244 | 89023.05 | 128293.9529 | 0 | 27899.3122 | 137912.5 | 475798.125 | 193077.5 | 12412.125 | 510276.25 | 8760 | 1720.1251 | 8351.1625 | 8988.7831 | 670.9823 | 0 | 0 | 0 | -1584.5237 | 0 | 3052.9751 | 8760 | 5200.7402 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33530.4579 | 12837.2464 | 0 | 6110.7671 | 8760 | 46861.8484 | 1379.125 | 0 | 2468.675 | 1947086.3579 | 110654.3789 | 294.525
136 | E | SOR | NAP | FC | ET | WC | R100 | 1.4877 | 25.5 | 1.9 | 8760 | 186024.0783 | 74383.65 | 120161.4951 | 65533.1035 | 81276.3026 | 106127.5 | 366139.875 | 148578.5 | 9551.475 | 49083.9688 | 8760 | 1720.1251 | 14737.639 | 3884.4012 | 2269.5581 | 0 | 0 | 0 | -1499.5238 | 0 | 2910.3261 | 8760 | 3840.5766 | 0 | 0 | 3843.066 | 4339.2219 | 2379.6621 | 15771.8539 | 9772.5564 | 1092.6056 | 12511.8259 | 8760 | 19954.2178 | 1061.275 | 0 | 2227.75 | 1396784.4829 | 178372.614 | 674.6
137 | E | SOR | NAP | FC | ET | WC | R100 | 1.4877 | 21.5 | 1.6 | 8760 | 184546.2066 | 91110.15 | 129453.3756 | 65533.1035 | 81276.3026 | 106842.5 | 368606.625 | 149579.5 | 9615.825 | 49414.6562 | 8760 | 1720.1251 | 13297.0507 | 4829.9048 | 2743.2629 | 0 | 0 | 0 | -1461.9803 | 0 | 2883.2907 | 8760 | 3839.2362 | 0 | 0 | 3843.066 | 4339.2219 | 2375.349 | 15772.0762 | 9724.6721 | 1092.4545 | 11156.5257 | 8760 | 19986.8352 | 1068.425 | 0 | 2227.75 | 1396735.2076 | 178372.614 | 567.775
138 | E | SOR | NAP | FC | ET | WC | R100 | 1.4877 | 18 | 1.35 | 8760 | 183531.3811 | 106477.2 | 137990.0564 | 65533.1035 | 81276.3026 | 107517.5 | 370935.375 | 150524.5 | 9676.575 | 49726.8438 | 8760 | 1720.1251 | 11847.1002 | 5780.8109 | 3251.5354 | 0 | 0 | 0 | -1424.842 | 0 | 2848.424 | 8760 | 3839.3462 | 0 | 0 | 3843.066 | 4339.2219 | 2371.793 | 15786.1963 | 9686.963 | 1092.2589 | 9794.1962 | 8760 | 20025.5949 | 1075.175 | 0 | 2227.75 | 1396697.7395 | 178372.614 | 467.25
139 | E | SOR | NAP | FC | ET | WC | R100 | 1.4877 | 14 | 1.05 | 8760 | 183320.6235 | 124468.65 | 147984.6401 | 65533.1035 | 81276.3026 | 108367.5 | 373867.875 | 151714.5 | 9753.075 | 50119.9688 | 8760 | 1720.1251 | 9958.4163 | 6706.2248 | 3847.3197 | 0 | 0 | 0 | -1381.2818 | 0 | 2786.5368 | 8760 | 3839.3768 | 0 | 0 | 3843.066 | 4339.2219 | 2369.8703 | 15801.4557 | 9638.0465 | 1092.1516 | 8038.7953 | 8760 | 20067.0644 | 1083.675 | 0 | 2227.75 | 1396916.1704 | 178372.614 | 341.425
140 | E | SOR | NAP | FC | ET | WC | R100 | 1.4877 | 10 | 0.75 | 8760 | 185151.4243 | 143168.85 | 158372.9475 | 65533.1035 | 81276.3026 | 108972.5 | 375955.125 | 152561.5 | 9807.525 | 50399.7812 | 8760 | 1720.1251 | 7830.2302 | 7715.4686 | 4563.409 | 0 | 0 | 0 | -1329.7437 | 0 | 2680.5699 | 8760 | 3838.4974 | 0 | 0 | 3843.066 | 4339.2219 | 2366.3713 | 15815.1983 | 9600.1845 | 1091.966 | 6090.8336 | 8760 | 20103.8018 | 1089.725 | 0 | 2227.75 | 1396827.2405 | 178372.614 | 196.825
141 | E | SOR | NAP | FC | ET | WC | R100 | 1.4877 | 25.5 | 1.3 | 8760 | 179460.8003 | 82395.9 | 124612.4483 | 65533.1035 | 81276.3026 | 105967.5 | 365587.875 | 148354.5 | 9537.075 | 49009.9688 | 8760 | 1720.1251 | 14066.1665 | 4319.9132 | 2616.1771 | 0 | 0 | 0 | -1510.3795 | 0 | 2958.1889 | 8760 | 3840.2522 | 0 | 0 | 3843.066 | 4339.2219 | 2381.5321 | 15812.078 | 9791.4619 | 1092.4338 | 11790.0023 | 8760 | 19980.3369 | 1059.675 | 0 | 2227.75 | 1396666.5643 | 178372.614 | 734.35
142 | E | SOR | NAP | FC | ET | WC | R100 | 1.4877 | 21.5 | 1.1 | 8760 | 179557.4314 | 95783.85 | 132049.7025 | 65533.1035 | 81276.3026 | 106715 | 368166.75 | 149401 | 9604.35 | 49355.6875 | 8760 | 1720.1251 | 12829.2294 | 5135.2034 | 3045.6544 | 0 | 0 | 0 | -1476.1338 | 0 | 2929.801 | 8760 | 3839.607 | 0 | 0 | 3843.066 | 4339.2219 | 2378.0951 | 15798.14 | 9738.7196 | 1092.3806 | 10641.2249 | 8760 | 20002.2282 | 1067.15 | 0 | 2227.75 | 1396632.0534 | 178372.614 | 617.05
143 | E | SOR | NAP | FC | ET | WC | R100 | 1.4877 | 18 | 0.9 | 8760 | 178935.8953 | 110952.45 | 140476.1407 | 65533.1035 | 81276.3026 | 107315 | 370236.75 | 150241 | 9658.35 | 49633.1875 | 8760 | 1720.1251 | 11470.6097 | 5981.9431 | 3467.0808 | 0 | 0 | 0 | -1445.7651 | 0 | 2902.6485 | 8760 | 3839.4557 | 0 | 0 | 3843.066 | 4339.2219 | 2375.4846 | 15807.8752 | 9702.0254 | 1092.2566 | 9365.2624 | 8760 | 20031.0053 | 1073.15 | 0 | 2227.75 | 1396754.6514 | 178372.614 | 516.5
144 | E | SOR | NAP | FC | ET | WC | R100 | 1.4877 | 14 | 0.7 | 8760 | 179792.34 | 127230.75 | 149519.0378 | 65533.1035 | 81276.3026 | 108170 | 373186.5 | 151438 | 9735.3 | 50028.625 | 8760 | 1720.1251 | 9714.8658 | 6920.343 | 4043.5934 | 0 | 0 | 0 | -1410.3213 | 0 | 2849.7698 | 8760 | 3838.5062 | 0 | 0 | 3843.066 | 4339.2219 | 2372.933 | 15806.8325 | 9646.8825 | 1092.0822 | 7734.6983 | 8760 | 20062.1727 | 1081.7 | 0 | 2227.75 | 1396887.331 | 178372.614 | 387.575
145 | E | SOR | NAP | FC | ET | WC | R10 | 1.4877 | 10 | 0.5 | 8760 | 182144.6557 | 147383.55 | 160714.2914 | 65533.1035 | 81276.3026 | 108777.5 | 375282.375 | 152288.5 | 9789.975 | 50309.5938 | 8760 | 1720.1251 | 7668.6479 | 8049.0304 | 4704.7353 | 0 | 0 | 0 | -1396.8303 | 0 | 2718.2584 | 8760 | 3837.1273 | 0 | 0 | 3843.066 | 4339.2219 | 2369.4754 | 15810.5072 | 9605.6881 | 1091.8092 | 5889.115 | 8760 | 20088.7682 | 1087.775 | 0 | 2227.75 | 1396880.2233 | 178372.614 | 240.675
146 | E | SOR | NAP | FC | ET | WC | R10 | 1.4877 | 25.5 | 0.65 | 8760 | 167826.9709 | 95910.75 | 132120.1978 | 65533.1035 | 81276.3026 | 105607.5 | 364345.875 | 147850.5 | 9504.675 | 48843.4688 | 8760 | 1720.1251 | 12944.394 | 4887.3623 | 3199.1014 | 0 | 0 | 0 | -1513.1698 | 0 | 3043.768 | 8760 | 3839.8482 | 0 | 0 | 3843.066 | 4339.2219 | 2380.4604 | 15857.5792 | 9825.3118 | 1092.2226 | 10603.3137 | 8760 | 20010.2699 | 1056.075 | 0 | 2227.75 | 1396632.7153 | 178372.614 | 846.575
147 | E | SOR | NAP | FC | ET | WC | R10 | 1.4877 | 21.5 | 0.55 | 8760 | 168483.494 | 109171.8 | 139486.9566 | 65533.1035 | 81276.3026 | 106315 | 366786.75 | 148841 | 9568.35 | 49170.6875 | 8760 | 1720.1251 | 11839.6738 | 5583.2697 | 3621.873 | 0 | 0 | 0 | -1495.3687 | 0 | 3036.0351 | 8760 | 3839.9925 | 0 | 0 | 3843.066 | 4339.2219 | 2378.7602 | 15843.5728 | 9771.2 | 1091.9145 | 9567.5829 | 8760 | 20018.0068 | 1063.15 | 0 | 2227.75 | 1396816.8996 | 178372.614 | 737.2
148 | E | SOR | NAP | FC | ET | WC | R10 | 1.4877 | 18 | 0.45 | 8760 | 168643.4714 | 123948.9 | 147695.9093 | 65533.1035 | 81276.3026 | 106967.5 | 369037.875 | 149754.5 | 9627.075 | 49472.4688 | 8760 | 1720.1251 | 10639.046 | 6457.9163 | 4048.2025 | 0 | 0 | 0 | -1494.7991 | 0 | 3003.1919 | 8760 | 3838.9993 | 0 | 0 | 3843.066 | 4339.2219 | 2377.3478 | 15825.8721 | 9723.581 | 1091.8065 | 8457.7304 | 8760 | 20028.5079 | 1069.675 | 0 | 2227.75 | 1396650.5929 | 178372.614 | 639.675
149 | E | SOR | NAP | FC | ET | WC | R10 | 1.4877 | 14 | 0.35 | 8760 | 169326.7373 | 142065.9 | 157760.2383 | 65533.1035 | 81276.3026 | 107705 | 371582.25 | 150787 | 9693.45 | 49813.5625 | 8760 | 1720.1251 | 8945.3898 | 7418.6483 | 4730.333 | 0 | 0 | 0 | -1499.5002 | 0 | 2999.19 | 8760 | 3838.6622 | 0 | 0 | 3843.066 | 4339.2219 | 2373.9905 | 15823.3567 | 9676.8519 | 1091.5319 | 6829.4114 | 8760 | 20061.2023 | 1077.05 | 0 | 2227.75 | 1396881.6888 | 178372.614 | 507.2
150 | E | SOR | NAP | FC | ET | WC | R10 | 1.4877 | 10 | 0.25 | 8760 | 165366.4094 | 170565.75 | 173592.4328 | 65533.1035 | 81276.3026 | 108207.5 | 373315.875 | 151490.5 | 9738.675 | 50045.9688 | 8760 | 1720.1251 | 6653.5231 | 8654.9772 | 5821.8276 | 0 | 0 | 0 | -1560.0369 | 0 | 3150.2963 | 8760 | 3839.1547 | 0 | 0 | 3843.066 | 4339.2219 | 2369.5456 | 15820.81 | 9645.5216 | 1090.1749 | 4448.3632 | 8760 | 20071.8572 | 1082.075 | 0 | 2227.75 | 1396877.9406 | 178372.614 | 391.4
151 | E | SOR | NAP | FC | ET | WC | R600 | 1.7084 | 25.5 | 1.9 | 8760 | 187357.0319 | 56663.55 | 110317.6514 | 65533.1035 | 49607.4578 | 115415 | 398181.75 | 161581 | 10387.35 | 53379.4375 | 8760 | 1720.1251 | 14527.2505 | 4285.3103 | 986.6804 | 0 | 0 | 0 | -1590.6631 | 0 | 2899.1144 | 8760 | 4171.047 | 0 | 0 | 4174.5441 | 2161.2871 | 2725.9352 | 17350.4041 | 10597.8327 | 1273.4883 | 12210.1542 | 8760 | 21828.612 | 1154.15 | 0 | 2346.175 | 1510469.2806 | 155104.6654 | 663.225
152 | E | SOR | NAP | FC | ET | WC | R600 | 1.7084 | 21.5 | 1.6 | 8760 | 186661.1986 | 69932.7 | 117688.9099 | 65533.1035 | 49607.4578 | 116362.5 | 401450.625 | 162907.5 | 10472.625 | 53817.6562 | 8760 | 1720.1251 | 13169.5776 | 5241.0776 | 1253.464 | 0 | 0 | 0 | -1551.3483 | 0 | 2865.7079 | 8760 | 4171.7803 | 0 | 0 | 4174.5441 | 2161.2871 | 2718.1496 | 17362.4974 | 10547.0838 | 1273.3075 | 10943.6335 | 8760 | 21881.0445 | 1163.625 | 0 | 2346.175 | 1510447.0997 | 155104.6654 | 548.75
153 | E | SOR | NAP | FC | ET | WC | R600 | 1.7084 | 18 | 1.35 | 8760 | 186468.2613 | 83133 | 125021.921 | 65533.1035 | 49607.4578 | 117080 | 403926 | 163912 | 10537.2 | 54149.5 | 8760 | 1720.1251 | 11793.5571 | 6282.6753 | 1543.1496 | 0 | 0 | 0 | -1511.0835 | 0 | 2819.2175 | 8760 | 4170.5296 | 0 | 0 | 4174.5441 | 2161.2871 | 2712.4787 | 17380.1296 | 10501.4648 | 1272.9 | 9667.6727 | 8760 | 21921.3906 | 1170.8 | 0 | 2346.175 | 1510579.4478 | 155104.6654 | 440.55
154 | E | SOR | NAP | FC | ET | WC | R600 | 1.7084 | 14 | 1.05 | 8760 | 186689.5387 | 99462.6 | 134093.3162 | 65533.1035 | 49607.4578 | 117955 | 406944.75 | 165137 | 10615.95 | 54554.1875 | 8760 | 1720.1251 | 9958.3932 | 7388.9863 | 1970.8199 | 0 | 0 | 0 | -1450.4638 | 0 | 2737.5266 | 8760 | 4170.2856 | 0 | 0 | 4174.5441 | 2161.2871 | 2703.6701 | 17409.7994 | 10453.3899 | 1272.5706 | 7986.5007 | 8760 | 21984.3633 | 1179.55 | 0 | 2346.175 | 1510723.5536 | 155104.6654 | 306.725
155 | E | SOR | NAP | FC | ET | WC | R600 | 1.7084 | 10 | 0.75 | 8760 | 188273.8684 | 118079.1 | 144435.1267 | 65533.1035 | 49607.4578 | 118657.5 | 409368.375 | 166120.5 | 10679.175 | 54879.0938 | 8760 | 1720.1251 | 7831.5254 | 8548.2708 | 2519.262 | 0 | 0 | 0 | -1383.3386 | 0 | 2613.9603 | 8760 | 4170.9011 | 0 | 0 | 4174.5441 | 2161.2871 | 2694.7835 | 17435.8697 | 10417.8589 | 1270.8191 | 6059.5923 | 8760 | 22033.5074 | 1186.575 | 0 | 2346.175 | 1510624.802 | 155104.6654 | 163.55
156 | E | SOR | NAP | FC | ET | WC | R600 | 1.7084 | 25.5 | 1.3 | 8760 | 180577.3393 | 63730.8 | 114243.6396 | 65533.1035 | 49607.4578 | 115312.5 | 397828.125 | 161437.5 | 10378.125 | 53332.0312 | 8760 | 1720.1251 | 13885.1272 | 4716.5297 | 1203.7464 | 0 | 0 | 0 | -1583.5345 | 0 | 2927.0219 | 8760 | 4171.3092 | 0 | 0 | 4174.5441 | 2161.2871 | 2722.9756 | 17406.9576 | 10617.2702 | 1273.2637 | 11538.4684 | 8760 | 21867.5255 | 1153.125 | 0 | 2346.175 | 1510470.1489 | 155104.6654 | 727.55
157 | E | SOR | NAP | FC | ET | WC | R600 | 1.7084 | 21.5 | 1.1 | 8760 | 180973.9045 | 75757.95 | 120924.9442 | 65533.1035 | 49607.4578 | 116192.5 | 400864.125 | 162669.5 | 10457.325 | 53739.0312 | 8760 | 1720.1251 | 12685.5132 | 5571.111 | 1490.8244 | 0 | 0 | 0 | -1553.2804 | 0 | 2902.409 | 8760 | 4170.6052 | 0 | 0 | 4174.5441 | 2161.2871 | 2718.9557 | 17398.8528 | 10557.5603 | 1273.2498 | 10423.2565 | 8760 | 21900.5775 | 1161.925 | 0 | 2346.175 | 1510412.2752 | 155104.6654 | 604.7
158 | E | SOR | NAP | FC | ET | WC | R600 | 1.7084 | 18 | 0.9 | 8760 | 181301.4385 | 88919.1 | 128236.2067 | 65533.1035 | 49607.4578 | 116940 | 403443 | 163716 | 10524.6 | 54084.75 | 8760 | 1720.1251 | 11399.8215 | 6536.8682 | 1791.1821 | 0 | 0 | 0 | -1523.1648 | 0 | 2870.9581 | 8760 | 4171.1365 | 0 | 0 | 4174.5441 | 2161.2871 | 2716.3241 | 17411.6497 | 10515.4328 | 1272.9882 | 9227.2036 | 8760 | 21941.0369 | 1169.4 | 0 | 2346.175 | 1510626.543 | 155104.6654 | 495.425
159 | E | SOR | NAP | FC | ET | WC | R600 | 1.7084 | 14 | 0.7 | 8760 | 182666.8315 | 103774.5 | 136488.6565 | 65533.1035 | 49607.4578 | 117805 | 406427.25 | 164927 | 10602.45 | 54484.8125 | 8760 | 1720.1251 | 9695.3676 | 7556.1732 | 2186.7141 | 0 | 0 | 0 | -1473.8119 | 0 | 2797.7796 | 8760 | 4170.8129 | 0 | 0 | 4174.5441 | 2161.2871 | 2708.8915 | 17420.9181 | 10464.319 | 1272.2791 | 7668.3589 | 8760 | 21986.2614 | 1178.05 | 0 | 2346.175 | 1510570.6379 | 155104.6654 | 356.975
160 | E | SOR | NAP | FC | ET | WC | R60 | 1.7084 | 10 | 0.5 | 8760 | 185203.5201 | 123504.75 | 147449.1758 | 65533.1035 | 49607.4578 | 118470 | 408721.5 | 165858 | 10662.3 | 54792.375 | 8760 | 1720.1251 | 7666.9683 | 8916.6105 | 2634.8183 | 0 | 0 | 0 | -1436.3326 | 0 | 2658.3611 | 8760 | 4170.8823 | 0 | 0 | 4174.5441 | 2161.2871 | 2701.0661 | 17439.4152 | 10428.6225 | 1270.2133 | 5848.5414 | 8760 | 22028.9201 | 1184.7 | 0 | 2346.175 | 1510645.0331 | 155104.6654 | 206.825
161 | E | SOR | NAP | FC | ET | WC | R60 | 1.7084 | 25.5 | 0.65 | 8760 | 168559.7884 | 77103.9 | 121672.6443 | 65533.1035 | 49607.4578 | 114972.5 | 396655.125 | 160961.5 | 10347.525 | 53174.7812 | 8760 | 1720.1251 | 12779.4624 | 5428.2476 | 1659.8869 | 0 | 0 | 0 | -1582.3285 | 0 | 2998.7357 | 8760 | 4171.7635 | 0 | 0 | 4174.5441 | 2161.2871 | 2722.7182 | 17464.5844 | 10652.5272 | 1272.786 | 10383.2523 | 8760 | 21907.6794 | 1149.725 | 0 | 2346.175 | 1510390.201 | 155104.6654 | 846.525
162 | E | SOR | NAP | FC | ET | WC | R60 | 1.7084 | 21.5 | 0.55 | 8760 | 169835.1182 | 88284.6 | 127883.7302 | 65533.1035 | 49607.4578 | 115662.5 | 399035.625 | 161927.5 | 10409.625 | 53493.9062 | 8760 | 1720.1251 | 11740.0948 | 6138.497 | 1926.5491 | 0 | 0 | 0 | -1560.0971 | 0 | 2981.7713 | 8760 | 4171.0639 | 0 | 0 | 4174.5441 | 2161.2871 | 2719.0471 | 17433.0301 | 10599.6738 | 1272.6452 | 9424.2931 | 8760 | 21907.7253 | 1156.625 | 0 | 2346.175 | 1510369.8935 | 155104.6654 | 726.325
163 | E | SOR | NAP | FC | ET | WC | R60 | 1.7084 | 18 | 0.45 | 8760 | 170611.9479 | 100533.15 | 134688.0266 | 65533.1035 | 49607.4578 | 116472.5 | 401830.125 | 163061.5 | 10482.525 | 53868.5312 | 8760 | 1720.1251 | 10582.7125 | 7075.6776 | 2213.6804 | 0 | 0 | 0 | -1546.4065 | 0 | 2949.4567 | 8760 | 4172.1317 | 0 | 0 | 4174.5441 | 2161.2871 | 2714.3803 | 17448.103 | 10551.5075 | 1271.617 | 8359.0703 | 8760 | 21948.5003 | 1164.725 | 0 | 2346.175 | 1510679.4604 | 155104.6654 | 619.675
164 | E | SOR | NAP | FC | ET | WC | R60 | 1.7084 | 14 | 0.35 | 8760 | 172269.5905 | 117150.3 | 143919.1611 | 65533.1035 | 49607.4578 | 117265 | 404564.25 | 164171 | 10553.85 | 54235.0625 | 8760 | 1720.1251 | 8972.3289 | 8132.5124 | 2667.078 | 0 | 0 | 0 | -1535.3549 | 0 | 2934.4061 | 8760 | 4171.3347 | 0 | 0 | 4174.5441 | 2161.2871 | 2707.7318 | 17439.0865 | 10498.972 | 1269.9808 | 6824.62 | 8760 | 21974.6148 | 1172.65 | 0 | 2346.175 | 1510660.995 | 155104.6654 | 478.85
165 | E | SOR | NAP | FC | ET | WC | R60 | 1.7084 | 10 | 0.25 | 8760 | 169036.525 | 144423 | 159069.651 | 65533.1035 | 49607.4578 | 117712.5 | 406108.125 | 164797.5 | 10594.125 | 54442.0312 | 8760 | 1720.1251 | 6706.431 | 9493.9552 | 3538.8256 | 0 | 0 | 0 | -1573.221 | 0 | 3063.6451 | 8760 | 4170.5588 | 0 | 0 | 4174.5441 | 2161.2871 | 2696.4242 | 17431.6966 | 10466.8888 | 1266.2869 | 4492.2995 | 8760 | 21992.0552 | 1177.125 | 0 | 2346.175 | 1510465.133 | 155104.6654 | 355.4
166 | E | SOR | NAP | FC | FP | WC | OFF0 | 0.20777 | 25.5 | 1.9 | 8760 | 181900.0061 | 38537.1 | 100248.0727 | 0 | 27899.3122 | 136542.5 | 471071.625 | 191159.5 | 12288.825 | 505207.25 | 8760 | 1720.1251 | 13345.3002 | 4595.1693 | 21.2707 | 0 | 0 | 0 | -1625.4464 | 0 | 2317.0672 | 8760 | 5200.7679 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33324.6414 | 12935.7381 | 0 | 11519.2074 | 8760 | 46489.8882 | 1365.425 | 0 | 2468.675 | 1946965.7248 | 110654.3789 | 233.875
167 | E | SOR | NAP | FC | FP | WC | OFF0 | 0.20777 | 21.5 | 1.6 | 8760 | 178219.6318 | 50625 | 106963.125 | 0 | 27899.3122 | 137797.5 | 475401.375 | 192916.5 | 12401.775 | 509850.75 | 8760 | 1720.1251 | 11941.9557 | 6304.8166 | 55.4098 | 0 | 0 | 0 | -1590.5208 | 0 | 2315.6308 | 8760 | 5200.739 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33498.9959 | 12870.1682 | 0 | 10170.4257 | 8760 | 46784.7229 | 1377.975 | 0 | 2468.675 | 1946921.8797 | 110654.3789 | 182.825
168 | E | SOR | NAP | FC | FP | WC | OFF0 | 0.20777 | 18 | 1.35 | 8760 | 175488.0814 | 59221.8 | 111738.8066 | 0 | 27899.3122 | 138917.5 | 479265.375 | 194484.5 | 12502.575 | 513994.75 | 8760 | 1720.1251 | 10545.4908 | 7389.1059 | 103.0848 | 0 | 0 | 0 | -1555.7927 | 0 | 2309.2824 | 8760 | 5200.7148 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33655.1153 | 12806.512 | 0 | 8834.1234 | 8760 | 47050.3747 | 1389.175 | 0 | 2468.675 | 1947053.0059 | 110654.3789 | 135.875
169 | E | SOR | NAP | FC | FP | WC | OFF0 | 0.20777 | 14 | 1.05 | 8760 | 171916.0869 | 71116.65 | 118346.6161 | 0 | 27899.3122 | 139857.5 | 482508.375 | 195800.5 | 12587.175 | 517472.75 | 8760 | 1720.1251 | 8719.0615 | 8709.0976 | 172.8729 | 0 | 0 | 0 | -1504.3988 | 0 | 2292.5463 | 8760 | 5200.7205 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33790.6795 | 12747.2576 | 0 | 7092.5744 | 8760 | 47261.9179 | 1398.575 | 0 | 2468.675 | 1947316.707 | 110654.3789 | 90.8
170 | E | SOR | NAP | FC | FP | WC | OFF0 | 0.20777 | 10 | 0.75 | 8760 | 168088.6178 | 84199.5 | 125614.3815 | 0 | 27899.3122 | 140540 | 484863 | 196756 | 12648.6 | 519998 | 8760 | 1720.1251 | 6673.3857 | 10258.4297 | 302.9418 | 0 | 0 | 0 | -1439.4054 | 0 | 2256.1413 | 8760 | 5200.6482 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33885.0704 | 12696.5751 | 0 | 5149.0454 | 8760 | 47423.8576 | 1405.4 | 0 | 2468.675 | 1947263.6065 | 110654.3789 | 48.175
171 | E | SOR | NAP | FC | FP | WC | OFF0 | 0.20777 | 25.5 | 1.3 | 8760 | 179800.733 | 40756.5 | 101480.9905 | 0 | 27899.3122 | 136260 | 470097 | 190764 | 12263.4 | 504162 | 8760 | 1720.1251 | 12969.5627 | 4824.6663 | 59.008 | 0 | 0 | 0 | -1608.1725 | 0 | 2343.1327 | 8760 | 5200.6734 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33346.2348 | 12971.3463 | 0 | 11125.2615 | 8760 | 46481.5334 | 1362.6 | 0 | 2468.675 | 1946836.3694 | 110654.3789 | 260.7
172 | E | SOR | NAP | FC | FP | WC | OFF0 | 0.20777 | 21.5 | 1.1 | 8760 | 176155.0751 | 52138.35 | 107803.819 | 0 | 27899.3122 | 137435 | 474150.75 | 192409 | 12369.15 | 508509.5 | 8760 | 1720.1251 | 11631.5845 | 6245.2468 | 103.4912 | 0 | 0 | 0 | -1576.5618 | 0 | 2344.6601 | 8760 | 5200.7213 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33482.1768 | 12892.194 | 0 | 9844.4493 | 8760 | 46723.0133 | 1374.35 | 0 | 2468.675 | 1946979.5691 | 110654.3789 | 208.325
173 | E | SOR | NAP | FC | FP | WC | OFF0 | 0.20777 | 18 | 0.9 | 8760 | 173445.4961 | 63537.75 | 114136.3968 | 0 | 27899.3122 | 138350 | 477307.5 | 193690 | 12451.5 | 511895 | 8760 | 1720.1251 | 10269.3371 | 7660.713 | 154.1345 | 0 | 0 | 0 | -1544.8789 | 0 | 2346.9277 | 8760 | 5201.2422 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33604.8768 | 12843.037 | 0 | 8536.2473 | 8760 | 46938.6826 | 1383.5 | 0 | 2468.675 | 1947157.5339 | 110654.3789 | 160.375
174 | E | SOR | NAP | FC | FP | WC | OFF0 | 0.20777 | 14 | 0.7 | 8760 | 170046.6842 | 74152.8 | 120033.2536 | 0 | 27899.3122 | 139377.5 | 480852.375 | 195128.5 | 12543.975 | 515696.75 | 8760 | 1720.1251 | 8532.4475 | 8991.5922 | 243.9533 | 0 | 0 | 0 | -1501.4799 | 0 | 2324.1115 | 8760 | 5200.7464 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33733.7874 | 12774.104 | 0 | 6888.0753 | 8760 | 47174.629 | 1393.775 | 0 | 2468.675 | 1947076.4114 | 110654.3789 | 107.525
175 | E | SOR | NAP | FC | FP | WC | OFF | 0.20777 | 10 | 0.5 | 8760 | 166867.6023 | 87430.05 | 127409.0119 | 0 | 27899.3122 | 140197.5 | 483681.375 | 196276.5 | 12617.775 | 518730.75 | 8760 | 1720.1251 | 6540.0653 | 10398.9007 | 376.1538 | 0 | 0 | 0 | -1463.0481 | 0 | 2287.3656 | 8760 | 5200.6593 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33845.3821 | 12714.5251 | 0 | 4993.9431 | 8760 | 47359.2937 | 1401.975 | 0 | 2468.675 | 1947329.451 | 110654.3789 | 62.8
176 | E | SOR | NAP | FC | FP | WC | OFF | 0.20777 | 25.5 | 0.65 | 8760 | 173172.7466 | 49411.35 | 106288.92 | 0 | 27899.3122 | 135690 | 468130.5 | 189966 | 12212.1 | 502053 | 8760 | 1720.1251 | 12056.8585 | 5444.6956 | 167.8566 | 0 | 0 | 0 | -1574.5432 | 0 | 2400.2604 | 8760 | 5200.7588 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33304.0146 | 13028.5788 | 0 | 10201.2564 | 8760 | 46401.5771 | 1356.9 | 0 | 2468.675 | 1946575.8465 | 110654.3789 | 326.65
177 | E | SOR | NAP | FC | FP | WC | OFF | 0.20777 | 21.5 | 0.55 | 8760 | 170256.9937 | 58955.85 | 111591.0665 | 0 | 27899.3122 | 136602.5 | 471278.625 | 191243.5 | 12294.225 | 505429.25 | 8760 | 1720.1251 | 10881.031 | 6549.4618 | 231.6008 | 0 | 0 | 0 | -1551.5973 | 0 | 2398.6035 | 8760 | 5200.7538 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33396.0979 | 12945.5662 | 0 | 9094.942 | 8760 | 46583.1226 | 1366.025 | 0 | 2468.675 | 1946778.237 | 110654.3789 | 271.875
178 | E | SOR | NAP | FC | FP | WC | OFF | 0.20777 | 18 | 0.45 | 8760 | 168373.3803 | 70723.8 | 118128.3806 | 0 | 27899.3122 | 137550 | 474547.5 | 192570 | 12379.5 | 508935 | 8760 | 1720.1251 | 9658.5652 | 7895.7755 | 298.2536 | 0 | 0 | 0 | -1537.2409 | 0 | 2400.9601 | 8760 | 5201.0182 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33496.8472 | 12887.451 | 0 | 7930.0412 | 8760 | 46777.3456 | 1375.5 | 0 | 2468.675 | 1946656.75 | 110654.3789 | 220.225
179 | E | SOR | NAP | FC | FP | WC | OFF | 0.20777 | 14 | 0.35 | 8760 | 164954.6307 | 83174.85 | 125045.1695 | 0 | 27899.3122 | 138612.5 | 478213.125 | 194057.5 | 12475.125 | 512866.25 | 8760 | 1720.1251 | 8023.0236 | 9065.2133 | 439.8388 | 0 | 0 | 0 | -1520.2519 | 0 | 2394.1213 | 8760 | 5201.1684 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33638.3893 | 12813.6964 | 0 | 6349.2597 | 8760 | 47006.0464 | 1386.125 | 0 | 2468.675 | 1947151.162 | 110654.3789 | 157.525
180 | E | SOR | NAP | FC | FP | WC | OFF | 0.20777 | 10 | 0.25 | 8760 | 149506.6101 | 103860.9 | 136536.6533 | 0 | 27899.3122 | 139305 | 480602.25 | 195027 | 12537.45 | 515428.5 | 8760 | 1720.1251 | 5745.214 | 10619.0007 | 833.5739 | 0 | 0 | 0 | -1529.9277 | 0 | 2360.9494 | 8760 | 5201.3665 | 0 | 0 | 5200.5155 | 580.9311 | 0 | 33723.3429 | 12759.3551 | 0 | 4127.0636 | 8760 | 47177.654 | 1393.05 | 0 | 2468.675 | 1947005.6891 | 110654.3789 | 111.15
181 | E | SOR | NAP | FC | FP | WC | R100 | 1.4877 | 25.5 | 1.9 | 8760 | 183867.0047 | 86389.2 | 126830.8004 | 65533.1035 | 81276.3026 | 106730 | 368218.5 | 149422 | 9605.7 | 49362.625 | 8760 | 1720.1251 | 13242.6441 | 4665.1937 | 2562.4872 | 0 | 0 | 0 | -1458.7405 | 0 | 2470.6651 | 8760 | 3840.2135 | 0 | 0 | 3843.066 | 4339.2219 | 2376.6574 | 15790.089 | 9741.7654 | 1092.3362 | 11430.6262 | 8760 | 19995.2504 | 1067.3 | 0 | 2227.75 | 1396650.2295 | 178372.614 | 371.425
182 | E | SOR | NAP | FC | FP | WC | R100 | 1.4877 | 21.5 | 1.6 | 8760 | 180601.1596 | 101004.3 | 134949.7591 | 65533.1035 | 81276.3026 | 107425 | 370616.25 | 150395 | 9668.25 | 49684.0625 | 8760 | 1720.1251 | 11903.3538 | 5516.1295 | 2989.4231 | 0 | 0 | 0 | -1424.442 | 0 | 2461.7655 | 8760 | 3840.1022 | 0 | 0 | 3843.066 | 4339.2219 | 2372.7326 | 15798.2433 | 9699.6379 | 1092.1836 | 10157.3946 | 8760 | 20031.6084 | 1074.25 | 0 | 2227.75 | 1396782.7113 | 178372.614 | 306.5
183 | E | SOR | NAP | FC | FP | WC | R100 | 1.4877 | 18 | 1.35 | 8760 | 177804.6589 | 114725.7 | 142572.2509 | 65533.1035 | 81276.3026 | 107942.5 | 372401.625 | 151119.5 | 9714.825 | 49923.4062 | 8760 | 1720.1251 | 10589.0349 | 6368.4675 | 3450.8343 | 0 | 0 | 0 | -1389.851 | 0 | 2448.7068 | 8760 | 3839.3355 | 0 | 0 | 3843.066 | 4339.2219 | 2371.0123 | 15800.1149 | 9666.4294 | 1092.0501 | 8908.3657 | 8760 | 20053.8791 | 1079.425 | 0 | 2227.75 | 1396794.6735 | 178372.614 | 247.625
184 | E | SOR | NAP | FC | FP | WC | R100 | 1.4877 | 14 | 1.05 | 8760 | 175953.9895 | 130397.85 | 151278.4205 | 65533.1035 | 81276.3026 | 108527.5 | 374419.875 | 151938.5 | 9767.475 | 50193.9688 | 8760 | 1720.1251 | 8944.0433 | 7207.202 | 3990.5732 | 0 | 0 | 0 | -1347.2553 | 0 | 2414.2688 | 8760 | 3838.1248 | 0 | 0 | 3843.066 | 4339.2219 | 2368.8065 | 15807.7589 | 9625.9402 | 1091.9634 | 7366.6014 | 8760 | 20079.6145 | 1085.275 | 0 | 2227.75 | 1396980.2891 | 178372.614 | 169.525
185 | E | SOR | NAP | FC | FP | WC | R100 | 1.4877 | 10 | 0.75 | 8760 | 175394.4012 | 147186.45 | 160604.7987 | 65533.1035 | 81276.3026 | 109100 | 376395 | 152740 | 9819 | 50458.75 | 8760 | 1720.1251 | 7069.3944 | 8039.5083 | 4665.2914 | 0 | 0 | 0 | -1292.2646 | 0 | 2352.3411 | 8760 | 3838.9433 | 0 | 0 | 3843.066 | 4339.2219 | 2365.0171 | 15817.3419 | 9595.9888 | 1091.8861 | 5628.5207 | 8760 | 20116.1695 | 1091 | 0 | 2227.75 | 1396872.9551 | 178372.614 | 92.725
186 | E | SOR | NAP | FC | FP | WC | R100 | 1.4877 | 25.5 | 1.3 | 8760 | 178448.4869 | 93290.4 | 130664.5448 | 65533.1035 | 81276.3026 | 106697.5 | 368106.375 | 149376.5 | 9602.775 | 49347.5938 | 8760 | 1720.1251 | 12546.6638 | 5020.5871 | 2913.4346 | 0 | 0 | 0 | -1464.5093 | 0 | 2509.958 | 8760 | 3839.6374 | 0 | 0 | 3843.066 | 4339.2219 | 2378.0226 | 15823.9286 | 9749.6642 | 1092.1774 | 10695.8255 | 8760 | 20020.8718 | 1066.975 | 0 | 2227.75 | 1396619.5579 | 178372.614 | 416.75
187 | E | SOR | NAP | FC | FP | WC | R100 | 1.4877 | 21.5 | 1.1 | 8760 | 176274.2185 | 106909.2 | 138230.0404 | 65533.1035 | 81276.3026 | 107242.5 | 369986.625 | 150139.5 | 9651.825 | 49599.6562 | 8760 | 1720.1251 | 11390.1432 | 5853.5861 | 3307.2588 | 0 | 0 | 0 | -1434.0428 | 0 | 2501.8236 | 8760 | 3839.2508 | 0 | 0 | 3843.066 | 4339.2219 | 2375.22 | 15818.042 | 9712.255 | 1092.2002 | 9605.0303 | 8760 | 20037.0885 | 1072.425 | 0 | 2227.75 | 1396821.4904 | 178372.614 | 339.75
188 | E | SOR | NAP | FC | FP | WC | R100 | 1.4877 | 18 | 0.9 | 8760 | 173821.0238 | 119979.9 | 145491.0563 | 65533.1035 | 81276.3026 | 107780 | 371841 | 150892 | 9700.2 | 49848.25 | 8760 | 1720.1251 | 10166.8017 | 6593.9222 | 3723.0498 | 0 | 0 | 0 | -1404.6184 | 0 | 2494.7412 | 8760 | 3840.2111 | 0 | 0 | 3843.066 | 4339.2219 | 2373.8644 | 15830.027 | 9680.4934 | 1092.1197 | 8443.744 | 8760 | 20063.7889 | 1077.8 | 0 | 2227.75 | 1396844.6045 | 178372.614 | 276.775
189 | E | SOR | NAP | FC | FP | WC | R100 | 1.4877 | 14 | 0.7 | 8760 | 172307.7157 | 134979.75 | 153823.7508 | 65533.1035 | 81276.3026 | 108452.5 | 374161.125 | 151833.5 | 9760.725 | 50159.2812 | 8760 | 1720.1251 | 8601.571 | 7364.0676 | 4257.5078 | 0 | 0 | 0 | -1368.638 | 0 | 2466.6676 | 8760 | 3839.331 | 0 | 0 | 3843.066 | 4339.2219 | 2370.757 | 15818.3752 | 9637.5692 | 1091.9086 | 6976.8997 | 8760 | 20083.3457 | 1084.525 | 0 | 2227.75 | 1396826.587 | 178372.614 | 200.5
190 | E | SOR | NAP | FC | FP | WC | R10 | 1.4877 | 10 | 0.5 | 8760 | 172611.3858 | 151854.75 | 163198.1258 | 65533.1035 | 81276.3026 | 108952.5 | 375886.125 | 152533.5 | 9805.725 | 50390.5312 | 8760 | 1720.1251 | 6857.878 | 8446.3315 | 4833.4626 | 0 | 0 | 0 | -1358.3107 | 0 | 2385.3115 | 8760 | 3838.9691 | 0 | 0 | 3843.066 | 4339.2219 | 2367.5643 | 15817.7155 | 9604.0723 | 1091.6016 | 5382.7075 | 8760 | 20102.5436 | 1089.525 | 0 | 2227.75 | 1396808.8449 | 178372.614 | 127.8
191 | E | SOR | NAP | FC | FP | WC | R10 | 1.4877 | 25.5 | 0.65 | 8760 | 166490.1949 | 110594.7 | 140277.4039 | 65533.1035 | 81276.3026 | 106492.5 | 367399.125 | 149089.5 | 9584.325 | 49252.7812 | 8760 | 1720.1251 | 11212.9344 | 5699.3933 | 3623.563 | 0 | 0 | 0 | -1460.4096 | 0 | 2590.5013 | 8760 | 3839.652 | 0 | 0 | 3843.066 | 4339.2219 | 2378.3223 | 15864.325 | 9776.376 | 1092.127 | 9307.952 | 8760 | 20050.1125 | 1064.925 | 0 | 2227.75 | 1396538.1336 | 178372.614 | 505.575
192 | E | SOR | NAP | FC | FP | WC | R10 | 1.4877 | 21.5 | 0.55 | 8760 | 164664.8882 | 122156.1 | 146699.9757 | 65533.1035 | 81276.3026 | 107005 | 369167.25 | 149807 | 9630.45 | 49489.8125 | 8760 | 1720.1251 | 10213.844 | 6309.4424 | 4033.4658 | 0 | 0 | 0 | -1444.5642 | 0 | 2589.3087 | 8760 | 3839.6654 | 0 | 0 | 3843.066 | 4339.2219 | 2376.2412 | 15843.0434 | 9734.313 | 1091.9323 | 8367.6558 | 8760 | 20048.0689 | 1070.05 | 0 | 2227.75 | 1396620.7293 | 178372.614 | 432
193 | E | SOR | NAP | FC | FP | WC | R10 | 1.4877 | 18 | 0.45 | 8760 | 163777.0462 | 134308.8 | 153451.0256 | 65533.1035 | 81276.3026 | 107550 | 371047.5 | 150570 | 9679.5 | 49741.875 | 8760 | 1720.1251 | 9189.7499 | 7189.2672 | 4380.2795 | 0 | 0 | 0 | -1450.7529 | 0 | 2573.3527 | 8760 | 3840.5973 | 0 | 0 | 3843.066 | 4339.2219 | 2374.1644 | 15844.4203 | 9700.9997 | 1091.6674 | 7415.7866 | 8760 | 20067.3171 | 1075.5 | 0 | 2227.75 | 1396749.7733 | 178372.614 | 371.35
194 | E | SOR | NAP | FC | FP | WC | R10 | 1.4877 | 14 | 0.35 | 8760 | 160459.6751 | 151178.4 | 162822.4008 | 65533.1035 | 81276.3026 | 108102.5 | 372953.625 | 151343.5 | 9729.225 | 49997.4062 | 8760 | 1720.1251 | 7620.7761 | 8020.8584 | 5014.6026 | 0 | 0 | 0 | -1458.7525 | 0 | 2565.4696 | 8760 | 3839.7865 | 0 | 0 | 3843.066 | 4339.2219 | 2370.7694 | 15841.9849 | 9661.7382 | 1091.3408 | 5910.0712 | 8760 | 20085.8867 | 1081.025 | 0 | 2227.75 | 1396856.0524 | 178372.614 | 294.375
195 | E | SOR | NAP | FC | FP | WC | R10 | 1.4877 | 10 | 0.25 | 8760 | 140236.6511 | 178704.9 | 178113.8813 | 65533.1035 | 81276.3026 | 108522.5 | 374402.625 | 151931.5 | 9767.025 | 50191.6562 | 8760 | 1720.1251 | 5250.6034 | 9169.4129 | 6136.6191 | 0 | 0 | 0 | -1522.3775 | 0 | 2552.8228 | 8760 | 3837.9892 | 0 | 0 | 3843.066 | 4339.2219 | 2365.5988 | 15830.0319 | 9626.1745 | 1089.6857 | 3575.6056 | 8760 | 20091.7172 | 1085.225 | 0 | 2227.75 | 1396956.47 | 178372.614 | 231.65
196 | E | SOR | NAP | FC | FP | WC | R600 | 1.7084 | 25.5 | 1.9 | 8760 | 182973.4018 | 67166.55 | 116152.2624 | 65533.1035 | 49607.4578 | 116132.5 | 400657.125 | 162585.5 | 10451.925 | 53711.2812 | 8760 | 1720.1251 | 12978.8218 | 5119.0854 | 1178.8387 | 0 | 0 | 0 | -1540.2087 | 0 | 2411.3772 | 8760 | 4172.1419 | 0 | 0 | 4174.5441 | 2161.2871 | 2719.3124 | 17395.6304 | 10572.9878 | 1273.1828 | 11120.6916 | 8760 | 21899.8406 | 1161.325 | 0 | 2346.175 | 1510460.0713 | 155104.6654 | 355.6
197 | E | SOR | NAP | FC | FP | WC | R600 | 1.7084 | 21.5 | 1.6 | 8760 | 180381.4798 | 79049.25 | 122753.3223 | 65533.1035 | 49607.4578 | 116880 | 403236 | 163632 | 10519.2 | 54057 | 8760 | 1720.1251 | 11745.8662 | 6019.4805 | 1446.9789 | 0 | 0 | 0 | -1500.3066 | 0 | 2401.6074 | 8760 | 4171.7297 | 0 | 0 | 4174.5441 | 2161.2871 | 2713.0573 | 17399.2468 | 10524.0068 | 1272.6558 | 9952.5004 | 8760 | 21925.3943 | 1168.8 | 0 | 2346.175 | 1510619.2865 | 155104.6654 | 292.625
198 | E | SOR | NAP | FC | FP | WC | R600 | 1.7084 | 18 | 1.35 | 8760 | 178096.9894 | 91382.85 | 129604.8655 | 65533.1035 | 49607.4578 | 117462.5 | 405245.625 | 164447.5 | 10571.625 | 54326.4062 | 8760 | 1720.1251 | 10514.3503 | 6881.3745 | 1740.9872 | 0 | 0 | 0 | -1457.6894 | 0 | 2379.6717 | 8760 | 4171.1931 | 0 | 0 | 4174.5441 | 2161.2871 | 2707.7481 | 17416.9173 | 10487.0373 | 1272.2012 | 8793.9042 | 8760 | 21967.6527 | 1174.625 | 0 | 2346.175 | 1510643.3458 | 155104.6654 | 229.25
199 | E | SOR | NAP | FC | FP | WC | R600 | 1.7084 | 14 | 1.05 | 8760 | 176962.6269 | 105935.85 | 137689.3265 | 65533.1035 | 49607.4578 | 118150 | 407617.5 | 165410 | 10633.5 | 54644.375 | 8760 | 1720.1251 | 8946.09 | 7856.8936 | 2113.1561 | 0 | 0 | 0 | -1406.4118 | 0 | 2339.1411 | 8760 | 4171.7341 | 0 | 0 | 4174.5441 | 2161.2871 | 2700.0919 | 17433.5727 | 10451.6754 | 1271.6828 | 7337.2704 | 8760 | 22008.9894 | 1181.5 | 0 | 2346.175 | 1510817.5665 | 155104.6654 | 151.05
200 | E | SOR | NAP | FC | FP | WC | R600 | 1.7084 | 10 | 0.75 | 8760 | 176441.8799 | 122343.75 | 146804.2188 | 65533.1035 | 49607.4578 | 118730 | 409618.5 | 166222 | 10685.7 | 54912.625 | 8760 | 1720.1251 | 7096.8084 | 8800.849 | 2610.2079 | 0 | 0 | 0 | -1338.2778 | 0 | 2267.9947 | 8760 | 4171.5732 | 0 | 0 | 4174.5441 | 2161.2871 | 2691.0191 | 17440.456 | 10418.3577 | 1269.0776 | 5636.5224 | 8760 | 22047.4232 | 1187.3 | 0 | 2346.175 | 1510619.3762 | 155104.6654 | 75.15
201 | E | SOR | NAP | FC | FP | WC | R600 | 1.7084 | 25.5 | 1.3 | 8760 | 176997.0155 | 74749.5 | 120364.7315 | 65533.1035 | 49607.4578 | 115982.5 | 400139.625 | 162375.5 | 10438.425 | 53641.9062 | 8760 | 1720.1251 | 12303.4618 | 5571.2633 | 1436.5138 | 0 | 0 | 0 | -1533.538 | 0 | 2444.5812 | 8760 | 4171.2897 | 0 | 0 | 4174.5441 | 2161.2871 | 2718.384 | 17430.5038 | 10585.215 | 1272.9036 | 10409.6899 | 8760 | 21920.9482 | 1159.825 | 0 | 2346.175 | 1510507.156 | 155104.6654 | 406.225
202 | E | SOR | NAP | FC | FP | WC | R600 | 1.7084 | 21.5 | 1.1 | 8760 | 175492.3295 | 85615.65 | 126401.0791 | 65533.1035 | 49607.4578 | 116695 | 402597.75 | 163373 | 10502.55 | 53971.4375 | 8760 | 1720.1251 | 11239.3352 | 6302.0952 | 1715.7929 | 0 | 0 | 0 | -1501.3632 | 0 | 2436.0264 | 8760 | 4171.7793 | 0 | 0 | 4174.5441 | 2161.2871 | 2715.7742 | 17428.9748 | 10539.2554 | 1272.8492 | 9412.2071 | 8760 | 21943.8848 | 1166.95 | 0 | 2346.175 | 1510656.6797 | 155104.6654 | 327.7
203 | E | SOR | NAP | FC | FP | WC | R600 | 1.7084 | 18 | 0.9 | 8760 | 173955.384 | 97347.15 | 132918.1446 | 65533.1035 | 49607.4578 | 117255 | 404529.75 | 164157 | 10552.95 | 54230.4375 | 8760 | 1720.1251 | 10100.1433 | 7147.6113 | 1996.3609 | 0 | 0 | 0 | -1467.9243 | 0 | 2420.3318 | 8760 | 4171.296 | 0 | 0 | 4174.5441 | 2161.2871 | 2711.1523 | 17442.128 | 10502.3798 | 1272.2118 | 8343.7517 | 8760 | 21978.8223 | 1172.55 | 0 | 2346.175 | 1510602.4229 | 155104.6654 | 261.85
204 | E | SOR | NAP | FC | FP | WC | R600 | 1.7084 | 14 | 0.7 | 8760 | 172645.6536 | 110971.35 | 140486.64 | 65533.1035 | 49607.4578 | 118030 | 407203.5 | 165242 | 10622.7 | 54588.875 | 8760 | 1720.1251 | 8593.5067 | 8069.6878 | 2368.027 | 0 | 0 | 0 | -1421.7129 | 0 | 2384.5247 | 8760 | 4171.9723 | 0 | 0 | 4174.5441 | 2161.2871 | 2703.7084 | 17441.6718 | 10460.7047 | 1271.1954 | 6944.1024 | 8760 | 22010.6297 | 1180.3 | 0 | 2346.175 | 1510560.6595 | 155104.6654 | 185.775
205 | E | SOR | NAP | FC | FP | WC | R60 | 1.7084 | 10 | 0.5 | 8760 | 173737.8986 | 127504.8 | 149671.2776 | 65533.1035 | 49607.4578 | 118562.5 | 409040.625 | 165987.5 | 10670.625 | 54835.1562 | 8760 | 1720.1251 | 6880.9958 | 9224.5974 | 2739.8106 | 0 | 0 | 0 | -1389.0357 | 0 | 2307.0163 | 8760 | 4171.1244 | 0 | 0 | 4174.5441 | 2161.2871 | 2695.138 | 17452.4798 | 10425.989 | 1268.4166 | 5381.3154 | 8760 | 22041.3231 | 1185.625 | 0 | 2346.175 | 1510736.5566 | 155104.6654 | 109.825
206 | E | SOR | NAP | FC | FP | WC | R60 | 1.7084 | 25.5 | 0.65 | 8760 | 165390.9498 | 90332.55 | 129021.4044 | 65533.1035 | 49607.4578 | 115837.5 | 399639.375 | 162172.5 | 10425.375 | 53574.8438 | 8760 | 1720.1251 | 11057.3147 | 6293.0952 | 1982.3962 | 0 | 0 | 0 | -1515.5897 | 0 | 2507.4435 | 8760 | 4171.7922 | 0 | 0 | 4174.5441 | 2161.2871 | 2717.0837 | 17478.625 | 10609.6748 | 1272.0612 | 9130.8345 | 8760 | 21958.3225 | 1158.375 | 0 | 2346.175 | 1510392.9697 | 155104.6654 | 498.775
207 | E | SOR | NAP | FC | FP | WC | R60 | 1.7084 | 21.5 | 0.55 | 8760 | 164211.1039 | 100028.25 | 134407.5453 | 65533.1035 | 49607.4578 | 116377.5 | 401502.375 | 162928.5 | 10473.975 | 53824.5938 | 8760 | 1720.1251 | 10144.0343 | 6912.5425 | 2242.4223 | 0 | 0 | 0 | -1494.4078 | 0 | 2502.0446 | 8760 | 4171.2645 | 0 | 0 | 4174.5441 | 2161.2871 | 2712.8852 | 17464.6643 | 10564.6709 | 1271.4328 | 8281.9086 | 8760 | 21956.6234 | 1163.775 | 0 | 2346.175 | 1510458.954 | 155104.6654 | 425.375
208 | E | SOR | NAP | FC | FP | WC | R60 | 1.7084 | 18 | 0.45 | 8760 | 163823.9169 | 110297.7 | 140112.4149 | 65533.1035 | 49607.4578 | 116912.5 | 403348.125 | 163677.5 | 10522.125 | 54072.0312 | 8760 | 1720.1251 | 9158.4024 | 7812.3917 | 2444.4811 | 0 | 0 | 0 | -1488.9082 | 0 | 2492.2599 | 8760 | 4171.234 | 0 | 0 | 4174.5441 | 2161.2871 | 2708.4148 | 17456.0422 | 10527.7525 | 1270.3425 | 7363.9673 | 8760 | 21973.3766 | 1169.125 | 0 | 2346.175 | 1510604.6464 | 155104.6654 | 359.325
209 | E | SOR | NAP | FC | FP | WC | R60 | 1.7084 | 14 | 0.35 | 8760 | 161379.8972 | 125815.95 | 148733.0902 | 65533.1035 | 49607.4578 | 117560 | 405582 | 164584 | 10580.4 | 54371.5 | 8760 | 1720.1251 | 7673.5908 | 8738.554 | 2891.1679 | 0 | 0 | 0 | -1484.2024 | 0 | 2480.7863 | 8760 | 4171.1215 | 0 | 0 | 4174.5441 | 2161.2871 | 2700.1696 | 17448.3267 | 10485.463 | 1268.4427 | 5946.8643 | 8760 | 21995.8665 | 1175.6 | 0 | 2346.175 | 1510472.555 | 155104.6654 | 275.8
210 | E | SOR | NAP | FC | FP | WC | R60 | 1.7084 | 10 | 0.25 | 8760 | 141417.7722 | 151984.35 | 163270.121 | 65533.1035 | 49607.4578 | 118042.5 | 407246.625 | 165259.5 | 10623.825 | 54594.6562 | 8760 | 1720.1251 | 5316.1275 | 9993.2562 | 3814.3671 | 0 | 0 | 0 | -1529.135 | 0 | 2455.8212 | 8760 | 4170.7252 | 0 | 0 | 4174.5441 | 2161.2871 | 2686.8574 | 17451.0034 | 10453.077 | 1264.2717 | 3637.3873 | 8760 | 22015.8183 | 1180.425 | 0 | 2346.175 | 1510612.0811 | 155104.6654 | 213.8
211 | E | SOR | STR | FC | ET | HC | OFF0 | 0.13269 | 13 | 1
212 | E | SOR | STR | FC | ET | HC | OFF0 | 0.13269 | 11 | 0.85
213 | E | SOR | STR | FC | ET | HC | OFF0 | 0.13269 | 9 | 0.7
214 | E | SOR | STR | FC | ET | HC | OFF0 | 0.13269 | 7 | 0.55
215 | E | SOR | STR | FC | ET | HC | OFF0 | 0.13269 | 5 | 0.4
216 | E | SOR | STR | FC | ET | HC | OFF0 | 0.13269 | 13 | 0.65
217 | E | SOR | STR | FC | ET | HC | OFF0 | 0.13269 | 11 | 0.55
218 | E | SOR | STR | FC | ET | HC | OFF0 | 0.13269 | 9 | 0.45
219 | E | SOR | STR | FC | ET | HC | OFF0 | 0.13269 | 7 | 0.35
220 | E | SOR | STR | FC | ET | HC | OFF | 0.13269 | 5 | 0.25
221 | E | SOR | STR | FC | ET | HC | OFF | 0.13269 | 13 | 0.35
222 | E | SOR | STR | FC | ET | HC | OFF | 0.13269 | 11 | 0.3
223 | E | SOR | STR | FC | ET | HC | OFF | 0.13269 | 7 | 0.2
224 | E | SOR | STR | FC | ET | WC | OFF0 | 0.26072 | 25.5 | 1.9 | 8760 | 145710.4514 | 112267.35 | 141206.592 | 0 | 113684.3977 | 84097.5 | 290136.375 | 117736.5 | 7568.775 | 2489.286 | 8760 | 1150.2925 | 9904.6732 | 2874.8638 | 3043.3327 | 0 | 0 | 0 | -1298.7502 | 0 | 2634.9731 | 8760 | 2671.2245 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 10216.6155 | 7559.5463 | 0 | 8067.1071 | 8760 | 12391.8283 | 840.975 | 0 | 1446.5 | 969212.2982 | 186766.0544 | 322.475 | 11.65
225 | E | SOR | STR | FC | ET | WC | OFF0 | 0.26072 | 21.5 | 1.6 | 8760 | 142074.6373 | 123963.75 | 147704.1588 | 0 | 113684.3977 | 84495 | 291507.75 | 118293 | 7604.55 | 2501.052 | 8760 | 1150.2925 | 8798.6196 | 3587.8966 | 3234.987 | 0 | 0 | 0 | -1270.5013 | 0 | 2607.5702 | 8760 | 2672.0434 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 10180.8261 | 7517.8046 | 0 | 7023.9186 | 8760 | 12357.6126 | 844.95 | 0 | 1446.5 | 969274.1656 | 186766.0544 | 264.075 | 13.2
226 | E | SOR | STR | FC | ET | WC | OFF0 | 0.26072 | 18 | 1.35 | 8760 | 139058.6686 | 135198.45 | 153945.2427 | 0 | 113684.3977 | 84715 | 292266.75 | 118601 | 7624.35 | 2507.564 | 8760 | 1150.2925 | 7721.6192 | 4216.5433 | 3417.0732 | 0 | 0 | 0 | -1247.3232 | 0 | 2579.7178 | 8760 | 2667.8984 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 10125.4441 | 7461.1188 | 0 | 6007.2502 | 8760 | 12299.6074 | 847.15 | 0 | 1446.5 | 969251.9743 | 186766.0544 | 209.125 | 12.675
227 | E | SOR | STR | FC | ET | WC | OFF0 | 0.26072 | 14 | 1.05 | 8760 | 135961.6258 | 149264.1 | 161758.9717 | 0 | 113684.3977 | 85085 | 293543.25 | 119119 | 7657.65 | 2518.516 | 8760 | 1150.2925 | 6362.7717 | 5013.9555 | 3647.4538 | 0 | 0 | 0 | -1223.7772 | 0 | 2534.6151 | 8760 | 2668.5139 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 10083.9065 | 7414.3046 | 0 | 4731.8221 | 8760 | 12257.0096 | 850.85 | 0 | 1446.5 | 969271.5299 | 186766.0544 | 145.35 | 16.275
228 | E | SOR | STR | FC | ET | WC | OFF0 | 0.26072 | 10 | 0.75 | 8760 | 133131.485 | 164542.05 | 170246.1559 | 0 | 113684.3977 | 85257.5 | 294138.375 | 119360.5 | 7673.175 | 2523.622 | 8760 | 1150.2925 | 4854.4755 | 5817.586 | 3871.6464 | 0 | 0 | 0 | -1200.0728 | 0 | 2448.9642 | 8760 | 2664.0011 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 10025.0498 | 7356.1527 | 0 | 3343.9832 | 8760 | 12193.4345 | 852.575 | 0 | 1446.5 | 969135.395 | 186766.0544 | 78.65 | 19.475
229 | E | SOR | STR | FC | ET | WC | OFF0 | 0.26072 | 25.5 | 1.3 | 8760 | 143547.9966 | 115414.2 | 142954.7254 | 0 | 113684.3977 | 84022.5 | 289877.625 | 117631.5 | 7562.025 | 2487.066 | 8760 | 1150.2925 | 9682.591 | 3065.6065 | 3066.4232 | 0 | 0 | 0 | -1311.2882 | 0 | 2660.2276 | 8760 | 2671.6165 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 10235.7909 | 7577.0054 | 0 | 7826.039 | 8760 | 12411.8173 | 840.225 | 0 | 1446.5 | 969316.1771 | 186766.0544 | 339.6 | 11.55
230 | E | SOR | STR | FC | ET | WC | OFF0 | 0.26072 | 21.5 | 1.1 | 8760 | 140311.1414 | 127210.5 | 149507.7885 | 0 | 113684.3977 | 84370 | 291076.5 | 118118 | 7593.3 | 2497.352 | 8760 | 1150.2925 | 8616.966 | 3742.9198 | 3300.42 | 0 | 0 | 0 | -1291.7242 | 0 | 2639.118 | 8760 | 2671.5959 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 10197.0392 | 7533.3197 | 0 | 6816.8111 | 8760 | 12373.1842 | 843.7 | 0 | 1446.5 | 969153.5317 | 186766.0544 | 279.8 | 12.7
231 | E | SOR | STR | FC | ET | WC | OFF0 | 0.26072 | 18 | 0.9 | 8760 | 137318.2639 | 138253.5 | 155642.3795 | 0 | 113684.3977 | 84610 | 291904.5 | 118454 | 7614.9 | 2504.456 | 8760 | 1150.2925 | 7563.4632 | 4344.8588 | 3504.1392 | 0 | 0 | 0 | -1276.5974 | 0 | 2612.4877 | 8760 | 2668.4668 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 10146.0228 | 7479.2139 | 0 | 5820.512 | 8760 | 12319.8653 | 846.1 | 0 | 1446.5 | 969363.8278 | 186766.0544 | 227.4 | 13.35
232 | E | SOR | STR | FC | ET | WC | OFF0 | 0.26072 | 14 | 0.7 | 8760 | 134343.6233 | 152801.1 | 163723.8407 | 0 | 113684.3977 | 84940 | 293043 | 118916 | 7644.6 | 2514.224 | 8760 | 1150.2925 | 6240.8869 | 5085.6073 | 3765.6333 | 0 | 0 | 0 | -1261.3774 | 0 | 2572.5124 | 8760 | 2666.7524 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 10090.1522 | 7420.294 | 0 | 4574.2012 | 8760 | 12261.7807 | 849.4 | 0 | 1446.5 | 969275.9317 | 186766.0544 | 164.375 | 14.65
233 | E | SOR | STR | FC | ET | WC | OFF | 0.26072 | 10 | 0.5 | 8760 | 132167.5884 | 166442.85 | 171302.0855 | 0 | 113684.3977 | 85190 | 293905.5 | 119266 | 7667.1 | 2521.624 | 8760 | 1150.2925 | 4803.109 | 5904.5284 | 3841.2741 | 0 | 0 | 0 | -1273.7418 | 0 | 2457.9409 | 8760 | 2663.7756 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 10033.5732 | 7363.2891 | 0 | 3282.7697 | 8760 | 12201.3334 | 851.9 | 0 | 1446.5 | 969094.2104 | 186766.0544 | 94.45 | 16.775
234 | E | SOR | STR | FC | ET | WC | OFF | 0.26072 | 25.5 | 0.65 | 8760 | 138310.7632 | 124021.8 | 147736.4066 | 0 | 113684.3977 | 83967.5 | 289687.875 | 117554.5 | 7557.075 | 2485.438 | 8760 | 1150.2925 | 9149.8309 | 3431.3537 | 3300.7035 | 0 | 0 | 0 | -1355.1249 | 0 | 2730.1877 | 8760 | 2675.145 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 10286.0158 | 7619.5404 | 0 | 7238.0004 | 8760 | 12468.4227 | 839.675 | 0 | 1446.5 | 969441.7575 | 186766.0544 | 389.9 | 10.225
235 | E | SOR | STR | FC | ET | WC | OFF | 0.26072 | 21.5 | 0.55 | 8760 | 135713.5682 | 135446.85 | 154083.2335 | 0 | 113684.3977 | 84207.5 | 290515.875 | 117890.5 | 7578.675 | 2492.542 | 8760 | 1150.2925 | 8175.993 | 4014.4611 | 3597.6516 | 0 | 0 | 0 | -1350.6304 | 0 | 2720.5543 | 8760 | 2672.5668 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 10237.4748 | 7568.1374 | 0 | 6308.8644 | 8760 | 12416.6956 | 842.075 | 0 | 1446.5 | 969392.289 | 186766.0544 | 327.1 | 11.025
236 | E | SOR | STR | FC | ET | WC | OFF | 0.26072 | 18 | 0.45 | 8760 | 133611.2296 | 146430.45 | 160184.8267 | 0 | 113684.3977 | 84487.5 | 291481.875 | 118282.5 | 7603.875 | 2500.83 | 8760 | 1150.2925 | 7248.2438 | 4554.2081 | 3454.9442 | 0 | 0 | 0 | -1368.4063 | 0 | 2679.8722 | 8760 | 2670.0115 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 10183.9671 | 7509.6145 | 0 | 5451.4142 | 8760 | 12361.1931 | 844.875 | 0 | 1446.5 | 969228.3061 | 186766.0544 | 273.3 | 12.075
237 | E | SOR | STR | FC | ET | WC | OFF | 0.26072 | 14 | 0.35 | 8760 | 131253.4834 | 160786.35 | 168159.795 | 0 | 113684.3977 | 84767.5 | 292447.875 | 118674.5 | 7629.075 | 2509.118 | 8760 | 1150.2925 | 5990.7049 | 5196.733 | 3736.8567 | 0 | 0 | 0 | -1387.3573 | 0 | 2661.8019 | 8760 | 2666.2052 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 10120.1899 | 7440.905 | 0 | 4246.722 | 8760 | 12292.7443 | 847.675 | 0 | 1446.5 | 969310.9449 | 186766.0544 | 203.225 | 12.45
238 | E | SOR | STR | FC | ET | WC | OFF | 0.26072 | 10 | 0.25 | 8760 | 124903.3491 | 181611.45 | 179728.5237 | 0 | 113684.3977 | 84972.5 | 293155.125 | 118961.5 | 7647.525 | 2515.186 | 8760 | 1150.2925 | 4386.8382 | 6231.7858 | 4918.2286 | 0 | 0 | 0 | -1464.2036 | 0 | 2748.5998 | 8760 | 2662.9712 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 10071.5951 | 7390.4829 | 0 | 2584.3017 | 8760 | 12241.1619 | 849.725 | 0 | 1446.5 | 969315.676 | 186766.0544 | 131.475 | 13.175
239 | E | SOR | STR | FC | FP | HC | OFF0 | 0.13269 | 13 | 1 | 8760 | 108937.7794 | 91809.45 | 129841.8497 | 0 | 100659.8294 | 46082.5 | 158984.625 | 64515.5 | 4147.425 | 274144.5206 | 8760 | 1150.2925 | 4310.9153 | 2425.18 | 2579.8168 | 0 | 0 | 0 | -1195.7315 | 0 | 1964.4718 | 8760 | 1406.9263 | 0 | 0 | 1406.1463 | 2786.0994 | 0 | 5423.624 | 3692.5108 | 0 | 3160.3607 | 8760 | 0 | 460.825 | 0 | 1446.5 | 481945.2577 | 186766.0544 | 39.15 | -112.4446
240 | E | SOR | STR | FC | FP | HC | OFF0 | 0.13269 | 11 | 0.85 | 8760 | 108084.3701 | 98498.7 | 133557.8519 | 0 | 100659.8294 | 46287.5 | 159691.875 | 64802.5 | 4165.875 | 275375.8449 | 8760 | 1150.2925 | 3820.3125 | 2730.117 | 2719.3559 | 0 | 0 | 0 | -1180.6165 | 0 | 1949.5549 | 8760 | 1407.1698 | 0 | 0 | 1406.1463 | 2786.0994 | 0 | 5436.4165 | 3684.0633 | 0 | 2705.6176 | 8760 | 0 | 462.875 | 0 | 1446.5 | 482020.3975 | 186766.0544 | 25.425 | -111.9627
241 | E | SOR | STR | FC | FP | HC | OFF0 | 0.13269 | 9 | 0.7 | 8760 | 106707.8418 | 107153.55 | 138365.7814 | 0 | 100659.8294 | 46450 | 160252.5 | 65030 | 4180.5 | 276344.3629 | 8760 | 1150.2925 | 3256.3698 | 3060.7905 | 2923.2505 | 0 | 0 | 0 | -1171.2969 | 0 | 1939.1913 | 8760 | 1406.6205 | 0 | 0 | 1406.1463 | 2786.0994 | 0 | 5443.4505 | 3676.036 | 0 | 2171.2606 | 8760 | 0 | 464.5 | 0 | 1446.5 | 481989.4173 | 186766.0544 | 14.8 | -111.838
242 | E | SOR | STR | FC | FP | HC | OFF0 | 0.13269 | 7 | 0.55 | 8760 | 105626.3313 | 116564.4 | 143593.6828 | 0 | 100659.8294 | 46547.5 | 160588.875 | 65166.5 | 4189.275 | 276925.1326 | 8760 | 1150.2925 | 2659.3495 | 3444.3504 | 3125.1265 | 0 | 0 | 0 | -1170.6726 | 0 | 1923.2517 | 8760 | 1406.6086 | 0 | 0 | 1406.1463 | 2786.0994 | 0 | 5441.1989 | 3671.1099 | 0 | 1610.1744 | 8760 | 0 | 465.475 | 0 | 1446.5 | 482108.9111 | 186766.0544 | 5.8 | -109.52
243 | E | SOR | STR | FC | FP | HC | OFF0 | 0.13269 | 5 | 0.4 | 8760 | 105554.2644 | 124654.95 | 148088.1332 | 0 | 100659.8294 | 46552.5 | 160606.125 | 65173.5 | 4189.725 | 276942.5688 | 8760 | 1150.2925 | 2042.0822 | 3880.1581 | 3261.6981 | 0 | 0 | 0 | -1213.306 | 0 | 1864.9554 | 8760 | 1406.2091 | 0 | 0 | 1406.1463 | 2786.0994 | 0 | 5425.1684 | 3669.1553 | 0 | 1075.2344 | 8760 | 0 | 465.525 | 0 | 1446.5 | 482031.0942 | 186766.0544 | 0 | -111.554
244 | E | SOR | STR | FC | FP | HC | OFF0 | 0.13269 | 13 | 0.65 | 8760 | 106445.9595 | 98244.9 | 133416.8613 | 0 | 100659.8294 | 45805 | 158027.25 | 64127 | 4122.45 | 272503.0828 | 8760 | 1150.2925 | 4120.434 | 2558.0779 | 2738.9813 | 0 | 0 | 0 | -1232.4191 | 0 | 1997.0829 | 8760 | 1406.214 | 0 | 0 | 1406.1463 | 2786.0994 | 0 | 5428.5294 | 3700.6515 | 0 | 2936.7278 | 8760 | 0 | 458.05 | 0 | 1446.5 | 481860.7592 | 186766.0544 | 53.475 | -112.1308
245 | E | SOR | STR | FC | FP | HC | OFF0 | 0.13269 | 11 | 0.55 | 8760 | 105276.8639 | 106223.4 | 137849.0658 | 0 | 100659.8294 | 46045 | 158855.25 | 64463 | 4144.05 | 273926.8789 | 8760 | 1150.2925 | 3628.0873 | 2846.2598 | 2911.0838 | 0 | 0 | 0 | -1229.4634 | 0 | 1996.8894 | 8760 | 1406.2179 | 0 | 0 | 1406.1463 | 2786.0994 | 0 | 5428.9718 | 3690.5531 | 0 | 2464.9056 | 8760 | 0 | 460.45 | 0 | 1446.5 | 482031.2504 | 186766.0544 | 40 | -111.2817
246 | E | SOR | STR | FC | FP | HC | OFF0 | 0.13269 | 9 | 0.45 | 8760 | 107221.8924 | 111117.15 | 140567.6346 | 0 | 100659.8294 | 46200 | 159390 | 64680 | 4158 | 274850.1904 | 8760 | 1150.2925 | 3201.0425 | 3192.1102 | 2966.9261 | 0 | 0 | 0 | -1254.0691 | 0 | 1971.6083 | 8760 | 1406.7578 | 0 | 0 | 1406.1463 | 2786.0994 | 0 | 5429.3786 | 3685.0204 | 0 | 2087.9445 | 8760 | 0 | 462 | 0 | 1446.5 | 482091.9533 | 186766.0544 | 26.4 | -111.1649
247 | E | SOR | STR | FC | FP | HC | OFF0 | 0.13269 | 7 | 0.35 | 8760 | 104095.8828 | 121952.25 | 146586.7333 | 0 | 100659.8294 | 46322.5 | 159812.625 | 64851.5 | 4169.025 | 275577.9243 | 8760 | 1150.2925 | 2556.9613 | 3594.9206 | 3226.6222 | 0 | 0 | 0 | -1282.7775 | 0 | 1959.4727 | 8760 | 1407.0192 | 0 | 0 | 1406.1463 | 2786.0994 | 0 | 5431.3031 | 3680.9302 | 0 | 1473.0133 | 8760 | 0 | 463.225 | 0 | 1446.5 | 481914.1613 | 186766.0544 | 13.25 | -111.8297
248 | E | SOR | STR | FC | FP | HC | OFF | 0.13269 | 5 | 0.25 | 8760 | 81987.1812 | 141998.4 | 157722.7408 | 0 | 100659.8294 | 46377.5 | 160002.375 | 64928.5 | 4173.975 | 275902.3121 | 8760 | 1150.2925 | 1555.6416 | 4089.6054 | 3798.1966 | 0 | 0 | 0 | -1381.3409 | 0 | 1893.4008 | 8760 | 1407.0413 | 0 | 0 | 1406.1463 | 2786.0994 | 0 | 5426.0095 | 3678.3348 | 0 | 513.8377 | 8760 | 0 | 463.775 | 0 | 1446.5 | 481900.5926 | 186766.0544 | 2 | -109.7514
249 | E | SOR | STR | FC | FP | HC | OFF | 0.13269 | 13 | 0.35 | 8760 | 102394.4812 | 109445.85 | 139639.1965 | 0 | 100659.8294 | 45520 | 157044 | 63728 | 4096.8 | 270806.9172 | 8760 | 1150.2925 | 3747.5713 | 2853.2167 | 2991.0732 | 0 | 0 | 0 | -1342.6321 | 0 | 2065.6172 | 8760 | 1406.9737 | 0 | 0 | 1406.1463 | 2786.0994 | 0 | 5444.6931 | 3716.9066 | 0 | 2509.1755 | 8760 | 0 | 455.2 | 0 | 1446.5 | 481995.8374 | 186766.0544 | 86.15 | -110.9194
250 | E | SOR | STR | FC | FP | HC | OFF | 0.13269 | 11 | 0.3 | 8760 | 100736.4077 | 117948.15 | 144362.3816 | 0 | 100659.8294 | 45735 | 157785.75 | 64029 | 4116.15 | 272077.4147 | 8760 | 1150.2925 | 3271.1013 | 3125.2429 | 3219.8203 | 0 | 0 | 0 | -1363.8567 | 0 | 2066.638 | 8760 | 1406.8063 | 0 | 0 | 1406.1463 | 2786.0994 | 0 | 5429.0858 | 3705.4796 | 0 | 2047.2494 | 8760 | 0 | 457.35 | 0 | 1446.5 | 481906.9319 | 186766.0544 | 69.6 | -112.1669
251 | E | SOR | STR | FC | FP | HC | OFF | 0.13269 | 7 | 0.2 | 8760 | 84849.1354 | 132576.75 | 152488.8398 | 0 | 100659.8294 | 45920 | 158424 | 64288 | 4132.8 | 273175.6132 | 8760 | 1150.2925 | 2448.2478 | 3500.0636 | 3637.5582 | 0 | 0 | 0 | -1421.4033 | 0 | 1978.819 | 8760 | 1406.9243 | 0 | 0 | 1406.1463 | 2786.0994 | 0 | 5432.8903 | 3699.2341 | 0 | 1300.3533 | 8760 | 0 | 459.2 | 0 | 1446.5 | 482035.7204 | 186766.0544 | 54.85 | -111.3961
252 | E | SOR | STR | FC | FP | WC | OFF0 | 0.26072 | 25.5 | 1.9 | 8760 | 122112.8966 | 125780.85 | 148713.5915 | 0 | 113684.3977 | 74415 | 256731.75 | 104181 | 6697.35 | 34416.9375 | 8760 | 1150.2925 | 7418.0598 | 3524.7652 | 3252.128 | 0 | 0 | 0 | -1232.9147 | 0 | 1982.6887 | 8760 | 2763.3034 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 14974.6831 | 6867.8698 | 0 | 6180.6008 | 8760 | 18923.0886 | 744.15 | 0 | 1446.5 | 970616.0922 | 186766.0544 | 103.975 | 700.925
253 | E | SOR | STR | FC | FP | WC | OFF0 | 0.26072 | 21.5 | 1.6 | 8760 | 118717.5959 | 134840.7 | 153746.5059 | 0 | 113684.3977 | 74852.5 | 258241.125 | 104793.5 | 6736.725 | 34619.2812 | 8760 | 1150.2925 | 6583.9577 | 4080.1349 | 3420.9244 | 0 | 0 | 0 | -1210.7833 | 0 | 1985.7916 | 8760 | 2763.4235 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 15030.9415 | 6847.6941 | 0 | 5373.4675 | 8760 | 19001.8398 | 748.525 | 0 | 1446.5 | 970591.6919 | 186766.0544 | 82.85 | 705.525
254 | E | SOR | STR | FC | FP | WC | OFF0 | 0.26072 | 18 | 1.35 | 8760 | 115572.5122 | 144013.95 | 158842.4162 | 0 | 113684.3977 | 75197.5 | 259431.375 | 105276.5 | 6767.775 | 34778.8438 | 8760 | 1150.2925 | 5773.7168 | 4531.1631 | 3534.1453 | 0 | 0 | 0 | -1189.9814 | 0 | 1982.1416 | 8760 | 2763.4194 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 15073.8929 | 6829.2732 | 0 | 4594.3614 | 8760 | 19069.248 | 751.975 | 0 | 1446.5 | 970549.1859 | 186766.0544 | 60.525 | 708.875
255 | E | SOR | STR | FC | FP | WC | OFF0 | 0.26072 | 14 | 1.05 | 8760 | 112388.3837 | 155355.3 | 165142.7461 | 0 | 113684.3977 | 75535 | 260595.75 | 105749 | 6798.15 | 34934.9375 | 8760 | 1150.2925 | 4761.1735 | 5091.7543 | 3758.6177 | 0 | 0 | 0 | -1166.6824 | 0 | 1972.5197 | 8760 | 2763.4822 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 15112.4491 | 6811.5558 | 0 | 3626.836 | 8760 | 19124.5955 | 755.35 | 0 | 1446.5 | 970561.2661 | 186766.0544 | 36.375 | 711.15
256 | E | SOR | STR | FC | FP | WC | OFF0 | 0.26072 | 10 | 0.75 | 8760 | 109787.8979 | 167548.5 | 171916.2945 | 0 | 113684.3977 | 75800 | 261510 | 106120 | 6822 | 35057.5 | 8760 | 1150.2925 | 3654.1799 | 5657.5615 | 3963.8741 | 0 | 0 | 0 | -1152.1707 | 0 | 1955.3033 | 8760 | 2763.4971 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 15145.4644 | 6795.5504 | 0 | 2570.5885 | 8760 | 19170.5533 | 758 | 0 | 1446.5 | 970627.2137 | 186766.0544 | 16.2 | 713.95
257 | E | SOR | STR | FC | FP | WC | OFF0 | 0.26072 | 25.5 | 1.3 | 8760 | 120453.6965 | 129708 | 150895.196 | 0 | 113684.3977 | 74207.5 | 256015.875 | 103890.5 | 6678.675 | 34320.9688 | 8760 | 1150.2925 | 7161.3451 | 3720.1394 | 3353.3526 | 0 | 0 | 0 | -1240.9996 | 0 | 2011.4747 | 8760 | 2763.4334 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 14951.5196 | 6883.1934 | 0 | 5894.9332 | 8760 | 18891.4582 | 742.075 | 0 | 1446.5 | 970547.1657 | 186766.0544 | 116.325 | 698.625
258 | E | SOR | STR | FC | FP | WC | OFF0 | 0.26072 | 21.5 | 1.1 | 8760 | 116790.8055 | 138993.3 | 156053.3521 | 0 | 113684.3977 | 74625 | 257456.25 | 104475 | 6716.25 | 34514.0625 | 8760 | 1150.2925 | 6353.6047 | 4208.4251 | 3530.0738 | 0 | 0 | 0 | -1224.0198 | 0 | 2013.1379 | 8760 | 2763.2665 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 15003.0664 | 6858.7296 | 0 | 5116.6122 | 8760 | 18963.2156 | 746.25 | 0 | 1446.5 | 970588.1416 | 186766.0544 | 95.55 | 702.725
259 | E | SOR | STR | FC | FP | WC | OFF0 | 0.26072 | 18 | 0.9 | 8760 | 113546.0822 | 148008.6 | 161061.5182 | 0 | 113684.3977 | 74970 | 258646.5 | 104958 | 6747.3 | 34673.625 | 8760 | 1150.2925 | 5560.9506 | 4631.4603 | 3709.1995 | 0 | 0 | 0 | -1211.6363 | 0 | 2011.3587 | 8760 | 2763.1947 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 15046.6108 | 6838.8134 | 0 | 4353.27 | 8760 | 19024.7839 | 749.7 | 0 | 1446.5 | 970668.6594 | 186766.0544 | 71.2 | 706.375
260 | E | SOR | STR | FC | FP | WC | OFF0 | 0.26072 | 14 | 0.7 | 8760 | 110608.5446 | 159572.7 | 167485.5899 | 0 | 113684.3977 | 75380 | 260061 | 105532 | 6784.2 | 34863.25 | 8760 | 1150.2925 | 4586.7474 | 5204.5947 | 3904.9962 | 0 | 0 | 0 | -1201.301 | 0 | 2010.4863 | 8760 | 2763.6949 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 15094.883 | 6819.9064 | 0 | 3415.4204 | 8760 | 19097.8411 | 753.8 | 0 | 1446.5 | 970665.8912 | 186766.0544 | 46.675 | 710.95
261 | E | SOR | STR | FC | FP | WC | OFF | 0.26072 | 10 | 0.5 | 8760 | 109705.476 | 170229.6 | 173405.6952 | 0 | 113684.3977 | 75647.5 | 260983.875 | 105906.5 | 6808.275 | 34986.9688 | 8760 | 1150.2925 | 3605.5654 | 5782.0949 | 3944.5802 | 0 | 0 | 0 | -1228.0869 | 0 | 1974.312 | 8760 | 2763.4924 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 15124.9268 | 6801.8944 | 0 | 2505.8003 | 8760 | 19142.7412 | 756.475 | 0 | 1446.5 | 970630.461 | 186766.0544 | 24.925 | 713.475
262 | E | SOR | STR | FC | FP | WC | OFF | 0.26072 | 25.5 | 0.65 | 8760 | 115314.0885 | 141216.75 | 157288.5198 | 0 | 113684.3977 | 73820 | 254679 | 103348 | 6643.8 | 34141.75 | 8760 | 1150.2925 | 6488.5938 | 4082.6442 | 3645.9712 | 0 | 0 | 0 | -1278.7939 | 0 | 2074.3593 | 8760 | 2763.4407 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 14914.627 | 6905.6405 | 0 | 5179.0843 | 8760 | 18837.5452 | 738.2 | 0 | 1446.5 | 970493.1567 | 186766.0544 | 153.475 | 694.725
263 | E | SOR | STR | FC | FP | WC | OFF | 0.26072 | 21.5 | 0.55 | 8760 | 111766.3477 | 150321.15 | 162346.1826 | 0 | 113684.3977 | 74220 | 256059 | 103908 | 6679.8 | 34326.75 | 8760 | 1150.2925 | 5765.1951 | 4486.6991 | 4167.7443 | 0 | 0 | 0 | -1277.3307 | 0 | 2080.2265 | 8760 | 2763.4107 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 14954.6532 | 6878.7413 | 0 | 4482.5627 | 8760 | 18894.8264 | 742.2 | 0 | 1446.5 | 970543.829 | 186766.0544 | 126.025 | 697.25
264 | E | SOR | STR | FC | FP | WC | OFF | 0.26072 | 18 | 0.45 | 8760 | 111050.35 | 157227.75 | 166182.9268 | 0 | 113684.3977 | 74577.5 | 257292.375 | 104408.5 | 6711.975 | 34492.0938 | 8760 | 1150.2925 | 5176.7101 | 4898.6068 | 3701.979 | 0 | 0 | 0 | -1303.7089 | 0 | 2075.484 | 8760 | 2763.4735 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 15000.8178 | 6859.3879 | 0 | 3927.7339 | 8760 | 18963.2175 | 745.775 | 0 | 1446.5 | 970651.4247 | 186766.0544 | 100.275 | 701.85
265 | E | SOR | STR | FC | FP | WC | OFF | 0.26072 | 14 | 0.35 | 8760 | 106505.62 | 169231.95 | 172851.4822 | 0 | 113684.3977 | 74982.5 | 258689.625 | 104975.5 | 6748.425 | 34679.4062 | 8760 | 1150.2925 | 4214.9108 | 5461.8176 | 3978.1662 | 0 | 0 | 0 | -1330.3533 | 0 | 2072.0895 | 8760 | 2763.5204 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 15052.4066 | 6836.1344 | 0 | 2996.4156 | 8760 | 19034.1697 | 749.825 | 0 | 1446.5 | 970768.9644 | 186766.0544 | 73 | 707.15
266 | E | SOR | STR | FC | FP | WC | OFF | 0.26072 | 10 | 0.25 | 8760 | 87583.002 | 189055.35 | 183863.7479 | 0 | 113684.3977 | 75287.5 | 259741.875 | 105402.5 | 6775.875 | 34820.4688 | 8760 | 1150.2925 | 2776.6802 | 6022.378 | 4835.6904 | 0 | 0 | 0 | -1421.1313 | 0 | 1992.5351 | 8760 | 2763.5617 | 0 | 0 | 2762.9066 | 5474.3465 | 0 | 15089.9708 | 6817.9228 | 0 | 1630.9566 | 8760 | 19091.5155 | 752.875 | 0 | 1446.5 | 970587.7001 | 186766.0544 | 49.35 | 710.25
267 | E | SOR | TOU | CC | ET | HC | R100 | 2.4656 | 31 | 2.3 | 8760 | 171515.5808 | 134443.8 | 153526.0206 | 65533.1035 | 168695.8939 | 35467.5 | 99309 | 49654.5 | 3192.075 | 210020.6405 | 8760 | 1482.4089 | 14175.6585 | 1011.8356 | 12799.0533 | 0 | 0 | 0 | -1296.7186 | 0 | 2736.8865 | 8760 | 1789.397 | 0 | 0 | 1788.9385 | 15720.4739 | 4062.394 | 4939.6794 | 3636.0129 | 1256.3885 | 12177.1661 | 8760 | 0 | 354.675 | 0 | 850.5 | 577762.4795 | 210834.9497 | 658.825 | -581.2394
268 | E | SOR | TOU | CC | ET | HC | R100 | 2.4656 | 26.5 | 2 | 8760 | 170097.6741 | 143325.45 | 158459.9417 | 65533.1035 | 168695.8939 | 35652.5 | 99827 | 49913.5 | 3208.725 | 211111.7086 | 8760 | 1482.4089 | 13114.8292 | 1240.9324 | 13635.549 | 0 | 0 | 0 | -1270.0351 | 0 | 2713.0723 | 8760 | 1788.9757 | 0 | 0 | 1788.9385 | 15720.4739 | 4053.8086 | 4933.9149 | 3621.4314 | 1255.5925 | 11177.8319 | 8760 | 0 | 356.525 | 0 | 850.5 | 577763.6606 | 210834.9497 | 554.7 | -580.3174
269 | E | SOR | TOU | CC | ET | HC | R100 | 2.4656 | 21.5 | 1.6 | 8760 | 169106.3986 | 153655.65 | 164198.5591 | 65533.1035 | 168695.8939 | 35960 | 100688 | 50344 | 3236.4 | 212945.8371 | 8760 | 1482.4089 | 11695.1155 | 1599.8344 | 14591.7972 | 0 | 0 | 0 | -1228.6009 | 0 | 2665.9422 | 8760 | 1789.2904 | 0 | 0 | 1788.9385 | 15720.4739 | 4033.3646 | 4934.6267 | 3598.3155 | 1254.2279 | 9856.1709 | 8760 | 0 | 359.6 | 0 | 850.5 | 577753.4721 | 210834.9497 | 428.075 | -575.0483
270 | E | SOR | TOU | CC | ET | HC | R100 | 2.4656 | 17 | 1.3 | 8760 | 168734.341 | 165726 | 170903.862 | 65533.1035 | 168695.8939 | 36317.5 | 101689 | 50844.5 | 3268.575 | 215067.0937 | 8760 | 1482.4089 | 10142.6963 | 2053.7386 | 15566.9548 | 0 | 0 | 0 | -1181.2064 | 0 | 2592.8085 | 8760 | 1789.6518 | 0 | 0 | 1788.9385 | 15720.4739 | 4007.0307 | 4935.3064 | 3578.4085 | 1251.5752 | 8428.6857 | 8760 | 0 | 363.175 | 0 | 850.5 | 577753.9955 | 210834.9497 | 303.8 | -571.7368
271 | E | SOR | TOU | CC | ET | HC | R100 | 2.4656 | 12.5 | 0.95 | 8760 | 169852.0151 | 179706.6 | 178670.3442 | 65533.1035 | 168695.8939 | 36500 | 102200 | 51100 | 3285 | 216144.932 | 8760 | 1482.4089 | 8274.44 | 2602.913 | 16670.0253 | 0 | 0 | 0 | -1131.4229 | 0 | 2489.8961 | 8760 | 1788.1497 | 0 | 0 | 1788.9385 | 15720.4739 | 3982.2377 | 4929.3939 | 3563.4561 | 1246.306 | 6726.1104 | 8760 | 0 | 365 | 0 | 850.5 | 577753.6697 | 210834.9497 | 165.4 | -571.3413
272 | E | SOR | TOU | CC | ET | HC | R100 | 2.4656 | 31 | 1.55 | 8760 | 167855.4712 | 134010.45 | 153285.2867 | 65533.1035 | 168695.8939 | 35520 | 99456 | 49728 | 3196.8 | 210341.2715 | 8760 | 1482.4089 | 13772.7158 | 1125.377 | 13257.0087 | 0 | 0 | 0 | -1305.0207 | 0 | 2778.3763 | 8760 | 1789.3914 | 0 | 0 | 1788.9385 | 15720.4739 | 4066.2845 | 4949.1827 | 3633.3919 | 1255.7844 | 11730.0622 | 8760 | 0 | 355.2 | 0 | 850.5 | 577783.0824 | 210834.9497 | 691.575 | -581.5262
273 | E | SOR | TOU | CC | ET | HC | R100 | 2.4656 | 26.5 | 1.35 | 8760 | 166827.1437 | 142985.25 | 158270.9543 | 65533.1035 | 168695.8939 | 35710 | 99988 | 49994 | 3213.9 | 211457.8836 | 8760 | 1482.4089 | 12767.0544 | 1347.0615 | 13943.0378 | 0 | 0 | 0 | -1281.1987 | 0 | 2755.7574 | 8760 | 1788.7107 | 0 | 0 | 1788.9385 | 15720.4739 | 4054.7206 | 4933.9582 | 3616.3966 | 1254.6731 | 10783.5741 | 8760 | 0 | 357.1 | 0 | 850.5 | 577776.7805 | 210834.9497 | 587.95 | -579.3578
274 | E | SOR | TOU | CC | ET | HC | R100 | 2.4656 | 21.5 | 1.1 | 8760 | 165749.4253 | 154938.15 | 164911.0116 | 65533.1035 | 168695.8939 | 36000 | 100800 | 50400 | 3240 | 213179.7867 | 8760 | 1482.4089 | 11376.4914 | 1689.7108 | 14850.6934 | 0 | 0 | 0 | -1247.2051 | 0 | 2714.037 | 8760 | 1788.9481 | 0 | 0 | 1788.9385 | 15720.4739 | 4033.7676 | 4931.8933 | 3596.1377 | 1252.8442 | 9487.825 | 8760 | 0 | 360 | 0 | 850.5 | 577762.996 | 210834.9497 | 465.375 | -573.5049
275 | E | SOR | TOU | CC | ET | HC | R100 | 2.4656 | 17 | 0.85 | 8760 | 165384.8954 | 167456.7 | 171865.2979 | 65533.1035 | 168695.8939 | 36252.5 | 101507 | 50753.5 | 3262.725 | 214679.4072 | 8760 | 1482.4089 | 9852.4742 | 2160.9718 | 15821.4227 | 0 | 0 | 0 | -1219.4853 | 0 | 2664.069 | 8760 | 1789.457 | 0 | 0 | 1788.9385 | 15720.4739 | 4013.2606 | 4931.5689 | 3581.1118 | 1249.1044 | 8066.1414 | 8760 | 0 | 362.525 | 0 | 850.5 | 577759.8678 | 210834.9497 | 345.35 | -573.6674
276 | E | SOR | TOU | CC | ET | HC | R10 | 2.4656 | 12.5 | 0.65 | 8760 | 166799.386 | 181182.15 | 179490.0396 | 65533.1035 | 168695.8939 | 36497.5 | 102193 | 51096.5 | 3284.775 | 216119.0565 | 8760 | 1482.4089 | 8045.1791 | 2724.0316 | 16953.8239 | 0 | 0 | 0 | -1182.5152 | 0 | 2574.475 | 8760 | 1788.3072 | 0 | 0 | 1788.9385 | 15720.4739 | 3982.8914 | 4921.5769 | 3565.1509 | 1242.4824 | 6412.2855 | 8760 | 0 | 364.975 | 0 | 850.5 | 577743.795 | 210834.9497 | 200.65 | -572.882
277 | E | SOR | TOU | CC | ET | HC | R10 | 2.4656 | 31 | 0.8 | 8760 | 158915.1558 | 142113.15 | 157786.4866 | 65533.1035 | 168695.8939 | 35440 | 99232 | 49616 | 3189.6 | 209890.1543 | 8760 | 1482.4089 | 12804.6561 | 1378.2131 | 14090.8502 | 0 | 0 | 0 | -1324.4592 | 0 | 2875.5608 | 8760 | 1789.2014 | 0 | 0 | 1788.9385 | 15720.4739 | 4053.6092 | 4962.2888 | 3637.3642 | 1253.6197 | 10671.945 | 8760 | 0 | 354.4 | 0 | 850.5 | 577768.7269 | 210834.9497 | 776.45 | -582.4313
278 | E | SOR | TOU | CC | ET | HC | R10 | 2.4656 | 26.5 | 0.65 | 8760 | 155763.5163 | 152194.95 | 163387.1132 | 65533.1035 | 168695.8939 | 35657.5 | 99841 | 49920.5 | 3209.175 | 211151.9542 | 8760 | 1482.4089 | 11659.7453 | 1642.1917 | 14954.0822 | 0 | 0 | 0 | -1314.8822 | 0 | 2876.2653 | 8760 | 1788.8043 | 0 | 0 | 1788.9385 | 15720.4739 | 4036.7653 | 4945.0615 | 3623.7417 | 1251.1757 | 9563.9516 | 8760 | 0 | 356.575 | 0 | 850.5 | 577750.5198 | 210834.9497 | 698.05 | -582.7801
279 | E | SOR | TOU | CC | ET | HC | R10 | 2.4656 | 21.5 | 0.55 | 8760 | 155044.3591 | 164632.5 | 170296.4025 | 65533.1035 | 168695.8939 | 35885 | 100478 | 50239 | 3229.65 | 212502.6137 | 8760 | 1482.4089 | 10369.3786 | 1966.0515 | 15904.5663 | 0 | 0 | 0 | -1304.3035 | 0 | 2863.9494 | 8760 | 1788.9683 | 0 | 0 | 1788.9385 | 15720.4739 | 4019.6337 | 4943.1341 | 3606.112 | 1247.1323 | 8336.2899 | 8760 | 0 | 358.85 | 0 | 850.5 | 577752.0462 | 210834.9497 | 578.725 | -576.5484
280 | E | SOR | TOU | CC | ET | HC | R10 | 2.4656 | 17 | 0.45 | 8760 | 154943.1244 | 177577.65 | 177487.6731 | 65533.1035 | 168695.8939 | 36090 | 101052 | 50526 | 3248.1 | 213730.5064 | 8760 | 1482.4089 | 9017.4534 | 2427.6148 | 16772.9843 | 0 | 0 | 0 | -1319.4665 | 0 | 2776.9795 | 8760 | 1788.5948 | 0 | 0 | 1788.9385 | 15720.4739 | 4001.5431 | 4943.851 | 3587.9805 | 1241.0185 | 7120.4218 | 8760 | 0 | 360.9 | 0 | 850.5 | 577755.0451 | 210834.9497 | 462.05 | -573.2581
281 | E | SOR | TOU | CC | ET | HC | R10 | 2.4656 | 12.5 | 0.3 | 8760 | 152023.9264 | 196082.1 | 187767.2377 | 65533.1035 | 168695.8939 | 36302.5 | 101647 | 50823.5 | 3267.225 | 214974.7244 | 8760 | 1482.4089 | 7005.6905 | 3128.7788 | 18398.0392 | 0 | 0 | 0 | -1375.7121 | 0 | 2824.7501 | 8760 | 1789.1443 | 0 | 0 | 1788.9385 | 15720.4739 | 3965.6092 | 4945.1833 | 3580.5203 | 1228.7927 | 5123.5951 | 8760 | 0 | 363.025 | 0 | 850.5 | 577735.5589 | 210834.9497 | 362.4 | -571.1508
282 | E | SOR | TOU | CC | ET | HC | R600 | 2.9038 | 31 | 2.3 | 8760 | 171256.2811 | 110997 | 140500.889 | 65533.1035 | 119230.8118 | 45297.5 | 126833 | 63416.5 | 4076.775 | 268901.9383 | 8760 | 1475.3019 | 13858.8587 | 1389.8256 | 8086.3629 | 0 | 0 | 0 | -1365.786 | 0 | 2716.4952 | 8760 | 2322.0573 | 0 | 0 | 2321.0821 | 9757.4188 | 4664.7885 | 6745.2209 | 4658.6872 | 1461.7748 | 11782.1714 | 8760 | 0 | 452.975 | 0 | 1048.625 | 739584.9577 | 189624.8638 | 659.55 | -607.4734
283 | E | SOR | TOU | CC | ET | HC | R600 | 2.9038 | 26.5 | 2 | 8760 | 169886.3696 | 118947.15 | 144917.3446 | 65533.1035 | 119230.8118 | 45660 | 127848 | 63924 | 4109.4 | 271045.6564 | 8760 | 1475.3019 | 12855.5444 | 1722.5775 | 8695.6423 | 0 | 0 | 0 | -1336.1285 | 0 | 2694.5086 | 8760 | 2321.7685 | 0 | 0 | 2321.0821 | 9757.4188 | 4648.9493 | 6743.5486 | 4634.7294 | 1459.3482 | 10839.05 | 8760 | 0 | 456.6 | 0 | 1048.625 | 739570.918 | 189624.8638 | 553.75 | -599.0094
284 | E | SOR | TOU | CC | ET | HC | R600 | 2.9038 | 21.5 | 1.6 | 8760 | 168963.5564 | 130612.5 | 151397.6625 | 65533.1035 | 119230.8118 | 46025 | 128870 | 64435 | 4142.25 | 273202.1575 | 8760 | 1475.3019 | 11471.4212 | 2249.2579 | 9507.5757 | 0 | 0 | 0 | -1302.7537 | 0 | 2657.7108 | 8760 | 2321.0523 | 0 | 0 | 2321.0821 | 9757.4188 | 4631.3954 | 6725.7033 | 4608.9433 | 1455.4105 | 9545.5205 | 8760 | 0 | 460.25 | 0 | 1048.625 | 739568.2281 | 189624.8638 | 427.475 | -598.4017
285 | E | SOR | TOU | CC | ET | HC | R600 | 2.9038 | 17 | 1.3 | 8760 | 169853.9595 | 142136.1 | 157799.2357 | 65533.1035 | 119230.8118 | 46312.5 | 129675 | 64837.5 | 4168.125 | 274907.3032 | 8760 | 1475.3019 | 10039.0191 | 2837.7527 | 10215.7414 | 0 | 0 | 0 | -1261.9055 | 0 | 2591.2823 | 8760 | 2321.369 | 0 | 0 | 2321.0821 | 9757.4188 | 4607.9165 | 6734.6966 | 4595.0995 | 1451.3576 | 8233.9116 | 8760 | 0 | 463.125 | 0 | 1048.625 | 739560.1278 | 189624.8638 | 291.375 | -596.3355
286 | E | SOR | TOU | CC | ET | HC | R600 | 2.9038 | 12.5 | 0.95 | 8760 | 171112.7128 | 156035.7 | 165520.7209 | 65533.1035 | 119230.8118 | 46585 | 130438 | 65219 | 4192.65 | 276536.67 | 8760 | 1475.3019 | 8231.5116 | 3580.2256 | 10975.4972 | 0 | 0 | 0 | -1194.2952 | 0 | 2462.0144 | 8760 | 2321.0735 | 0 | 0 | 2321.0821 | 9757.4188 | 4555.4318 | 6741.5705 | 4576.4009 | 1439.5517 | 6620.8242 | 8760 | 0 | 465.85 | 0 | 1048.625 | 739561.0983 | 189624.8638 | 153.475 | -592.4835
287 | E | SOR | TOU | CC | ET | HC | R600 | 2.9038 | 31 | 1.55 | 8760 | 167250.6814 | 112460.4 | 141313.8348 | 65533.1035 | 119230.8118 | 45340 | 126952 | 63476 | 4080.6 | 269159.0385 | 8760 | 1475.3019 | 13441.9076 | 1579.3974 | 8520.1794 | 0 | 0 | 0 | -1373.5051 | 0 | 2753.2574 | 8760 | 2321.6842 | 0 | 0 | 2321.0821 | 9757.4188 | 4665.2714 | 6749.2676 | 4656.9738 | 1460.3362 | 11323.9476 | 8760 | 0 | 453.4 | 0 | 1048.625 | 739575.6994 | 189624.8638 | 696.775 | -609.0713
288 | E | SOR | TOU | CC | ET | HC | R600 | 2.9038 | 26.5 | 1.35 | 8760 | 166092.1335 | 120826.35 | 145961.275 | 65533.1035 | 119230.8118 | 45675 | 127890 | 63945 | 4110.75 | 271125.6435 | 8760 | 1475.3019 | 12472.9256 | 1879.3909 | 9088.7624 | 0 | 0 | 0 | -1348.8309 | 0 | 2733.7594 | 8760 | 2321.5505 | 0 | 0 | 2321.0821 | 9757.4188 | 4650.1967 | 6740.67 | 4637.2388 | 1457.1767 | 10413.7676 | 8760 | 0 | 456.75 | 0 | 1048.625 | 739575.0012 | 189624.8638 | 593.825 | -602.6711
289 | E | SOR | TOU | CC | ET | HC | R600 | 2.9038 | 21.5 | 1.1 | 8760 | 165658.4753 | 131988.15 | 152161.8616 | 65533.1035 | 119230.8118 | 45930 | 128604 | 64302 | 4133.7 | 272644.5156 | 8760 | 1475.3019 | 11171.7953 | 2386.9591 | 9768.5513 | 0 | 0 | 0 | -1318.1899 | 0 | 2698.5691 | 8760 | 2320.3725 | 0 | 0 | 2321.0821 | 9757.4188 | 4631.5827 | 6731.7353 | 4613.4176 | 1452.6867 | 9200.5816 | 8760 | 0 | 459.3 | 0 | 1048.625 | 739556.4723 | 189624.8638 | 464.55 | -597.635
290 | E | SOR | TOU | CC | ET | HC | R600 | 2.9038 | 17 | 0.85 | 8760 | 166451.7712 | 143764.2 | 158703.6754 | 65533.1035 | 119230.8118 | 46255 | 129514 | 64757 | 4162.95 | 274572.3815 | 8760 | 1475.3019 | 9769.9773 | 2980.1801 | 10418.14 | 0 | 0 | 0 | -1284.6524 | 0 | 2642.087 | 8760 | 2321.1607 | 0 | 0 | 2321.0821 | 9757.4188 | 4605.6059 | 6737.8056 | 4596.8333 | 1447.4618 | 7912.1141 | 8760 | 0 | 462.55 | 0 | 1048.625 | 739565.512 | 189624.8638 | 332.75 | -596.0851
291 | E | SOR | TOU | CC | ET | HC | R60 | 2.9038 | 12.5 | 0.65 | 8760 | 168177.5573 | 157272.3 | 166207.6751 | 65533.1035 | 119230.8118 | 46532.5 | 130291 | 65145.5 | 4187.925 | 276226.5761 | 8760 | 1475.3019 | 8024.2456 | 3699.0558 | 11202.7157 | 0 | 0 | 0 | -1231.1255 | 0 | 2535.2921 | 8760 | 2320.794 | 0 | 0 | 2321.0821 | 9757.4188 | 4550.0918 | 6741.8665 | 4578.5021 | 1434.8967 | 6340.7726 | 8760 | 0 | 465.325 | 0 | 1048.625 | 739537.1153 | 189624.8638 | 186.5 | -589.3955
292 | E | SOR | TOU | CC | ET | HC | R60 | 2.9038 | 31 | 0.8 | 8760 | 158518.0112 | 119184.75 | 145049.3358 | 65533.1035 | 119230.8118 | 45230 | 126644 | 63322 | 4070.7 | 268508.7579 | 8760 | 1475.3019 | 12490.6303 | 1992.6291 | 9171.0736 | 0 | 0 | 0 | -1390.5817 | 0 | 2841.7878 | 8760 | 2321.0134 | 0 | 0 | 2321.0821 | 9757.4188 | 4656.2919 | 6763.7795 | 4667.9258 | 1454.3697 | 10296.4665 | 8760 | 0 | 452.3 | 0 | 1048.625 | 739585.2031 | 189624.8638 | 775.875 | -611.5308
293 | E | SOR | TOU | CC | ET | HC | R60 | 2.9038 | 26.5 | 0.65 | 8760 | 156278.4924 | 128683.35 | 150325.984 | 65533.1035 | 119230.8118 | 45452.5 | 127267 | 63633.5 | 4090.725 | 269840.2314 | 8760 | 1475.3019 | 11487.5471 | 2316.7279 | 9775.19 | 0 | 0 | 0 | -1375.089 | 0 | 2838.3729 | 8760 | 2321.9666 | 0 | 0 | 2321.0821 | 9757.4188 | 4634.1449 | 6766.7603 | 4651.5383 | 1449.3288 | 9335.3861 | 8760 | 0 | 454.525 | 0 | 1048.625 | 739581.2913 | 189624.8638 | 691.85 | -607.1586
294 | E | SOR | TOU | CC | ET | HC | R60 | 2.9038 | 21.5 | 0.55 | 8760 | 155978.5385 | 140759.1 | 157034.2867 | 65533.1035 | 119230.8118 | 45750 | 128100 | 64050 | 4117.5 | 271607.5649 | 8760 | 1475.3019 | 10293.9686 | 2757.3695 | 10446.6445 | 0 | 0 | 0 | -1356.7579 | 0 | 2819.9912 | 8760 | 2321.2804 | 0 | 0 | 2321.0821 | 9757.4188 | 4607.5202 | 6767.1768 | 4628.3546 | 1442.832 | 8213.1412 | 8760 | 0 | 457.5 | 0 | 1048.625 | 739560.0461 | 189624.8638 | 570.25 | -602.968
295 | E | SOR | TOU | CC | ET | HC | R60 | 2.9038 | 17 | 0.45 | 8760 | 156849.8722 | 152431.2 | 163518.3544 | 65533.1035 | 119230.8118 | 46087.5 | 129045 | 64522.5 | 4147.875 | 273589.0614 | 8760 | 1475.3019 | 9033.9735 | 3305.9619 | 11011.9055 | 0 | 0 | 0 | -1359.3159 | 0 | 2732.4921 | 8760 | 2321.7226 | 0 | 0 | 2321.0821 | 9757.4188 | 4572.727 | 6751.1152 | 4609.2614 | 1434.7956 | 7095.4521 | 8760 | 0 | 460.875 | 0 | 1048.625 | 739563.1439 | 189624.8638 | 442.2 | -600.0189
296 | E | SOR | TOU | CC | ET | HC | R60 | 2.9038 | 12.5 | 0.3 | 8760 | 153718.5167 | 170672.4 | 173651.6788 | 65533.1035 | 119230.8118 | 46262.5 | 129535 | 64767.5 | 4163.625 | 274638.7107 | 8760 | 1475.3019 | 7022.1443 | 4160.0579 | 12440.7247 | 0 | 0 | 0 | -1399.5565 | 0 | 2783.2431 | 8760 | 2320.4792 | 0 | 0 | 2321.0821 | 9757.4188 | 4510.9841 | 6759.9484 | 4593.5256 | 1417.5282 | 5096.2459 | 8760 | 0 | 462.625 | 0 | 1048.625 | 739538.9453 | 189624.8638 | 343.725 | -596.9749
297 | E | SOR | TOU | CC | ET | WC | R100 | 3.4612 | 43.5 | 3.25 | 8760 | 195847.1104 | 135554.85 | 154143.2295 | 65533.1035 | 200991.9069 | 41372.5 | 142735.125 | 57921.5 | 3723.525 | 19134.7812 | 8760 | 1482.4089 | 18487.3543 | 1059.3732 | 17215.5404 | 0 | 0 | 0 | -1302.2828 | 0 | 2709.4596 | 8760 | 2511.6502 | 0 | 0 | 2511.3333 | 22068.5897 | 5293.0347 | 8423.2817 | 4750.2399 | 1667.9013 | 16452.9983 | 8760 | 10676.0214 | 413.725 | 0 | 850.5 | 819543.9142 | 210834.9497 | 779.25
298 | E | SOR | TOU | CC | ET | WC | R100 | 3.4612 | 37 | 2.8 | 8760 | 189405.8863 | 144555.3 | 159143.1461 | 65533.1035 | 200991.9069 | 41552.5 | 143356.125 | 58173.5 | 3739.725 | 19218.0312 | 8760 | 1482.4089 | 17102.6647 | 1341.0585 | 18411.2827 | 0 | 0 | 0 | -1276.2952 | 0 | 2708.5452 | 8760 | 2509.6503 | 0 | 0 | 2511.3333 | 22068.5897 | 5278.1391 | 8430.2866 | 4728.1812 | 1665.3653 | 15108.8173 | 8760 | 10685.1169 | 415.525 | 0 | 850.5 | 819513.3978 | 210834.9497 | 661.55
299 | E | SOR | TOU | CC | ET | WC | R100 | 3.4612 | 30.5 | 2.3 | 8760 | 184094.9205 | 154373.85 | 164597.5324 | 65533.1035 | 200991.9069 | 41802.5 | 144218.625 | 58523.5 | 3762.225 | 19333.6562 | 8760 | 1482.4089 | 15467.9623 | 1757.7996 | 19610.4127 | 0 | 0 | 0 | -1240.712 | 0 | 2680.9071 | 8760 | 2509.6332 | 0 | 0 | 2511.3333 | 22068.5897 | 5251.0541 | 8433.1724 | 4705.3554 | 1661.7742 | 13550.224 | 8760 | 10704.1074 | 418.025 | 0 | 850.5 | 819488.0967 | 210834.9497 | 536.025
300 | E | SOR | TOU | CC | ET | WC | R100 | 3.4612 | 24 | 1.8 | 8760 | 179244.8943 | 166841.1 | 171523.3207 | 65533.1035 | 200991.9069 | 42217.5 | 145650.375 | 59104.5 | 3799.575 | 19525.5938 | 8760 | 1482.4089 | 13442.2939 | 2259.8054 | 20964.4478 | 0 | 0 | 0 | -1191.47 | 0 | 2621.9129 | 8760 | 2509.7011 | 0 | 0 | 2511.3333 | 22068.5897 | 5205.8898 | 8459.1191 | 4673.2238 | 1654.4881 | 11641.5345 | 8760 | 10749.4568 | 422.175 | 0 | 850.5 | 819481.8573 | 210834.9497 | 401.125
301 | E | SOR | TOU | CC | ET | WC | R100 | 3.4612 | 17.5 | 1.3 | 8760 | 176025.1682 | 182564.55 | 180257.9884 | 65533.1035 | 200991.9069 | 42537.5 | 146754.375 | 59552.5 | 3828.375 | 19673.5938 | 8760 | 1482.4089 | 10953.3339 | 2982.2811 | 22481.7865 | 0 | 0 | 0 | -1138.7808 | 0 | 2540.665 | 8760 | 2509.3853 | 0 | 0 | 2511.3333 | 22068.5897 | 5164.9202 | 8486.7586 | 4649.3444 | 1645.6418 | 9303.9205 | 8760 | 10783.9469 | 425.375 | 0 | 850.5 | 819447.8919 | 210834.9497 | 248.65
302 | E | SOR | TOU | CC | ET | WC | R100 | 3.4612 | 43.5 | 2.2 | 8760 | 191700.2712 | 135357.75 | 154033.7368 | 65533.1035 | 200991.9069 | 41470 | 143071.5 | 58058 | 3732.3 | 19179.875 | 8760 | 1482.4089 | 17963.765 | 1189.6737 | 17947.2759 | 0 | 0 | 0 | -1307.9522 | 0 | 2747.2653 | 8760 | 2511.8175 | 0 | 0 | 2511.3333 | 22068.5897 | 5297.5995 | 8435.6933 | 4745.5737 | 1665.5395 | 15888.0019 | 8760 | 10688.0099 | 414.7 | 0 | 850.5 | 819548.6203 | 210834.9497 | 810.85
303 | E | SOR | TOU | CC | ET | WC | R100 | 3.4612 | 37 | 1.85 | 8760 | 185035.6976 | 143896.5 | 158777.1705 | 65533.1035 | 200991.9069 | 41675 | 143778.75 | 58345 | 3750.75 | 19274.6875 | 8760 | 1482.4089 | 16600.8392 | 1487.2936 | 18928.6593 | 0 | 0 | 0 | -1283.1948 | 0 | 2741.9357 | 8760 | 2510.3875 | 0 | 0 | 2511.3333 | 22068.5897 | 5279.0483 | 8438.1242 | 4723.6946 | 1662.8697 | 14568.1143 | 8760 | 10695.4807 | 416.75 | 0 | 850.5 | 819506.9668 | 210834.9497 | 703.325
304 | E | SOR | TOU | CC | ET | WC | R100 | 3.4612 | 30.5 | 1.55 | 8760 | 180008.174 | 154861.2 | 164868.2644 | 65533.1035 | 200991.9069 | 41935 | 144675.75 | 58709 | 3774.15 | 19394.9375 | 8760 | 1482.4089 | 15028.3032 | 1862.2669 | 19997.017 | 0 | 0 | 0 | -1251.1458 | 0 | 2719.4351 | 8760 | 2509.6928 | 0 | 0 | 2511.3333 | 22068.5897 | 5248.1157 | 8448.7141 | 4697.6532 | 1658.7738 | 13068.8619 | 8760 | 10718.7389 | 419.35 | 0 | 850.5 | 819485.013 | 210834.9497 | 573.725
305 | E | SOR | TOU | CC | ET | WC | R100 | 3.4612 | 24 | 1.2 | 8760 | 175245.3384 | 168628.5 | 172516.2545 | 65533.1035 | 200991.9069 | 42227.5 | 145684.875 | 59118.5 | 3800.475 | 19530.2188 | 8760 | 1482.4089 | 13031.589 | 2408.6244 | 21246.1252 | 0 | 0 | 0 | -1215.7741 | 0 | 2680.3547 | 8760 | 2509.7569 | 0 | 0 | 2511.3333 | 22068.5897 | 5212.6606 | 8465.8838 | 4673.3363 | 1651.1561 | 11170.0895 | 8760 | 10751.8443 | 422.275 | 0 | 850.5 | 819493.8348 | 210834.9497 | 444.825
306 | E | SOR | TOU | CC | ET | WC | R10 | 3.4612 | 17.5 | 0.9 | 8760 | 172998.2227 | 183481.2 | 180767.2044 | 65533.1035 | 200991.9069 | 42565 | 146849.25 | 59591 | 3830.85 | 19686.3125 | 8760 | 1482.4089 | 10681.614 | 3105.1901 | 22785.2633 | 0 | 0 | 0 | -1172.7318 | 0 | 2604.1745 | 8760 | 2510.3462 | 0 | 0 | 2511.3333 | 22068.5897 | 5167.6134 | 8497.8894 | 4650.5574 | 1640.4987 | 8966.9073 | 8760 | 10793.6356 | 425.65 | 0 | 850.5 | 819450.3119 | 210834.9497 | 283.275
307 | E | SOR | TOU | CC | ET | WC | R10 | 3.4612 | 43.5 | 1.1 | 8760 | 180933.0717 | 141974.1 | 157709.2417 | 65533.1035 | 200991.9069 | 41512.5 | 143218.125 | 58117.5 | 3736.125 | 19199.5312 | 8760 | 1482.4089 | 16630.6376 | 1531.2467 | 19119.8738 | 0 | 0 | 0 | -1312.2457 | 0 | 2828.272 | 8760 | 2510.9374 | 0 | 0 | 2511.3333 | 22068.5897 | 5277.6729 | 8450.3852 | 4745.9751 | 1659.7685 | 14480.5929 | 8760 | 10698.8286 | 415.125 | 0 | 850.5 | 819553.8167 | 210834.9497 | 890.575
308 | E | SOR | TOU | CC | ET | WC | R10 | 3.4612 | 37 | 0.95 | 8760 | 174518.5526 | 150839.55 | 162634.1634 | 65533.1035 | 200991.9069 | 41677.5 | 143787.375 | 58348.5 | 3750.975 | 19275.8438 | 8760 | 1482.4089 | 15369.1823 | 1807.1377 | 20033.4533 | 0 | 0 | 0 | -1294.9663 | 0 | 2833.7985 | 8760 | 2510.0099 | 0 | 0 | 2511.3333 | 22068.5897 | 5255.5087 | 8451.3783 | 4727.4942 | 1656.126 | 13252.9115 | 8760 | 10710.7668 | 416.775 | 0 | 850.5 | 819519.2113 | 210834.9497 | 790.15
309 | E | SOR | TOU | CC | ET | WC | R10 | 3.4612 | 30.5 | 0.75 | 8760 | 167906.6918 | 162758.7 | 169255.4719 | 65533.1035 | 200991.9069 | 41915 | 144606.75 | 58681 | 3772.35 | 19385.6875 | 8760 | 1482.4089 | 13703.6755 | 2193.8707 | 21231.0305 | 0 | 0 | 0 | -1279.495 | 0 | 2832.6655 | 8760 | 2510.0748 | 0 | 0 | 2511.3333 | 22068.5897 | 5223.9901 | 8455.9678 | 4703.63 | 1649.1882 | 11637.9991 | 8760 | 10721.0751 | 419.15 | 0 | 850.5 | 819481.5097 | 210834.9497 | 688.975
310 | E | SOR | TOU | CC | ET | WC | R10 | 3.4612 | 24 | 0.6 | 8760 | 163290.3377 | 177476.4 | 177431.4268 | 65533.1035 | 200991.9069 | 42182.5 | 145529.625 | 59055.5 | 3796.425 | 19509.4062 | 8760 | 1482.4089 | 11815.9375 | 2728.4713 | 22648.0407 | 0 | 0 | 0 | -1265.2749 | 0 | 2833.8228 | 8760 | 2510.7395 | 0 | 0 | 2511.3333 | 22068.5897 | 5190.0512 | 8472.1629 | 4682.1623 | 1637.4447 | 9808.634 | 8760 | 10752.1568 | 421.825 | 0 | 850.5 | 819488.1754 | 210834.9497 | 564.9
311 | E | SOR | TOU | CC | ET | WC | R10 | 3.4612 | 17.5 | 0.45 | 8760 | 160239.19 | 193199.85 | 186166.0944 | 65533.1035 | 200991.9069 | 42442.5 | 146426.625 | 59419.5 | 3819.825 | 19629.6562 | 8760 | 1482.4089 | 9631.7327 | 3524.5372 | 23908.8068 | 0 | 0 | 0 | -1280.4024 | 0 | 2739.9742 | 8760 | 2509.3968 | 0 | 0 | 2511.3333 | 22068.5897 | 5143.9518 | 8482.1624 | 4657.0569 | 1621.387 | 7784.7753 | 8760 | 10775.2778 | 424.425 | 0 | 850.5 | 819466.146 | 210834.9497 | 420.625
312 | E | SOR | TOU | CC | ET | WC | R600 | 4.0765 | 43.5 | 3.25 | 8760 | 194865.271 | 111865.05 | 140983.1069 | 65533.1035 | 139231.0069 | 53802.5 | 185618.625 | 75323.5 | 4842.225 | 24883.6562 | 8760 | 1475.3019 | 17938.1193 | 1485.5943 | 10730.1267 | 0 | 0 | 0 | -1378.3319 | 0 | 2699.6215 | 8760 | 3257.752 | 0 | 0 | 3258.3629 | 13697.5815 | 6009.3423 | 11228.9379 | 6141.0125 | 1903.1443 | 15814.8524 | 8760 | 13997.2316 | 538.025 | 0 | 1048.625 | 1049020.9532 | 189624.8638 | 786.5
313 | E | SOR | TOU | CC | ET | WC | R600 | 4.0765 | 37 | 2.8 | 8760 | 188345.4009 | 120807.45 | 145950.7757 | 65533.1035 | 139231.0069 | 54160 | 186852 | 75824 | 4874.4 | 25049 | 8760 | 1475.3019 | 16635.5972 | 1883.9401 | 11612.8745 | 0 | 0 | 0 | -1347.6212 | 0 | 2692.147 | 8760 | 3257.8751 | 0 | 0 | 3258.3629 | 13697.5815 | 5981.8385 | 11250.2086 | 6112.9176 | 1898.6794 | 14557.6302 | 8760 | 14029.8063 | 541.6 | 0 | 1048.625 | 1048984.1896 | 189624.8638 | 671.775
314 | E | SOR | TOU | CC | ET | WC | R600 | 4.0765 | 30.5 | 2.3 | 8760 | 182849.6915 | 132170.4 | 152263.1048 | 65533.1035 | 139231.0069 | 54597.5 | 188361.375 | 76436.5 | 4913.775 | 25251.3438 | 8760 | 1475.3019 | 15049.5489 | 2471.4474 | 12591.4248 | 0 | 0 | 0 | -1315.6229 | 0 | 2669.4529 | 8760 | 3256.3706 | 0 | 0 | 3258.3629 | 13697.5815 | 5955.7721 | 11276.7019 | 6073.5861 | 1890.9277 | 13043.9171 | 8760 | 14073.5955 | 545.975 | 0 | 1048.625 | 1048933.4719 | 189624.8638 | 547.325
315 | E | SOR | TOU | CC | ET | WC | R600 | 4.0765 | 24 | 1.8 | 8760 | 178668.2379 | 146149.65 | 160028.8371 | 65533.1035 | 139231.0069 | 54990 | 189715.5 | 76986 | 4949.1 | 25432.875 | 8760 | 1475.3019 | 13127.4201 | 3249.1465 | 13642.5968 | 0 | 0 | 0 | -1277.0516 | 0 | 2629.1539 | 8760 | 3257.5099 | 0 | 0 | 3258.3629 | 13697.5815 | 5923.7369 | 11313.2372 | 6046.9582 | 1883.2742 | 11223.0961 | 8760 | 14127.656 | 549.9 | 0 | 1048.625 | 1048930.6647 | 189624.8638 | 407.425
316 | E | SOR | TOU | CC | ET | WC | R600 | 4.0765 | 17.5 | 1.3 | 8760 | 177093.4564 | 160721.55 | 168123.7974 | 65533.1035 | 139231.0069 | 55387.5 | 191086.875 | 77542.5 | 4984.875 | 25616.7188 | 8760 | 1475.3019 | 10844.629 | 4194.6083 | 14721.0069 | 0 | 0 | 0 | -1218.4727 | 0 | 2532.692 | 8760 | 3256.8493 | 0 | 0 | 3258.3629 | 13697.5815 | 5870.7925 | 11351.3726 | 6016.0824 | 1871.1299 | 9110.2091 | 8760 | 14180.6105 | 553.875 | 0 | 1048.625 | 1048916.7124 | 189624.8638 | 236.475
317 | E | SOR | TOU | CC | ET | WC | R600 | 4.0765 | 43.5 | 2.2 | 8760 | 190129.3907 | 112733.1 | 141465.3247 | 65533.1035 | 139231.0069 | 53972.5 | 186205.125 | 75561.5 | 4857.525 | 24962.2812 | 8760 | 1475.3019 | 17377.7277 | 1695.9063 | 11306.5133 | 0 | 0 | 0 | -1381.7204 | 0 | 2716.6268 | 8760 | 3258.651 | 0 | 0 | 3258.3629 | 13697.5815 | 6007.8501 | 11258.5398 | 6135.8796 | 1899.9895 | 15229.6549 | 8760 | 14027.3874 | 539.725 | 0 | 1048.625 | 1049021.1448 | 189624.8638 | 821.675
318 | E | SOR | TOU | CC | ET | WC | R600 | 4.0765 | 37 | 1.85 | 8760 | 183533.1865 | 122685.3 | 146993.9561 | 65533.1035 | 139231.0069 | 54260 | 187197 | 75964 | 4883.4 | 25095.25 | 8760 | 1475.3019 | 16083.3152 | 2119.6528 | 12163.8029 | 0 | 0 | 0 | -1356.4854 | 0 | 2725.0356 | 8760 | 3258.1636 | 0 | 0 | 3258.3629 | 13697.5815 | 5984.6743 | 11273.6566 | 6110.3871 | 1895.4915 | 13966.4231 | 8760 | 14050.5918 | 542.6 | 0 | 1048.625 | 1048996.9777 | 189624.8638 | 711.575
319 | E | SOR | TOU | CC | ET | WC | R600 | 4.0765 | 30.5 | 1.55 | 8760 | 178614.5787 | 133502.85 | 153003.3055 | 65533.1035 | 139231.0069 | 54582.5 | 188309.625 | 76415.5 | 4912.425 | 25244.4062 | 8760 | 1475.3019 | 14591.9024 | 2675.5414 | 13012.1585 | 0 | 0 | 0 | -1327.0876 | 0 | 2707.6274 | 8760 | 3256.3748 | 0 | 0 | 3258.3629 | 13697.5815 | 5958.6776 | 11282.4382 | 6076.4096 | 1888.6914 | 12542.1062 | 8760 | 14076.3744 | 545.825 | 0 | 1048.625 | 1048946.3913 | 189624.8638 | 585.625
320 | E | SOR | TOU | CC | ET | WC | R600 | 4.0765 | 24 | 1.2 | 8760 | 175182.5274 | 146264.4 | 160092.5828 | 65533.1035 | 139231.0069 | 54970 | 189646.5 | 76958 | 4947.3 | 25423.625 | 8760 | 1475.3019 | 12784.2397 | 3420.2687 | 13933.0589 | 0 | 0 | 0 | -1291.7702 | 0 | 2670.6442 | 8760 | 3258.0665 | 0 | 0 | 3258.3629 | 13697.5815 | 5924.2345 | 11321.4029 | 6050.3106 | 1879.2097 | 10832.2447 | 8760 | 14130.1879 | 549.7 | 0 | 1048.625 | 1048953.9942 | 189624.8638 | 443.075
321 | E | SOR | TOU | CC | ET | WC | R60 | 4.0765 | 17.5 | 0.9 | 8760 | 174265.7267 | 160848.45 | 168194.2927 | 65533.1035 | 139231.0069 | 55355 | 190974.75 | 77497 | 4981.95 | 25601.6875 | 8760 | 1475.3019 | 10607.1841 | 4338.4536 | 14865.8708 | 0 | 0 | 0 | -1238.4512 | 0 | 2581.3072 | 8760 | 3256.7764 | 0 | 0 | 3258.3629 | 13697.5815 | 5864.2546 | 11346.7583 | 6018.2264 | 1863.8622 | 8823.1479 | 8760 | 14171.9324 | 553.55 | 0 | 1048.625 | 1048909.4382 | 189624.8638 | 268.9
322 | E | SOR | TOU | CC | ET | WC | R60 | 4.0765 | 43.5 | 1.1 | 8760 | 178989.2721 | 120248.55 | 145640.2964 | 65533.1035 | 139231.0069 | 53972.5 | 186205.125 | 75561.5 | 4857.525 | 24962.2812 | 8760 | 1475.3019 | 16043.321 | 2265.4569 | 12261.8255 | 0 | 0 | 0 | -1387.1562 | 0 | 2801.6437 | 8760 | 3257.7107 | 0 | 0 | 3258.3629 | 13697.5815 | 5994.3095 | 11278.4504 | 6139.6833 | 1890.0243 | 13824.3354 | 8760 | 14038.4985 | 539.725 | 0 | 1048.625 | 1049021.657 | 189624.8638 | 904.275
323 | E | SOR | TOU | CC | ET | WC | R60 | 4.0765 | 37 | 0.95 | 8760 | 173516.2464 | 129354.3 | 150698.7091 | 65533.1035 | 139231.0069 | 54242.5 | 187136.625 | 75939.5 | 4881.825 | 25087.1562 | 8760 | 1475.3019 | 14920.8003 | 2618.4574 | 12926.487 | 0 | 0 | 0 | -1367.3953 | 0 | 2804.2716 | 8760 | 3258.359 | 0 | 0 | 3258.3629 | 13697.5815 | 5970.1961 | 11288.7145 | 6117.5455 | 1884.621 | 12735.4165 | 8760 | 14060.7785 | 542.425 | 0 | 1048.625 | 1048999.8232 | 189624.8638 | 794.45
324 | E | SOR | TOU | CC | ET | WC | R60 | 4.0765 | 30.5 | 0.75 | 8760 | 168153.0056 | 140448.6 | 156861.7982 | 65533.1035 | 139231.0069 | 54537.5 | 188154.375 | 76352.5 | 4908.375 | 25223.5938 | 8760 | 1475.3019 | 13466.1878 | 3123.8543 | 13794.6336 | 0 | 0 | 0 | -1345.0874 | 0 | 2800.902 | 8760 | 3258.1364 | 0 | 0 | 3258.3629 | 13697.5815 | 5931.9456 | 11297.1461 | 6090.241 | 1874.6766 | 11334.8011 | 8760 | 14084.7702 | 545.375 | 0 | 1048.625 | 1048954.194 | 189624.8638 | 684.9
325 | E | SOR | TOU | CC | ET | WC | R60 | 4.0765 | 24 | 0.6 | 8760 | 164466.1348 | 153647.55 | 164194.0594 | 65533.1035 | 139231.0069 | 54817.5 | 189120.375 | 76744.5 | 4933.575 | 25353.0938 | 8760 | 1475.3019 | 11746.5551 | 3822.7932 | 14738.2754 | 0 | 0 | 0 | -1322.8086 | 0 | 2790.1753 | 8760 | 3256.4804 | 0 | 0 | 3258.3629 | 13697.5815 | 5881.9149 | 11312.1503 | 6058.2333 | 1861.7535 | 9690.6121 | 8760 | 14110.5686 | 548.175 | 0 | 1048.625 | 1048919.2208 | 189624.8638 | 555.9
326 | E | SOR | TOU | CC | ET | WC | R60 | 4.0765 | 17.5 | 0.45 | 8760 | 162481.0726 | 169125.3 | 172792.2361 | 65533.1035 | 139231.0069 | 55212.5 | 190483.125 | 77297.5 | 4969.125 | 25535.7812 | 8760 | 1475.3019 | 9676.963 | 4776.4356 | 15622.7109 | 0 | 0 | 0 | -1321.3533 | 0 | 2691.5237 | 8760 | 3256.8187 | 0 | 0 | 3258.3629 | 13697.5815 | 5805.3543 | 11341.6151 | 6028.7538 | 1840.056 | 7791.9494 | 8760 | 14156.869 | 552.125 | 0 | 1048.625 | 1048902.248 | 189624.8638 | 399.55
327 | E | SOR | TOU | CC | FP | HC | R100 | 2.4656 | 31 | 2.3 | 8760 | 175178.3499 | 142253.55 | 157864.4814 | 65533.1035 | 168695.8939 | 35835 | 100338 | 50169 | 3225.15 | 212197.6248 | 8760 | 1482.4089 | 12829.7524 | 1409.9238 | 13323.5243 | 0 | 0 | 0 | -1253.241 | 0 | 2334.6958 | 8760 | 1789.0264 | 0 | 0 | 1788.9385 | 15720.4739 | 4046.7021 | 4958.012 | 3615.8956 | 1254.5036 | 11216.3005 | 8760 | 0 | 358.35 | 0 | 850.5 | 577768.231 | 210834.9497 | 335 | -578.7426
328 | E | SOR | TOU | CC | FP | HC | R100 | 2.4656 | 26.5 | 2 | 8760 | 171013.9342 | 150032.25 | 162185.6933 | 65533.1035 | 168695.8939 | 36015 | 100842 | 50421 | 3241.35 | 213271.8253 | 8760 | 1482.4089 | 11824.9389 | 1667.8877 | 14047.4843 | 0 | 0 | 0 | -1220.8184 | 0 | 2314.7048 | 8760 | 1789.3994 | 0 | 0 | 1788.9385 | 15720.4739 | 4032.6632 | 4958.8048 | 3602.7262 | 1253.4233 | 10266.1921 | 8760 | 0 | 360.15 | 0 | 850.5 | 577757.7284 | 210834.9497 | 276.275 | -574.7775
329 | E | SOR | TOU | CC | FP | HC | R100 | 2.4656 | 21.5 | 1.6 | 8760 | 167309.085 | 160471.8 | 167985.0566 | 65533.1035 | 168695.8939 | 36302.5 | 101647 | 50823.5 | 3267.225 | 214982.0322 | 8760 | 1482.4089 | 10501.7378 | 2025.7812 | 14992.0121 | 0 | 0 | 0 | -1179.5013 | 0 | 2292.0473 | 8760 | 1789.9426 | 0 | 0 | 1788.9385 | 15720.4739 | 4010.7365 | 4959.603 | 3584.3855 | 1250.4007 | 9016.6896 | 8760 | 0 | 363.025 | 0 | 850.5 | 577769.8174 | 210834.9497 | 210.3 | -571.7147
330 | E | SOR | TOU | CC | FP | HC | R100 | 2.4656 | 17 | 1.3 | 8760 | 165145.9689 | 171300.15 | 174000.4056 | 65533.1035 | 168695.8939 | 36452.5 | 102067 | 51033.5 | 3280.725 | 215880.7904 | 8760 | 1482.4089 | 9119.3089 | 2415.3538 | 15841.733 | 0 | 0 | 0 | -1135.3392 | 0 | 2255.2202 | 8760 | 1788.7461 | 0 | 0 | 1788.9385 | 15720.4739 | 3988.5094 | 4963.2123 | 3570.7677 | 1246.3554 | 7721.6612 | 8760 | 0 | 364.525 | 0 | 850.5 | 577739.7014 | 210834.9497 | 137.925 | -567.4631
331 | E | SOR | TOU | CC | FP | HC | R100 | 2.4656 | 12.5 | 0.95 | 8760 | 163297.5369 | 184121.1 | 181122.6807 | 65533.1035 | 168695.8939 | 36642.5 | 102599 | 51299.5 | 3297.825 | 216994.0656 | 8760 | 1482.4089 | 7435.5156 | 2892.8638 | 16864.1693 | 0 | 0 | 0 | -1082.7265 | 0 | 2193.1874 | 8760 | 1788.3736 | 0 | 0 | 1788.9385 | 15720.4739 | 3959.8209 | 4958.9655 | 3560.8316 | 1238.2789 | 6164.2578 | 8760 | 0 | 366.425 | 0 | 850.5 | 577761.7351 | 210834.9497 | 66.7 | -571.3719
332 | E | SOR | TOU | CC | FP | HC | R100 | 2.4656 | 31 | 1.55 | 8760 | 172218.8454 | 143706.15 | 158671.4276 | 65533.1035 | 168695.8939 | 35852.5 | 100387 | 50193.5 | 3226.725 | 212323.0107 | 8760 | 1482.4089 | 12295.4617 | 1536.372 | 13871.4801 | 0 | 0 | 0 | -1256.8475 | 0 | 2369.4287 | 8760 | 1789.1416 | 0 | 0 | 1788.9385 | 15720.4739 | 4046.1733 | 4966.3947 | 3611.8297 | 1253.4863 | 10646.9637 | 8760 | 0 | 358.525 | 0 | 850.5 | 577768.7355 | 210834.9497 | 361.15 | -580.4457
333 | E | SOR | TOU | CC | FP | HC | R100 | 2.4656 | 26.5 | 1.35 | 8760 | 168248.8355 | 152207.1 | 163393.8627 | 65533.1035 | 168695.8939 | 36062.5 | 100975 | 50487.5 | 3245.625 | 213559.8362 | 8760 | 1482.4089 | 11348.7948 | 1771.1532 | 14489.0362 | 0 | 0 | 0 | -1228.6933 | 0 | 2357.4504 | 8760 | 1789.619 | 0 | 0 | 1788.9385 | 15720.4739 | 4031.869 | 4961.999 | 3600.0647 | 1251.9692 | 9749.1568 | 8760 | 0 | 360.625 | 0 | 850.5 | 577745.3103 | 210834.9497 | 302.025 | -577.8843
334 | E | SOR | TOU | CC | FP | HC | R100 | 2.4656 | 21.5 | 1.1 | 8760 | 164190.0033 | 163598.4 | 169721.9408 | 65533.1035 | 168695.8939 | 36242.5 | 101479 | 50739.5 | 3261.825 | 214630.3897 | 8760 | 1482.4089 | 10072.9473 | 2103.2862 | 15301.0184 | 0 | 0 | 0 | -1196.2482 | 0 | 2336.3977 | 8760 | 1789.2704 | 0 | 0 | 1788.9385 | 15720.4739 | 4012.0838 | 4957.5584 | 3585.2007 | 1247.9736 | 8543.4553 | 8760 | 0 | 362.425 | 0 | 850.5 | 577745.3591 | 210834.9497 | 234.8 | -572.8238
335 | E | SOR | TOU | CC | FP | HC | R100 | 2.4656 | 17 | 0.85 | 8760 | 161569.2456 | 174681.9 | 175879.0303 | 65533.1035 | 168695.8939 | 36417.5 | 101969 | 50984.5 | 3277.575 | 215664.5047 | 8760 | 1482.4089 | 8694.7831 | 2513.1303 | 16214.1777 | 0 | 0 | 0 | -1166.4182 | 0 | 2311.0118 | 8760 | 1788.6019 | 0 | 0 | 1788.9385 | 15720.4739 | 3991.9204 | 4955.5647 | 3572.9662 | 1242.9556 | 7242.8271 | 8760 | 0 | 364.175 | 0 | 850.5 | 577756.7396 | 210834.9497 | 164.825 | -572.818
336 | E | SOR | TOU | CC | FP | HC | R10 | 2.4656 | 12.5 | 0.65 | 8760 | 159406.4829 | 187003.35 | 182723.824 | 65533.1035 | 168695.8939 | 36675 | 102690 | 51345 | 3300.75 | 217175.2255 | 8760 | 1482.4089 | 7062.1599 | 3027.7395 | 17274.9128 | 0 | 0 | 0 | -1129.0283 | 0 | 2258.7916 | 8760 | 1789.8288 | 0 | 0 | 1788.9385 | 15720.4739 | 3959.752 | 4959.8329 | 3566.0525 | 1233.9154 | 5724.2647 | 8760 | 0 | 366.75 | 0 | 850.5 | 577737.3478 | 210834.9497 | 93.225 | -566.8353
337 | E | SOR | TOU | CC | FP | HC | R10 | 2.4656 | 31 | 0.8 | 8760 | 162683.6308 | 154576.35 | 164710.025 | 65533.1035 | 168695.8939 | 35870 | 100436 | 50218 | 3228.3 | 212430.8862 | 8760 | 1482.4089 | 11019.0857 | 1833.4452 | 14880.2261 | 0 | 0 | 0 | -1265.9319 | 0 | 2449.1159 | 8760 | 1789.9128 | 0 | 0 | 1788.9385 | 15720.4739 | 4030.7672 | 4977.2765 | 3617.0913 | 1248.6748 | 9306.2646 | 8760 | 0 | 358.7 | 0 | 850.5 | 577761.9228 | 210834.9497 | 427.45 | -579.67
338 | E | SOR | TOU | CC | FP | HC | R10 | 2.4656 | 26.5 | 0.65 | 8760 | 157205.8739 | 164000.7 | 169945.4259 | 65533.1035 | 168695.8939 | 35992.5 | 100779 | 50389.5 | 3239.325 | 213155.3659 | 8760 | 1482.4089 | 9959.7215 | 2085.2983 | 15722.0789 | 0 | 0 | 0 | -1254.6666 | 0 | 2454.36 | 8760 | 1789.4579 | 0 | 0 | 1788.9385 | 15720.4739 | 4014.6987 | 4975.6403 | 3606.1709 | 1244.556 | 8278.3841 | 8760 | 0 | 359.925 | 0 | 850.5 | 577751.3818 | 210834.9497 | 383.525 | -576.1769
339 | E | SOR | TOU | CC | FP | HC | R10 | 2.4656 | 21.5 | 0.55 | 8760 | 153060.1639 | 175034.25 | 176074.7673 | 65533.1035 | 168695.8939 | 36170 | 101276 | 50638 | 3255.3 | 214193.9349 | 8760 | 1482.4089 | 8779.1282 | 2405.3231 | 16599.1224 | 0 | 0 | 0 | -1244.3172 | 0 | 2447.7656 | 8760 | 1789.6227 | 0 | 0 | 1788.9385 | 15720.4739 | 3998.0197 | 4966.3168 | 3595.4713 | 1239.4939 | 7151.5351 | 8760 | 0 | 361.7 | 0 | 850.5 | 577754.1866 | 210834.9497 | 311.45 | -576.9961
340 | E | SOR | TOU | CC | FP | HC | R10 | 2.4656 | 17 | 0.45 | 8760 | 152165.1546 | 185098.5 | 181665.6445 | 65533.1035 | 168695.8939 | 36347.5 | 101773 | 50886.5 | 3271.275 | 215243.832 | 8760 | 1482.4089 | 7726.4617 | 2828.1695 | 17255.9633 | 0 | 0 | 0 | -1262.545 | 0 | 2399.023 | 8760 | 1789.3383 | 0 | 0 | 1788.9385 | 15720.4739 | 3979.1814 | 4964.1945 | 3582.4555 | 1233.3364 | 6195.2838 | 8760 | 0 | 363.475 | 0 | 850.5 | 577741.5628 | 210834.9497 | 243.275 | -573.8892
341 | E | SOR | TOU | CC | FP | HC | R10 | 2.4656 | 12.5 | 0.3 | 8760 | 143856.149 | 203931 | 192127.447 | 65533.1035 | 168695.8939 | 36480 | 102144 | 51072 | 3283.2 | 216029.282 | 8760 | 1482.4089 | 5693.7653 | 3543.1192 | 18854.6792 | 0 | 0 | 0 | -1326.3579 | 0 | 2444.2118 | 8760 | 1788.751 | 0 | 0 | 1788.9385 | 15720.4739 | 3942.9457 | 4967.2603 | 3573.5315 | 1219.8184 | 4170.8737 | 8760 | 0 | 364.8 | 0 | 850.5 | 577751.908 | 210834.9497 | 205.125 | -571.4767
342 | E | SOR | TOU | CC | FP | HC | R600 | 2.9038 | 31 | 2.3 | 8760 | 172330.3182 | 120363.3 | 145704.0421 | 65533.1035 | 119230.8118 | 45877.5 | 128457 | 64228.5 | 4128.975 | 272346.1717 | 8760 | 1475.3019 | 12344.7333 | 1943.7078 | 8558.8266 | 0 | 0 | 0 | -1321.2648 | 0 | 2274.2197 | 8760 | 2321.2703 | 0 | 0 | 2321.0821 | 9757.4188 | 4644.0277 | 6783.6242 | 4627.9893 | 1456.5761 | 10686.6584 | 8760 | 0 | 458.775 | 0 | 1048.625 | 739568.8515 | 189624.8638 | 324.575 | -602.7349
343 | E | SOR | TOU | CC | FP | HC | R600 | 2.9038 | 26.5 | 2 | 8760 | 168876.295 | 128105.55 | 150005.0054 | 65533.1035 | 119230.8118 | 46120 | 129136 | 64568 | 4150.8 | 273771.9699 | 8760 | 1475.3019 | 11394.8092 | 2294.3173 | 9120.7333 | 0 | 0 | 0 | -1292.8141 | 0 | 2262.0517 | 8760 | 2320.7565 | 0 | 0 | 2321.0821 | 9757.4188 | 4628.8734 | 6771.7201 | 4611.563 | 1453.1766 | 9789.0194 | 8760 | 0 | 461.2 | 0 | 1048.625 | 739560.1365 | 189624.8638 | 270.075 | -598.6914
344 | E | SOR | TOU | CC | FP | HC | R600 | 2.9038 | 21.5 | 1.6 | 8760 | 165801.432 | 138271.05 | 155652.1289 | 65533.1035 | 119230.8118 | 46337.5 | 129745 | 64872.5 | 4170.375 | 275067.1388 | 8760 | 1475.3019 | 10158.3942 | 2780.7648 | 9822.0759 | 0 | 0 | 0 | -1251.9842 | 0 | 2244.1099 | 8760 | 2321.4291 | 0 | 0 | 2321.0821 | 9757.4188 | 4605.4566 | 6774.6739 | 4598.911 | 1449.4586 | 8622.0401 | 8760 | 0 | 463.375 | 0 | 1048.625 | 739545.3234 | 189624.8638 | 197.3 | -596.7167
345 | E | SOR | TOU | CC | FP | HC | R600 | 2.9038 | 17 | 1.3 | 8760 | 164647.26 | 148271.85 | 161207.7585 | 65533.1035 | 119230.8118 | 46500 | 130200 | 65100 | 4185 | 276044.0666 | 8760 | 1475.3019 | 8902.8926 | 3292.1458 | 10430.7119 | 0 | 0 | 0 | -1203.0222 | 0 | 2209.4742 | 8760 | 2320.4212 | 0 | 0 | 2321.0821 | 9757.4188 | 4570.1899 | 6782.3691 | 4584.9844 | 1441.9126 | 7455.2463 | 8760 | 0 | 465 | 0 | 1048.625 | 739551.501 | 189624.8638 | 125.45 | -590.7051
346 | E | SOR | TOU | CC | FP | HC | R600 | 2.9038 | 12.5 | 0.95 | 8760 | 162172.1679 | 160810.65 | 168173.2941 | 65533.1035 | 119230.8118 | 46702.5 | 130767 | 65383.5 | 4203.225 | 277257.2435 | 8760 | 1475.3019 | 7285.4754 | 3915.6117 | 11163.2095 | 0 | 0 | 0 | -1135.4256 | 0 | 2133.9842 | 8760 | 2321.0363 | 0 | 0 | 2321.0821 | 9757.4188 | 4512.9751 | 6795.2425 | 4574.2614 | 1426.5076 | 5978.4173 | 8760 | 0 | 467.025 | 0 | 1048.625 | 739545.3306 | 189624.8638 | 60.7 | -590.9229
347 | E | SOR | TOU | CC | FP | HC | R600 | 2.9038 | 31 | 1.55 | 8760 | 168526.9665 | 123603.3 | 147503.9221 | 65533.1035 | 119230.8118 | 45877.5 | 128457 | 64228.5 | 4128.975 | 272347.4013 | 8760 | 1475.3019 | 11794.9703 | 2141.1208 | 9060.0352 | 0 | 0 | 0 | -1323.6032 | 0 | 2305.201 | 8760 | 2321.8887 | 0 | 0 | 2321.0821 | 9757.4188 | 4641.0088 | 6787.3624 | 4631.7799 | 1454.7184 | 10106.1234 | 8760 | 0 | 458.775 | 0 | 1048.625 | 739571.5878 | 189624.8638 | 358.45 | -603.4775
348 | E | SOR | TOU | CC | FP | HC | R600 | 2.9038 | 26.5 | 1.35 | 8760 | 165597.8232 | 130844.7 | 151526.6539 | 65533.1035 | 119230.8118 | 46065 | 128982 | 64491 | 4145.85 | 273452.1346 | 8760 | 1475.3019 | 10921.4519 | 2463.8399 | 9564.5983 | 0 | 0 | 0 | -1297.2531 | 0 | 2300.7633 | 8760 | 2320.9228 | 0 | 0 | 2321.0821 | 9757.4188 | 4625.7601 | 6777.0332 | 4615.6548 | 1450.9417 | 9275.0659 | 8760 | 0 | 460.65 | 0 | 1048.625 | 739540.7196 | 189624.8638 | 297 | -598.6357
349 | E | SOR | TOU | CC | FP | HC | R600 | 2.9038 | 21.5 | 1.1 | 8760 | 163008.281 | 140643 | 156969.791 | 65533.1035 | 119230.8118 | 46250 | 129500 | 64750 | 4162.5 | 274562.0454 | 8760 | 1475.3019 | 9780.4288 | 2928.7881 | 10141.9295 | 0 | 0 | 0 | -1261.064 | 0 | 2282.2962 | 8760 | 2321.9449 | 0 | 0 | 2321.0821 | 9757.4188 | 4600.7379 | 6785.7662 | 4604.7053 | 1445.0756 | 8204.9562 | 8760 | 0 | 462.5 | 0 | 1048.625 | 739556.6796 | 189624.8638 | 222.525 | -599.2971
350 | E | SOR | TOU | CC | FP | HC | R600 | 2.9038 | 17 | 0.85 | 8760 | 160571.5058 | 150840.9 | 162634.9133 | 65533.1035 | 119230.8118 | 46480 | 130144 | 65072 | 4183.2 | 275918.2259 | 8760 | 1475.3019 | 8515.7135 | 3426.3478 | 10739.9414 | 0 | 0 | 0 | -1218.8004 | 0 | 2251.025 | 8760 | 2321.1437 | 0 | 0 | 2321.0821 | 9757.4188 | 4562.4221 | 6785.8848 | 4590.7987 | 1436.1187 | 7026.4763 | 8760 | 0 | 464.8 | 0 | 1048.625 | 739569.7923 | 189624.8638 | 153.275 | -594.8453
351 | E | SOR | TOU | CC | FP | HC | R60 | 2.9038 | 12.5 | 0.65 | 8760 | 158913.5541 | 163067.85 | 169427.2105 | 65533.1035 | 119230.8118 | 46665 | 130662 | 65331 | 4199.85 | 277012.7576 | 8760 | 1475.3019 | 6967.5587 | 4061.9918 | 11478.1279 | 0 | 0 | 0 | -1170.3984 | 0 | 2191.842 | 8760 | 2320.3221 | 0 | 0 | 2321.0821 | 9757.4188 | 4508.8535 | 6776.6232 | 4576.4391 | 1423.2822 | 5603.8667 | 8760 | 0 | 466.65 | 0 | 1048.625 | 739534.4619 | 189624.8638 | 81.875 | -592.4348
352 | E | SOR | TOU | CC | FP | HC | R60 | 2.9038 | 31 | 0.8 | 8760 | 159339.0306 | 133247.7 | 152861.5649 | 65533.1035 | 119230.8118 | 45727.5 | 128037 | 64018.5 | 4115.475 | 271483.9269 | 8760 | 1475.3019 | 10633.0279 | 2582.2863 | 9856.1501 | 0 | 0 | 0 | -1321.7669 | 0 | 2379.0697 | 8760 | 2321.1379 | 0 | 0 | 2321.0821 | 9757.4188 | 4619.7589 | 6805.2787 | 4639.0011 | 1445.595 | 8890.3908 | 8760 | 0 | 457.275 | 0 | 1048.625 | 739563.6678 | 189624.8638 | 422.725 | -609.5972
353 | E | SOR | TOU | CC | FP | HC | R60 | 2.9038 | 26.5 | 0.65 | 8760 | 154994.9098 | 141187.05 | 157272.0209 | 65533.1035 | 119230.8118 | 45895 | 128506 | 64253 | 4130.55 | 272473.587 | 8760 | 1475.3019 | 9720.2873 | 2891.1733 | 10388.3124 | 0 | 0 | 0 | -1304.9371 | 0 | 2379.5197 | 8760 | 2321.3034 | 0 | 0 | 2321.0821 | 9757.4188 | 4592.8814 | 6808.4945 | 4628.7638 | 1439.8976 | 8015.2173 | 8760 | 0 | 458.95 | 0 | 1048.625 | 739539.8132 | 189624.8638 | 374.175 | -603.6886
354 | E | SOR | TOU | CC | FP | HC | R60 | 2.9038 | 21.5 | 0.55 | 8760 | 151228.0529 | 151201.35 | 162835.15 | 65533.1035 | 119230.8118 | 46050 | 128940 | 64470 | 4144.5 | 273409.0333 | 8760 | 1475.3019 | 8638.6048 | 3318.1262 | 11019.0404 | 0 | 0 | 0 | -1288.088 | 0 | 2367.6408 | 8760 | 2320.6788 | 0 | 0 | 2321.0821 | 9757.4188 | 4566.0457 | 6807.1831 | 4610.5296 | 1433.3347 | 6994.142 | 8760 | 0 | 460.5 | 0 | 1048.625 | 739529.2173 | 189624.8638 | 300.225 | -597.9639
355 | E | SOR | TOU | CC | FP | HC | R60 | 2.9038 | 17 | 0.45 | 8760 | 151961.8596 | 160450.2 | 167973.0574 | 65533.1035 | 119230.8118 | 46327.5 | 129717 | 64858.5 | 4169.475 | 275028.6513 | 8760 | 1475.3019 | 7660.8964 | 3813.7697 | 11425.6837 | 0 | 0 | 0 | -1295.2338 | 0 | 2328.9267 | 8760 | 2321.5304 | 0 | 0 | 2321.0821 | 9757.4188 | 4532.2201 | 6800.749 | 4600.122 | 1423.4816 | 6107.9259 | 8760 | 0 | 463.275 | 0 | 1048.625 | 739537.7238 | 189624.8638 | 227.15 | -596.5766
356 | E | SOR | TOU | CC | FP | HC | R60 | 2.9038 | 12.5 | 0.3 | 8760 | 142787.8631 | 178837.2 | 178187.3764 | 65533.1035 | 119230.8118 | 46502.5 | 130207 | 65103.5 | 4185.225 | 276045.7383 | 8760 | 1475.3019 | 5643.1842 | 4627.7907 | 12865.9435 | 0 | 0 | 0 | -1345.2641 | 0 | 2369.5621 | 8760 | 2320.3084 | 0 | 0 | 2321.0821 | 9757.4188 | 4475.4456 | 6786.4702 | 4588.9821 | 1405.6537 | 4102.6579 | 8760 | 0 | 465.025 | 0 | 1048.625 | 739526.1884 | 189624.8638 | 185.5 | -594.4452
357 | E | SOR | TOU | CC | FP | WC | R100 | 3.4612 | 43.5 | 3.25 | 8760 | 203879.1646 | 143900.55 | 158779.4204 | 65533.1035 | 200991.9069 | 41697.5 | 143856.375 | 58376.5 | 3752.775 | 19285.0938 | 8760 | 1482.4089 | 16860.6529 | 1564.8053 | 17954.0843 | 0 | 0 | 0 | -1265.5214 | 0 | 2327.1876 | 8760 | 2511.0158 | 0 | 0 | 2511.3333 | 22068.5897 | 5266.9569 | 8438.0756 | 4721.1409 | 1662.3434 | 15187.1313 | 8760 | 10700.3041 | 416.975 | 0 | 850.5 | 819512.6259 | 210834.9497 | 404.325
358 | E | SOR | TOU | CC | FP | WC | R100 | 3.4612 | 37 | 2.8 | 8760 | 193785.0464 | 152263.8 | 163425.3606 | 65533.1035 | 200991.9069 | 41937.5 | 144684.375 | 58712.5 | 3774.375 | 19396.0938 | 8760 | 1482.4089 | 15565.0973 | 1833.5747 | 18984.6613 | 0 | 0 | 0 | -1233.2987 | 0 | 2317.9884 | 8760 | 2510.5687 | 0 | 0 | 2511.3333 | 22068.5897 | 5243.9082 | 8450.3989 | 4701.9495 | 1658.4356 | 13941.3758 | 8760 | 10723.818 | 419.375 | 0 | 850.5 | 819496.0058 | 210834.9497 | 339.125
359 | E | SOR | TOU | CC | FP | WC | R100 | 3.4612 | 30.5 | 2.3 | 8760 | 185432.116 | 161561.25 | 168590.2663 | 65533.1035 | 200991.9069 | 42165 | 145469.25 | 59031 | 3794.85 | 19501.3125 | 8760 | 1482.4089 | 14012.5426 | 2213.6956 | 20159.6035 | 0 | 0 | 0 | -1194.1949 | 0 | 2304.9628 | 8760 | 2510.3628 | 0 | 0 | 2511.3333 | 22068.5897 | 5210.2695 | 8462.217 | 4680.9066 | 1653.8864 | 12451.5902 | 8760 | 10746.1295 | 421.65 | 0 | 850.5 | 819494.3753 | 210834.9497 | 271.525
360 | E | SOR | TOU | CC | FP | WC | R100 | 3.4612 | 24 | 1.8 | 8760 | 177838.7011 | 173858.4 | 175421.5608 | 65533.1035 | 200991.9069 | 42460 | 146487 | 59444 | 3821.4 | 19637.75 | 8760 | 1482.4089 | 12132.977 | 2754.4204 | 21372.6606 | 0 | 0 | 0 | -1147.1063 | 0 | 2277.9004 | 8760 | 2510.7299 | 0 | 0 | 2511.3333 | 22068.5897 | 5171.2991 | 8484.041 | 4660.1323 | 1644.4772 | 10657.1508 | 8760 | 10782.0779 | 424.6 | 0 | 850.5 | 819491.7528 | 210834.9497 | 197.275
361 | E | SOR | TOU | CC | FP | WC | R100 | 3.4612 | 17.5 | 1.3 | 8760 | 172033.2879 | 187871.4 | 183206.0418 | 65533.1035 | 200991.9069 | 42660 | 147177 | 59724 | 3839.4 | 19730.25 | 8760 | 1482.4089 | 9905.8586 | 3362.1438 | 22765.445 | 0 | 0 | 0 | -1090.9594 | 0 | 2228.2465 | 8760 | 2509.5775 | 0 | 0 | 2511.3333 | 22068.5897 | 5130.6197 | 8495.556 | 4641.1221 | 1631.1111 | 8548.6652 | 8760 | 10802.0843 | 426.6 | 0 | 850.5 | 819454.3164 | 210834.9497 | 108.1
362 | E | SOR | TOU | CC | FP | WC | R100 | 3.4612 | 43.5 | 2.2 | 8760 | 199616.889 | 145671.75 | 159763.3548 | 65533.1035 | 200991.9069 | 41775 | 144123.75 | 58485 | 3759.75 | 19320.9375 | 8760 | 1482.4089 | 16170.4609 | 1709.4467 | 18700.2642 | 0 | 0 | 0 | -1265.5253 | 0 | 2352.4742 | 8760 | 2510.3355 | 0 | 0 | 2511.3333 | 22068.5897 | 5266.3342 | 8444.6139 | 4714.9985 | 1659.9732 | 14471.0485 | 8760 | 10709.9481 | 417.75 | 0 | 850.5 | 819517.4822 | 210834.9497 | 435.7
363 | E | SOR | TOU | CC | FP | WC | R100 | 3.4612 | 37 | 1.85 | 8760 | 190476.6783 | 154286.1 | 164548.7857 | 65533.1035 | 200991.9069 | 41975 | 144813.75 | 58765 | 3777.75 | 19413.4375 | 8760 | 1482.4089 | 14891.5626 | 1995.4649 | 19610.4347 | 0 | 0 | 0 | -1237.0244 | 0 | 2355.2447 | 8760 | 2510.1447 | 0 | 0 | 2511.3333 | 22068.5897 | 5240.6956 | 8455.4835 | 4698.8368 | 1656.5915 | 13233.0288 | 8760 | 10728.2594 | 419.75 | 0 | 850.5 | 819508.5857 | 210834.9497 | 367.025
364 | E | SOR | TOU | CC | FP | WC | R100 | 3.4612 | 30.5 | 1.55 | 8760 | 181599.9308 | 164617.65 | 170288.1531 | 65533.1035 | 200991.9069 | 42212.5 | 145633.125 | 59097.5 | 3799.125 | 19523.2812 | 8760 | 1482.4089 | 13405.0977 | 2396.5988 | 20611.9607 | 0 | 0 | 0 | -1202.9884 | 0 | 2342.6278 | 8760 | 2510.6441 | 0 | 0 | 2511.3333 | 22068.5897 | 5211.5906 | 8467.343 | 4680.1226 | 1650.4958 | 11807.8351 | 8760 | 10752.9815 | 422.125 | 0 | 850.5 | 819506.0164 | 210834.9497 | 298.8
365 | E | SOR | TOU | CC | FP | WC | R100 | 3.4612 | 24 | 1.2 | 8760 | 174192.0261 | 176465.25 | 176869.7143 | 65533.1035 | 200991.9069 | 42417.5 | 146340.375 | 59384.5 | 3817.575 | 19618.0938 | 8760 | 1482.4089 | 11597.0743 | 2900.5097 | 21773.0146 | 0 | 0 | 0 | -1166.1043 | 0 | 2322.1653 | 8760 | 2510.5143 | 0 | 0 | 2511.3333 | 22068.5897 | 5177.2133 | 8480.6768 | 4662.8406 | 1640.0872 | 10077.0429 | 8760 | 10774.6867 | 424.175 | 0 | 850.5 | 819472.6545 | 210834.9497 | 224.975
366 | E | SOR | TOU | CC | FP | WC | R10 | 3.4612 | 17.5 | 0.9 | 8760 | 168254.0418 | 189611.55 | 184172.7274 | 65533.1035 | 200991.9069 | 42665 | 147194.25 | 59731 | 3839.85 | 19732.5625 | 8760 | 1482.4089 | 9473.7554 | 3511.6205 | 23172.8623 | 0 | 0 | 0 | -1118.3051 | 0 | 2276.8804 | 8760 | 2509.5026 | 0 | 0 | 2511.3333 | 22068.5897 | 5127.0257 | 8497.3332 | 4641.0254 | 1624.5127 | 8067.9037 | 8760 | 10806.29 | 426.65 | 0 | 850.5 | 819469.0246 | 210834.9497 | 133.75
367 | E | SOR | TOU | CC | FP | WC | R10 | 3.4612 | 43.5 | 1.1 | 8760 | 188712.0995 | 154950.3 | 164917.7611 | 65533.1035 | 200991.9069 | 41907.5 | 144580.875 | 58670.5 | 3771.675 | 19382.2188 | 8760 | 1482.4089 | 14466.8806 | 2095.6986 | 20103.9319 | 0 | 0 | 0 | -1257.209 | 0 | 2425.8849 | 8760 | 2511.5971 | 0 | 0 | 2511.3333 | 22068.5897 | 5238.1773 | 8467.6994 | 4714.8285 | 1649.9683 | 12713.4141 | 8760 | 10736.3153 | 419.075 | 0 | 850.5 | 819555.3481 | 210834.9497 | 507.1
368 | E | SOR | TOU | CC | FP | WC | R10 | 3.4612 | 37 | 0.95 | 8760 | 179822.2934 | 163398.6 | 169610.9482 | 65533.1035 | 200991.9069 | 42020 | 144969 | 58828 | 3781.8 | 19434.25 | 8760 | 1482.4089 | 13321.3136 | 2375.1902 | 20922.9306 | 0 | 0 | 0 | -1239.5726 | 0 | 2431.313 | 8760 | 2510.2844 | 0 | 0 | 2511.3333 | 22068.5897 | 5216.9723 | 8470.979 | 4699.8881 | 1644.4865 | 11603.367 | 8760 | 10743.6483 | 420.2 | 0 | 850.5 | 819506.9439 | 210834.9497 | 437.675
369 | E | SOR | TOU | CC | FP | WC | R10 | 3.4612 | 30.5 | 0.75 | 8760 | 169969.2345 | 174108.15 | 175560.3016 | 65533.1035 | 200991.9069 | 42172.5 | 145495.125 | 59041.5 | 3795.525 | 19504.7812 | 8760 | 1482.4089 | 11790.1175 | 2740.7985 | 22106.8246 | 0 | 0 | 0 | -1221.3063 | 0 | 2433.8637 | 8760 | 2509.3987 | 0 | 0 | 2511.3333 | 22068.5897 | 5187.4645 | 8471.5317 | 4681.8334 | 1635.8557 | 10118.5495 | 8760 | 10748.4007 | 421.725 | 0 | 850.5 | 819480.243 | 210834.9497 | 384.525
370 | E | SOR | TOU | CC | FP | WC | R10 | 3.4612 | 24 | 0.6 | 8760 | 161278.7581 | 187157.25 | 182809.3183 | 65533.1035 | 200991.9069 | 42355 | 146124.75 | 59297 | 3811.95 | 19589.1875 | 8760 | 1482.4089 | 10053.4761 | 3234.221 | 23427.0961 | 0 | 0 | 0 | -1206.3489 | 0 | 2433.6326 | 8760 | 2509.9658 | 0 | 0 | 2511.3333 | 22068.5897 | 5151.2003 | 8481.0038 | 4665.941 | 1623.0196 | 8435.3153 | 8760 | 10771.7834 | 423.55 | 0 | 850.5 | 819471.1913 | 210834.9497 | 307.875
371 | E | SOR | TOU | CC | FP | WC | R10 | 3.4612 | 17.5 | 0.45 | 8760 | 156049.2411 | 200398.05 | 190164.8278 | 65533.1035 | 200991.9069 | 42570 | 146866.5 | 59598 | 3831.3 | 19688.625 | 8760 | 1482.4089 | 8246.4744 | 3940.9298 | 24398.4939 | 0 | 0 | 0 | -1226.2231 | 0 | 2374.6985 | 8760 | 2509.7845 | 0 | 0 | 2511.3333 | 22068.5897 | 5102.5961 | 8490.4364 | 4648.879 | 1603.7016 | 6750.4545 | 8760 | 10792.5376 | 425.7 | 0 | 850.5 | 819460.8865 | 210834.9497 | 227.125
372 | E | SOR | TOU | CC | FP | WC | R600 | 4.0765 | 43.5 | 3.25 | 8760 | 198954.193 | 122242.5 | 146747.9725 | 65533.1035 | 139231.0069 | 54417.5 | 187740.375 | 76184.5 | 4897.575 | 25168.0938 | 8760 | 1475.3019 | 16099.9723 | 2160.6108 | 11426.5456 | 0 | 0 | 0 | -1333.5529 | 0 | 2264.8112 | 8760 | 3258.4399 | 0 | 0 | 3258.3629 | 13697.5815 | 5971.7039 | 11282.0198 | 6097.746 | 1893.4162 | 14383.5626 | 8760 | 14066.6769 | 544.175 | 0 | 1048.625 | 1048981.3851 | 189624.8638 | 404.325
373 | E | SOR | TOU | CC | FP | WC | R600 | 4.0765 | 37 | 2.8 | 8760 | 190525.7011 | 131770.8 | 152041.1196 | 65533.1035 | 139231.0069 | 54657.5 | 188568.375 | 76520.5 | 4919.175 | 25279.0938 | 8760 | 1475.3019 | 14880.358 | 2580.3066 | 12204.8398 | 0 | 0 | 0 | -1308.8395 | 0 | 2269.04 | 8760 | 3256.6371 | 0 | 0 | 3258.3629 | 13697.5815 | 5952.6935 | 11289.2055 | 6072.4857 | 1888.617 | 13203.7009 | 8760 | 14088.2887 | 546.575 | 0 | 1048.625 | 1048934.501 | 189624.8638 | 335.6
374 | E | SOR | TOU | CC | FP | WC | R600 | 4.0765 | 30.5 | 2.3 | 8760 | 182547.881 | 142345.35 | 157915.478 | 65533.1035 | 139231.0069 | 54940 | 189543 | 76916 | 4944.6 | 25409.75 | 8760 | 1475.3019 | 13383.4557 | 3160.2133 | 13080.3057 | 0 | 0 | 0 | -1273.294 | 0 | 2261.6326 | 8760 | 3256.4672 | 0 | 0 | 3258.3629 | 13697.5815 | 5923.9931 | 11308.427 | 6049.2203 | 1881.8542 | 11764.3305 | 8760 | 14118.9636 | 549.4 | 0 | 1048.625 | 1048918.7516 | 189624.8638 | 264.35
375 | E | SOR | TOU | CC | FP | WC | R600 | 4.0765 | 24 | 1.8 | 8760 | 176342.5453 | 153260.1 | 163978.8237 | 65533.1035 | 139231.0069 | 55197.5 | 190431.375 | 77276.5 | 4967.775 | 25528.8438 | 8760 | 1475.3019 | 11704.5174 | 3842.8421 | 13977.2394 | 0 | 0 | 0 | -1226.9645 | 0 | 2237.5753 | 8760 | 3256.7826 | 0 | 0 | 3258.3629 | 13697.5815 | 5879.764 | 11335.685 | 6029.9807 | 1871.2751 | 10168.6435 | 8760 | 14152.5272 | 551.975 | 0 | 1048.625 | 1048925.3259 | 189624.8638 | 186.75
376 | E | SOR | TOU | CC | FP | WC | R600 | 4.0765 | 17.5 | 1.3 | 8760 | 170977.1009 | 166237.65 | 171188.0931 | 65533.1035 | 139231.0069 | 55492.5 | 191449.125 | 77689.5 | 4994.325 | 25665.2812 | 8760 | 1475.3019 | 9647.8372 | 4655.1671 | 14942.9184 | 0 | 0 | 0 | -1157.792 | 0 | 2179.6877 | 8760 | 3256.71 | 0 | 0 | 3258.3629 | 13697.5815 | 5801.8009 | 11358.5435 | 6008.5484 | 1848.5204 | 8242.866 | 8760 | 14192.1528 | 554.925 | 0 | 1048.625 | 1048903.7819 | 189624.8638 | 100.3
377 | E | SOR | TOU | CC | FP | WC | R600 | 4.0765 | 43.5 | 2.2 | 8760 | 195027.1187 | 125702.55 | 148670.0944 | 65533.1035 | 139231.0069 | 54470 | 187921.5 | 76258 | 4902.3 | 25192.375 | 8760 | 1475.3019 | 15411.4074 | 2387.3936 | 12062.8875 | 0 | 0 | 0 | -1335.5697 | 0 | 2293.1846 | 8760 | 3258.3441 | 0 | 0 | 3258.3629 | 13697.5815 | 5970.8445 | 11285.7712 | 6096.4658 | 1890.9877 | 13665.2195 | 8760 | 14074.4712 | 544.7 | 0 | 1048.625 | 1048995.0843 | 189624.8638 | 431.925
378 | E | SOR | TOU | CC | FP | WC | R600 | 4.0765 | 37 | 1.85 | 8760 | 186152.6622 | 134353.35 | 153475.774 | 65533.1035 | 139231.0069 | 54682.5 | 188654.625 | 76555.5 | 4921.425 | 25290.6562 | 8760 | 1475.3019 | 14186.2057 | 2837.2776 | 12815.4092 | 0 | 0 | 0 | -1309.6252 | 0 | 2304.0078 | 8760 | 3257.7507 | 0 | 0 | 3258.3629 | 13697.5815 | 5947.0086 | 11301.4 | 6077.4869 | 1884.8456 | 12471.9457 | 8760 | 14099.2865 | 546.825 | 0 | 1048.625 | 1048945.5951 | 189624.8638 | 366.875
379 | E | SOR | TOU | CC | FP | WC | R600 | 4.0765 | 30.5 | 1.55 | 8760 | 178809.546 | 143429.4 | 158517.6878 | 65533.1035 | 139231.0069 | 54902.5 | 189413.625 | 76863.5 | 4941.225 | 25392.4062 | 8760 | 1475.3019 | 12842.2783 | 3365.2284 | 13557.3164 | 0 | 0 | 0 | -1277.2833 | 0 | 2294.4741 | 8760 | 3257.2317 | 0 | 0 | 3258.3629 | 13697.5815 | 5920.99 | 11315.0852 | 6055.8613 | 1877.5575 | 11186.2712 | 8760 | 14120.04 | 549.025 | 0 | 1048.625 | 1048937.5401 | 189624.8638 | 294.325
380 | E | SOR | TOU | CC | FP | WC | R600 | 4.0765 | 24 | 1.2 | 8760 | 172897.2621 | 154491.3 | 164662.7781 | 65533.1035 | 139231.0069 | 55172.5 | 190345.125 | 77241.5 | 4965.525 | 25517.2812 | 8760 | 1475.3019 | 11244.3086 | 4042.8798 | 14315.2142 | 0 | 0 | 0 | -1233.0869 | 0 | 2272.3505 | 8760 | 3257.2253 | 0 | 0 | 3258.3629 | 13697.5815 | 5870.4861 | 11335.569 | 6034.3728 | 1862.1842 | 9671.9387 | 8760 | 14153.9651 | 551.725 | 0 | 1048.625 | 1048940.1934 | 189624.8638 | 215.05
381 | E | SOR | TOU | CC | FP | WC | R60 | 4.0765 | 17.5 | 0.9 | 8760 | 167676.2487 | 167630.85 | 171962.0415 | 65533.1035 | 139231.0069 | 55465 | 191354.25 | 77651 | 4991.85 | 25652.5625 | 8760 | 1475.3019 | 9289.6472 | 4783.0585 | 15199.4781 | 0 | 0 | 0 | -1172.9953 | 0 | 2219.5434 | 8760 | 3256.867 | 0 | 0 | 3258.3629 | 13697.5815 | 5794.478 | 11361.7704 | 6011.0979 | 1843.937 | 7845.7802 | 8760 | 14190.7269 | 554.65 | 0 | 1048.625 | 1048906.585 | 189624.8638 | 122.375
382 | E | SOR | TOU | CC | FP | WC | R60 | 4.0765 | 43.5 | 1.1 | 8760 | 184196.916 | 135469.8 | 154095.9826 | 65533.1035 | 139231.0069 | 54482.5 | 187964.625 | 76275.5 | 4903.425 | 25198.1562 | 8760 | 1475.3019 | 13794.3241 | 2994.2395 | 13139.0566 | 0 | 0 | 0 | -1322.6539 | 0 | 2361.7256 | 8760 | 3257.9439 | 0 | 0 | 3258.3629 | 13697.5815 | 5946.1398 | 11305.8574 | 6099.4134 | 1877.3928 | 12004.5761 | 8760 | 14088.3618 | 544.825 | 0 | 1048.625 | 1049000.8143 | 189624.8638 | 502.575
383 | E | SOR | TOU | CC | FP | WC | R60 | 4.0765 | 37 | 0.95 | 8760 | 175921.6064 | 142742.25 | 158135.9633 | 65533.1035 | 139231.0069 | 54647.5 | 188533.875 | 76506.5 | 4918.275 | 25274.4688 | 8760 | 1475.3019 | 12799.052 | 3348.8647 | 13705.0443 | 0 | 0 | 0 | -1301.0366 | 0 | 2365.5279 | 8760 | 3257.5413 | 0 | 0 | 3258.3629 | 13697.5815 | 5915.5044 | 11313.4472 | 6083.2419 | 1869.7927 | 11044.9907 | 8760 | 14102.3786 | 546.475 | 0 | 1048.625 | 1048974.4947 | 189624.8638 | 434.425
384 | E | SOR | TOU | CC | FP | WC | R60 | 4.0765 | 30.5 | 0.75 | 8760 | 167717.6226 | 152845.65 | 163748.5891 | 65533.1035 | 139231.0069 | 54835 | 189180.75 | 76769 | 4935.15 | 25361.1875 | 8760 | 1475.3019 | 11471.8151 | 3834.5835 | 14436.1304 | 0 | 0 | 0 | -1276.9789 | 0 | 2366.2117 | 8760 | 3256.6475 | 0 | 0 | 3258.3629 | 13697.5815 | 5870.7841 | 11319.6676 | 6061.6893 | 1858.9093 | 9767.3409 | 8760 | 14114.8746 | 548.35 | 0 | 1048.625 | 1048929.1313 | 189624.8638 | 374.2
385 | E | SOR | TOU | CC | FP | WC | R60 | 4.0765 | 24 | 0.6 | 8760 | 160234.737 | 164357.1 | 170143.4127 | 65533.1035 | 139231.0069 | 55055 | 189939.75 | 77077 | 4954.95 | 25462.9375 | 8760 | 1475.3019 | 9911.2038 | 4446.2058 | 15363.7836 | 0 | 0 | 0 | -1254.649 | 0 | 2356.5396 | 8760 | 3256.9126 | 0 | 0 | 3258.3629 | 13697.5815 | 5819.1243 | 11332.0855 | 6042.3514 | 1843.7936 | 8273.0818 | 8760 | 14141.4698 | 550.55 | 0 | 1048.625 | 1048939.3476 | 189624.8638 | 296.95
386 | E | SOR | TOU | CC | FP | WC | R60 | 4.0765 | 17.5 | 0.45 | 8760 | 156631.9778 | 176862.15 | 177090.1996 | 65533.1035 | 139231.0069 | 55360 | 190992 | 77504 | 4982.4 | 25604 | 8760 | 1475.3019 | 8207.5175 | 5323.9083 | 16117.0853 | 0 | 0 | 0 | -1260.207 | 0 | 2312.4523 | 8760 | 3257.1797 | 0 | 0 | 3258.3629 | 13697.5815 | 5746.4074 | 11352.9233 | 6019.7291 | 1819.7187 | 6684.2869 | 8760 | 14173.6035 | 553.6 | 0 | 1048.625 | 1048926.8851 | 189624.8638 | 209.35
387 | E | SOR | TOU | FC | ET | HC | OFF0 | 0.11424 | 13 | 1 | 8760 | 160664.5613 | 32350.05 | 96811.0519 | 0 | 67726.415 | 62092.5 | 173859 | 86929.5 | 5588.325 | 366096.9427 | 8760 | 1475.304 | 7477.9724 | 2003.0849 | 644.2007 | 0 | 0 | 0 | -1476.3207 | 0 | 2847.4234 | 8760 | 1779.1582 | 0 | 0 | 1780.4022 | 1192.337 | 0 | 6439.2391 | 4886.9498 | 0 | 5436.9654 | 8760 | 0 | 620.925 | 0 | 1821 | 629109.4662 | 155421.1443 | 257.9 | -349.3632
388 | E | SOR | TOU | FC | ET | HC | OFF0 | 0.11424 | 11 | 0.85 | 8760 | 161709.2064 | 40404.15 | 101285.2536 | 0 | 67726.415 | 62722.5 | 175623 | 87811.5 | 5645.025 | 370054.7803 | 8760 | 1475.304 | 6697.8824 | 2520.4615 | 791.6068 | 0 | 0 | 0 | -1436.5642 | 0 | 2788.0391 | 8760 | 1779.4989 | 0 | 0 | 1780.4022 | 1192.337 | 0 | 6420.5893 | 4858.7666 | 0 | 4751.848 | 8760 | 0 | 627.225 | 0 | 1821 | 629302.8214 | 155421.1443 | 194.4 | -347.9103
389 | E | SOR | TOU | FC | ET | HC | OFF0 | 0.11424 | 9 | 0.7 | 8760 | 162224.8501 | 50450.85 | 106866.3815 | 0 | 67726.415 | 63365 | 177422 | 88711 | 5702.85 | 373365.4676 | 8760 | 1475.304 | 5782.2044 | 3119.6044 | 988.6867 | 0 | 0 | 0 | -1395.8389 | 0 | 2721.1236 | 8760 | 1778.9693 | 0 | 0 | 1780.4022 | 1192.337 | 0 | 6430.1449 | 4833.0926 | 0 | 3936.5558 | 8760 | 0 | 633.65 | 0 | 1821 | 629255.8442 | 155421.1443 | 134.85 | -335.9751
390 | E | SOR | TOU | FC | ET | HC | OFF0 | 0.11424 | 7 | 0.55 | 8760 | 161957.2039 | 62595.45 | 113612.9317 | 0 | 67726.415 | 63697.5 | 178353 | 89176.5 | 5732.775 | 374856.9523 | 8760 | 1475.304 | 4721.3963 | 3846.4296 | 1239.5773 | 0 | 0 | 0 | -1366.331 | 0 | 2644.6665 | 8760 | 1776.7336 | 0 | 0 | 1780.4022 | 1192.337 | 0 | 6424.5161 | 4809.9266 | 0 | 2983.2165 | 8760 | 0 | 636.975 | 0 | 1821 | 629320.0633 | 155421.1443 | 78.55 | -330.6621
391 | E | SOR | TOU | FC | ET | HC | OFF0 | 0.11424 | 5 | 0.4 | 8760 | 161084.2601 | 74987.1 | 120496.7227 | 0 | 67726.415 | 63825 | 178710 | 89355 | 5744.25 | 375659.5462 | 8760 | 1475.304 | 3548.8613 | 4578.1849 | 1485.8862 | 0 | 0 | 0 | -1357.0745 | 0 | 2496.3608 | 8760 | 1776.1286 | 0 | 0 | 1780.4022 | 1192.337 | 0 | 6416.4817 | 4801.6224 | 0 | 1992.6464 | 8760 | 0 | 638.25 | 0 | 1821 | 629376.8308 | 155421.1443 | 16.475 | -328.5751
392 | E | SOR | TOU | FC | ET | HC | OFF0 | 0.11424 | 13 | 0.65 | 8760 | 158023.0715 | 36439.2 | 99082.6504 | 0 | 67726.415 | 61900 | 173320 | 86660 | 5571 | 364758.9982 | 8760 | 1475.304 | 7306.6849 | 2146.399 | 753.7243 | 0 | 0 | 0 | -1484.4543 | 0 | 2877.0134 | 8760 | 1779.6601 | 0 | 0 | 1780.4022 | 1192.337 | 0 | 6440.8284 | 4902.0329 | 0 | 5238.8733 | 8760 | 0 | 619 | 0 | 1821 | 629162.7681 | 155421.1443 | 287.5 | -352.8218
393 | E | SOR | TOU | FC | ET | HC | OFF0 | 0.11424 | 11 | 0.55 | 8760 | 159174.6061 | 45334.35 | 104024.071 | 0 | 67726.415 | 62462.5 | 174895 | 87447.5 | 5621.625 | 367843.8215 | 8760 | 1475.304 | 6538.6988 | 2649.5884 | 937.4258 | 0 | 0 | 0 | -1455.7521 | 0 | 2833.6889 | 8760 | 1778.293 | 0 | 0 | 1780.4022 | 1192.337 | 0 | 6451.2564 | 4866.9393 | 0 | 4548.7194 | 8760 | 0 | 624.625 | 0 | 1821 | 629290.6671 | 155421.1443 | 220.3 | -337.122
394 | E | SOR | TOU | FC | ET | HC | OFF0 | 0.11424 | 9 | 0.45 | 8760 | 160000.0938 | 54796.5 | 109280.4705 | 0 | 67726.415 | 62997.5 | 176393 | 88196.5 | 5669.775 | 370885.9142 | 8760 | 1475.304 | 5655.608 | 3253.4824 | 1101.2218 | 0 | 0 | 0 | -1442.2082 | 0 | 2755.4026 | 8760 | 1778.0971 | 0 | 0 | 1780.4022 | 1192.337 | 0 | 6453.0901 | 4845.883 | 0 | 3774.0733 | 8760 | 0 | 629.975 | 0 | 1821 | 629153.3973 | 155421.1443 | 166.275 | -336.6417
395 | E | SOR | TOU | FC | ET | HC | OFF0 | 0.11424 | 7 | 0.35 | 8760 | 159960.5831 | 68288.4 | 116775.4708 | 0 | 67726.415 | 63275 | 177170 | 88585 | 5694.75 | 372386.5197 | 8760 | 1475.304 | 4619.4669 | 3947.5841 | 1379.8185 | 0 | 0 | 0 | -1436.4545 | 0 | 2709.476 | 8760 | 1777.0593 | 0 | 0 | 1780.4022 | 1192.337 | 0 | 6449.5698 | 4828.1057 | 0 | 2820.0102 | 8760 | 0 | 632.75 | 0 | 1821 | 629345.4549 | 155421.1443 | 104.95 | -331.8557
396 | E | SOR | TOU | FC | ET | HC | OFF | 0.11424 | 5 | 0.25 | 8760 | 151622.7233 | 90830.7 | 129298.1359 | 0 | 67726.415 | 63367.5 | 177429 | 88714.5 | 5703.075 | 373811.7322 | 8760 | 1475.304 | 3295.5846 | 4835.2602 | 1933.9349 | 0 | 0 | 0 | -1473.3464 | 0 | 2786.9457 | 8760 | 1778.7552 | 0 | 0 | 1780.4022 | 1192.337 | 0 | 6421.517 | 4831.5883 | 0 | 1445.5534 | 8760 | 0 | 633.675 | 0 | 1821 | 629322.3427 | 155421.1443 | 32.175 | -345.7769
397 | E | SOR | TOU | FC | ET | HC | OFF | 0.11424 | 13 | 0.35 | 8760 | 151661.6312 | 47467.35 | 105208.992 | 0 | 67726.415 | 61325 | 171710 | 85855 | 5519.25 | 361942.7316 | 8760 | 1475.304 | 6878.4602 | 2456.7594 | 1027.1617 | 0 | 0 | 0 | -1528.3289 | 0 | 2963.8594 | 8760 | 1779.5575 | 0 | 0 | 1780.4022 | 1192.337 | 0 | 6488.1327 | 4919.0716 | 0 | 4741.7543 | 8760 | 0 | 613.25 | 0 | 1821 | 629237.518 | 155421.1443 | 364.175 | -349.8662
398 | E | SOR | TOU | FC | ET | HC | OFF | 0.11424 | 11 | 0.3 | 8760 | 152912.9962 | 57279.15 | 110659.6286 | 0 | 67726.415 | 61810 | 173068 | 86534 | 5562.9 | 365125.2549 | 8760 | 1475.304 | 6148.1482 | 2955.1413 | 1241.4793 | 0 | 0 | 0 | -1523.3371 | 0 | 2948.4174 | 8760 | 1779.4864 | 0 | 0 | 1780.4022 | 1192.337 | 0 | 6455.9198 | 4895.0687 | 0 | 4056.493 | 8760 | 0 | 618.1 | 0 | 1821 | 629246.9393 | 155421.1443 | 299.2 | -351.0822
399 | E | SOR | TOU | FC | ET | HC | OFF | 0.11424 | 7 | 0.2 | 8760 | 150469.3343 | 72121.05 | 118904.5789 | 0 | 67726.415 | 62272.5 | 174363 | 87181.5 | 5604.525 | 367745.9363 | 8760 | 1475.304 | 5178.7832 | 3560.6237 | 1635.5382 | 0 | 0 | 0 | -1544.6774 | 0 | 3006.4688 | 8760 | 1779.8613 | 0 | 0 | 1780.4022 | 1192.337 | 0 | 6468.6015 | 4879.2059 | 0 | 3061.5212 | 8760 | 0 | 622.725 | 0 | 1821 | 629448.3837 | 155421.1443 | 236.4 | -351.6032
400 | E | SOR | TOU | FC | ET | HC | R100 | 0.9912 | 13 | 1 | 8760 | 154281.516 | 123009.3 | 147173.9441 | 65533.1035 | 121012.2992 | 27840 | 77952 | 38976 | 2505.6 | 163135.516 | 8760 | 1482.4089 | 7397.9675 | 1078.3409 | 5891.731 | 0 | 0 | 0 | -1283.621 | 0 | 2700.6531 | 8760 | 785.1982 | 0 | 0 | 790.1071 | 6319.9461 | 1763.4198 | 2862.8412 | 2163.0856 | 636.7884 | 5580.9412 | 8760 | 0 | 278.4 | 0 | 1024.225 | 277902.6241 | 210834.9497 | 337.2 | 242.376
401 | E | SOR | TOU | FC | ET | HC | R100 | 0.9912 | 11 | 0.85 | 8760 | 156950.1778 | 132112.35 | 152230.857 | 65533.1035 | 121012.2992 | 28112.5 | 78715 | 39357.5 | 2530.125 | 164301.7434 | 8760 | 1482.4089 | 6693.8804 | 1291.83 | 6277.3537 | 0 | 0 | 0 | -1251.8016 | 0 | 2637.7487 | 8760 | 784.0101 | 0 | 0 | 790.1071 | 6319.9461 | 1763.4302 | 2860.6973 | 2147.8048 | 636.8454 | 4974.7749 | 8760 | 0 | 281.125 | 0 | 1024.225 | 277896.6122 | 210834.9497 | 253.85 | 255.8158
402 | E | SOR | TOU | FC | ET | HC | R100 | 0.9912 | 9 | 0.7 | 8760 | 159711.8442 | 142585.65 | 158048.9691 | 65533.1035 | 121012.2992 | 28235 | 79058 | 39529 | 2541.15 | 164837.4935 | 8760 | 1482.4089 | 5859.5576 | 1552.0737 | 6760.3134 | 0 | 0 | 0 | -1220.8239 | 0 | 2572.6965 | 8760 | 783.2107 | 0 | 0 | 790.1071 | 6319.9461 | 1762.5575 | 2857.8491 | 2137.4451 | 636.8788 | 4240.1748 | 8760 | 0 | 282.35 | 0 | 1024.225 | 277843.5468 | 210834.9497 | 169.225 | 261.3457
403 | E | SOR | TOU | FC | ET | HC | R100 | 0.9912 | 7 | 0.55 | 8760 | 162074.336 | 155812.95 | 165396.9792 | 65533.1035 | 121012.2992 | 28465 | 79702 | 39851 | 2561.85 | 166360.092 | 8760 | 1482.4089 | 4874.6263 | 1879.0545 | 7320.9722 | 0 | 0 | 0 | -1192.2365 | 0 | 2478.5921 | 8760 | 783.9197 | 0 | 0 | 790.1071 | 6319.9461 | 1761.9086 | 2847.2579 | 2136.3831 | 636.8534 | 3383.3402 | 8760 | 0 | 284.65 | 0 | 1024.225 | 277819.899 | 210834.9497 | 85.65 | 251.1805
404 | E | SOR | TOU | FC | ET | HC | R100 | 0.9912 | 5 | 0.4 | 8760 | 162285.0848 | 170405.1 | 173503.1887 | 65533.1035 | 121012.2992 | 28520 | 79856 | 39928 | 2566.8 | 166562.7365 | 8760 | 1482.4089 | 3702.0778 | 2327.9328 | 7872.6205 | 0 | 0 | 0 | -1204.8895 | 0 | 2266.038 | 8760 | 783.8191 | 0 | 0 | 790.1071 | 6319.9461 | 1761.0955 | 2859.0603 | 2132.2431 | 636.4484 | 2453.6523 | 8760 | 0 | 285.2 | 0 | 1024.225 | 277816.5728 | 210834.9497 | 18.65 | 273.9179
405 | E | SOR | TOU | FC | ET | HC | R100 | 0.9912 | 13 | 0.65
406 | E | SOR | TOU | FC | ET | HC | R600 | 1.1319 | 13 | 1 | 8760 | 153717.2729 | 94220.55 | 131181.2604 | 65533.1035 | 89289.5943 | 33525 | 93870 | 46935 | 3017.25 | 197720.137 | 8760 | 1475.3019 | 7260.6849 | 1343.9805 | 3775.3353 | 0 | 0 | 0 | -1346.124 | 0 | 2672.8499 | 8760 | 967.0134 | 0 | 0 | 970.2131 | 3803.496 | 2009.3031 | 3713.9108 | 2626.9104 | 821.6273 | 5377.2768 | 8760 | 0 | 335.25 | 0 | 1166.025 | 337556.2092 | 189624.8638 | 340.775 | 680.433
407 | E | SOR | TOU | FC | ET | HC | R600 | 1.1319 | 11 | 0.85 | 8760 | 156874.1335 | 103381.65 | 136270.4211 | 65533.1035 | 89289.5943 | 33742.5 | 94479 | 47239.5 | 3036.825 | 197970.4799 | 8760 | 1475.3019 | 6593.2626 | 1631.8027 | 4099.3792 | 0 | 0 | 0 | -1319.0891 | 0 | 2616.3169 | 8760 | 963.9616 | 0 | 0 | 970.2131 | 3803.496 | 2008.9493 | 3706.8898 | 2605.1361 | 821.6324 | 4801.7471 | 8760 | 0 | 337.425 | 0 | 1166.025 | 337450.3621 | 189624.8638 | 255.1 | 678.6083
408 | E | SOR | TOU | FC | ET | HC | R600 | 1.1319 | 9 | 0.7 | 8760 | 160195.6534 | 112731.75 | 141464.5748 | 65533.1035 | 89289.5943 | 33892.5 | 94899 | 47449.5 | 3050.325 | 198560.839 | 8760 | 1475.3019 | 5806.5992 | 1923.3339 | 4455.0102 | 0 | 0 | 0 | -1282.2376 | 0 | 2538.8594 | 8760 | 962.4389 | 0 | 0 | 970.2131 | 3803.496 | 2008.3317 | 3709.027 | 2589.7293 | 821.5912 | 4127.1907 | 8760 | 0 | 338.925 | 0 | 1166.025 | 337528.3136 | 189624.8638 | 165.025 | 700.0243
409 | E | SOR | TOU | FC | ET | HC | R600 | 1.1319 | 7 | 0.55 | 8760 | 162494.6275 | 124622.55 | 148070.1344 | 65533.1035 | 89289.5943 | 34055 | 95354 | 47677 | 3064.95 | 199267.4524 | 8760 | 1475.3019 | 4840.8427 | 2325.744 | 4875.9862 | 0 | 0 | 0 | -1234.8855 | 0 | 2424.8164 | 8760 | 961.8552 | 0 | 0 | 970.2131 | 3803.496 | 2007.0473 | 3706.6387 | 2581.3135 | 820.9618 | 3309.4659 | 8760 | 0 | 340.55 | 0 | 1166.025 | 337477.8294 | 189624.8638 | 79.9 | 703.7743
410 | E | SOR | TOU | FC | ET | HC | R600 | 1.1319 | 13 | 0.65 | 8760 | 162382.1399 | 137173.5 | 155042.4195 | 65533.1035 | 89289.5943 | 34132.5 | 95571 | 47785.5 | 3071.925 | 200392.8019 | 8760 | 1475.3019 | 3674.0143 | 2884.679 | 5275.7794 | 0 | 0 | 0 | -1220.5876 | 0 | 2201.113 | 8760 | 964.8669 | 0 | 0 | 970.2131 | 3803.496 | 2003.422 | 3718.6223 | 2591.3606 | 819.406 | 2396.7081 | 8760 | 0 | 341.325 | 0 | 1166.025 | 337530.9566 | 189624.8638 | 15.175 | 722.6026
411 | E | SOR | TOU | FC | ET | WC | OFF0 | 0.22447 | 25.5 | 1.9 | 8760 | 160784.8547 | 27237.6 | 93970.9912 | 0 | 73058.5349 | 90687.5 | 312871.875 | 126962.5 | 8161.875 | 335543.75 | 8760 | 1475.304 | 13339.7442 | 1684.0748 | 469.9851 | 0 | 0 | 0 | -1546.1107 | 0 | 2946.9181 | 8760 | 3499.2165 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 28316.5689 | 8863.3911 | 0 | 11040.5246 | 8760 | 38486.3975 | 906.875 | 0 | 1821 | 1266667.4458 | 155421.1443 | 617.775
412 | E | SOR | TOU | FC | ET | WC | OFF0 | 0.22447 | 21.5 | 1.6 | 8760 | 161053.1561 | 38672.1 | 100323.0677 | 0 | 73058.5349 | 92182.5 | 318029.625 | 129055.5 | 8296.425 | 341075.25 | 8760 | 1475.304 | 12246.5885 | 2304.0541 | 705.6399 | 0 | 0 | 0 | -1506.6107 | 0 | 2923.7646 | 8760 | 3499.2979 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 28584.2309 | 8789.0375 | 0 | 10016.1536 | 8760 | 38908.9064 | 921.825 | 0 | 1821 | 1267118.1004 | 155421.1443 | 517
413 | E | SOR | TOU | FC | ET | WC | OFF0 | 0.22447 | 18 | 1.35 | 8760 | 161400.1976 | 51213.6 | 107290.1032 | 0 | 73058.5349 | 93595 | 322902.75 | 131033 | 8423.55 | 346301.5 | 8760 | 1475.304 | 11063.0421 | 3189.1199 | 910.6764 | 0 | 0 | 0 | -1470.3679 | 0 | 2892.8578 | 8760 | 3498.511 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 28867.369 | 8719.4799 | 0 | 8912.1049 | 8760 | 39352.0146 | 935.95 | 0 | 1821 | 1267194.168 | 155421.1443 | 417.825
414 | E | SOR | TOU | FC | ET | WC | OFF0 | 0.22447 | 14 | 1.05 | 8760 | 161423.8253 | 68044.05 | 116639.7299 | 0 | 73058.5349 | 94920 | 327474 | 132888 | 8542.8 | 351204 | 8760 | 1475.304 | 9365.3936 | 4330.087 | 1191.9744 | 0 | 0 | 0 | -1418.3394 | 0 | 2837.7007 | 8760 | 3498.9292 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 29103.3108 | 8655.9749 | 0 | 7333.4815 | 8760 | 39742.6185 | 949.2 | 0 | 1821 | 1266976.7121 | 155421.1443 | 302.05
415 | E | SOR | TOU | FC | ET | WC | OFF0 | 0.22447 | 10 | 0.75 | 8760 | 161073.5069 | 89075.7 | 128323.2009 | 0 | 73058.5349 | 95947.5 | 331018.875 | 134326.5 | 8635.275 | 355005.75 | 8760 | 1475.304 | 7283.8704 | 5771.0642 | 1586.3443 | 0 | 0 | 0 | -1358.7354 | 0 | 2751.4563 | 8760 | 3498.9766 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 29319.6662 | 8603.8332 | 0 | 5404.6393 | 8760 | 40060.1477 | 959.475 | 0 | 1821 | 1267252.3584 | 155421.1443 | 189.8
416 | E | SOR | TOU | FC | ET | WC | OFF0 | 0.22447 | 25.5 | 1.3 | 8760 | 158503.9673 | 31452.3 | 96312.3351 | 0 | 73058.5349 | 90742.5 | 313061.625 | 127039.5 | 8166.825 | 335747.25 | 8760 | 1475.304 | 13082.0815 | 1838.1897 | 584.7664 | 0 | 0 | 0 | -1541.1221 | 0 | 2965.8169 | 8760 | 3498.8966 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 28355.3463 | 8865.7071 | 0 | 10771.5868 | 8760 | 38515.4656 | 907.425 | 0 | 1821 | 1266688.6897 | 155421.1443 | 639.225
417 | E | SOR | TOU | FC | ET | WC | OFF0 | 0.22447 | 21.5 | 1.1 | 8760 | 158846.4259 | 42805.8 | 102619.4146 | 0 | 73058.5349 | 92080 | 317676 | 128912 | 8287.2 | 340696 | 8760 | 1475.304 | 12014.5665 | 2461.5292 | 807.2339 | 0 | 0 | 0 | -1505.5316 | 0 | 2944.8905 | 8760 | 3498.2839 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 28586.6408 | 8795.5484 | 0 | 9774.2827 | 8760 | 38896.6492 | 920.8 | 0 | 1821 | 1266971.7212 | 155421.1443 | 540.65
418 | E | SOR | TOU | FC | ET | WC | OFF0 | 0.22447 | 18 | 0.9 | 8760 | 158927.8356 | 55996.65 | 109947.1761 | 0 | 73058.5349 | 93285 | 321833.25 | 130599 | 8395.65 | 345154.5 | 8760 | 1475.304 | 10828.4806 | 3303.4492 | 1014.9374 | 0 | 0 | 0 | -1472.16 | 0 | 2921.1518 | 8760 | 3498.9486 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 28813.8196 | 8738.4233 | 0 | 8664.1921 | 8760 | 39264.0232 | 932.85 | 0 | 1821 | 1267151.3474 | 155421.1443 | 445.7
419 | E | SOR | TOU | FC | ET | WC | OFF0 | 0.22447 | 14 | 0.7 | 8760 | 159180.9135 | 73215.9 | 119512.7883 | 0 | 73058.5349 | 94547.5 | 326188.875 | 132366.5 | 8509.275 | 349825.75 | 8760 | 1475.304 | 9177.7455 | 4499.0181 | 1317.2525 | 0 | 0 | 0 | -1432.3273 | 0 | 2877.8379 | 8760 | 3498.9596 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 29053.4002 | 8674.3289 | 0 | 7120.0019 | 8760 | 39644.8154 | 945.475 | 0 | 1821 | 1267006.735 | 155421.1443 | 326.35
420 | E | SOR | TOU | FC | ET | WC | OFF | 0.22447 | 10 | 0.5 | 8760 | 159281.2552 | 93457.8 | 130757.5386 | 0 | 73058.5349 | 95637.5 | 329949.375 | 133892.5 | 8607.375 | 353858.75 | 8760 | 1475.304 | 7166.734 | 5889.1987 | 1683.9398 | 0 | 0 | 0 | -1406.5502 | 0 | 2785.6023 | 8760 | 3498.5054 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 29258.4425 | 8615.7522 | 0 | 5258.038 | 8760 | 39977.0311 | 956.375 | 0 | 1821 | 1267344.2454 | 155421.1443 | 214.875
421 | E | SOR | TOU | FC | ET | WC | OFF | 0.22447 | 25.5 | 0.65 | 8760 | 151731.7789 | 43595.55 | 103058.1354 | 0 | 73058.5349 | 90470 | 312121.5 | 126658 | 8142.3 | 334739 | 8760 | 1475.304 | 12355.9956 | 2345.0902 | 863.8659 | 0 | 0 | 0 | -1527.7148 | 0 | 3021.1452 | 8760 | 3498.2779 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 28313.2222 | 8883.9833 | 0 | 10019.3264 | 8760 | 38454.7193 | 904.7 | 0 | 1821 | 1266742.4171 | 155421.1443 | 705.05
422 | E | SOR | TOU | FC | ET | WC | OFF | 0.22447 | 21.5 | 0.55 | 8760 | 152292.3638 | 54796.5 | 109280.4705 | 0 | 73058.5349 | 91510 | 315709.5 | 128114 | 8235.9 | 338587 | 8760 | 1475.304 | 11355.187 | 2868.5262 | 1106.6214 | 0 | 0 | 0 | -1507.4892 | 0 | 3014.6086 | 8760 | 3498.5193 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 28486.4614 | 8827.2414 | 0 | 9075.2994 | 8760 | 38742.457 | 915.1 | 0 | 1821 | 1266882.1857 | 155421.1443 | 612.525
423 | E | SOR | TOU | FC | ET | WC | OFF | 0.22447 | 18 | 0.45 | 8760 | 152534.1927 | 67390.65 | 116276.7541 | 0 | 73058.5349 | 92567.5 | 319357.875 | 129594.5 | 8331.075 | 342499.75 | 8760 | 1475.304 | 10237.3485 | 3583.386 | 1301.1751 | 0 | 0 | 0 | -1500.2521 | 0 | 2993.7364 | 8760 | 3498.9601 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 28671.0344 | 8772.0574 | 0 | 8030.7179 | 8760 | 39052.4069 | 925.675 | 0 | 1821 | 1266746.3731 | 155421.1443 | 521.275
424 | E | SOR | TOU | FC | ET | WC | OFF | 0.22447 | 14 | 0.35 | 8760 | 153133.9258 | 85954.5 | 126589.3165 | 0 | 73058.5349 | 93797.5 | 323601.375 | 131316.5 | 8441.775 | 347050.75 | 8760 | 1475.304 | 8678.921 | 4662.438 | 1607.6681 | 0 | 0 | 0 | -1491.8574 | 0 | 2983.4834 | 8760 | 3498.9227 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 28918.5454 | 8707.1134 | 0 | 6542.5689 | 8760 | 39438.8439 | 937.975 | 0 | 1821 | 1266985.9053 | 155421.1443 | 402.225
425 | E | SOR | TOU | FC | ET | WC | OFF | 0.22447 | 10 | 0.25 | 8760 | 150481.177 | 112815.45 | 141511.0717 | 0 | 73058.5349 | 94710 | 326749.5 | 132594 | 8523.9 | 350427 | 8760 | 1475.304 | 6585.441 | 6065.3325 | 2397.6535 | 0 | 0 | 0 | -1531.1091 | 0 | 3060.5602 | 8760 | 3498.9032 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 29101.5256 | 8655.6429 | 0 | 4419.3283 | 8760 | 39718.6795 | 947.1 | 0 | 1821 | 1267162.7668 | 155421.1443 | 290.875
426 | E | SOR | TOU | FC | ET | WC | R100 | 1.9476 | 25.5 | 1.9 | 8760 | 165096.4108 | 133753.95 | 153142.7962 | 65533.1035 | 151897.8787 | 41157.5 | 141993.375 | 57620.5 | 3704.175 | 19035.3438 | 8760 | 1482.4089 | 12355.8364 | 1417.8658 | 10242.4116 | 0 | 0 | 0 | -1291.6937 | 0 | 2749.8016 | 8760 | 1551.2535 | 0 | 0 | 1552.4644 | 12417.9257 | 3322.8953 | 7187.1017 | 3925.4006 | 1242.7992 | 10389.1895 | 8760 | 9264.9021 | 411.575 | 0 | 1024.225 | 559101.6747 | 210834.9497 | 570.55
427 | E | SOR | TOU | FC | ET | WC | R100 | 1.9476 | 21.5 | 1.6 | 8760 | 164996.1627 | 143874.9 | 158765.1713 | 65533.1035 | 151897.8787 | 41550 | 143347.5 | 58170 | 3739.5 | 19216.875 | 8760 | 1482.4089 | 11285.8043 | 1710.0483 | 11019.3105 | 0 | 0 | 0 | -1262.9728 | 0 | 2717.7503 | 8760 | 1552.2682 | 0 | 0 | 1552.4644 | 12417.9257 | 3319.1974 | 7226.1714 | 3907.8266 | 1242.3512 | 9392.5171 | 8760 | 9322.5464 | 415.5 | 0 | 1024.225 | 559168.3735 | 210834.9497 | 465.7
428 | E | SOR | TOU | FC | ET | WC | R100 | 1.9476 | 18 | 1.35 | 8760 | 165371.9084 | 152953.65 | 163808.5851 | 65533.1035 | 151897.8787 | 42000 | 144900 | 58800 | 3780 | 19425 | 8760 | 1482.4089 | 10191.8753 | 2028.0501 | 11670.82 | 0 | 0 | 0 | -1227.2767 | 0 | 2670.3225 | 8760 | 1551.8455 | 0 | 0 | 1552.4644 | 12417.9257 | 3309.62 | 7266.1215 | 3883.4052 | 1241.2969 | 8387.1293 | 8760 | 9382.6137 | 420 | 0 | 1024.225 | 559230.2501 | 210834.9497 | 366.225
429 | E | SOR | TOU | FC | ET | WC | R100 | 1.9476 | 14 | 1.05 | 8760 | 165988.9782 | 166194.45 | 171164.0947 | 65533.1035 | 151897.8787 | 42430 | 146383.5 | 59402 | 3818.7 | 19623.875 | 8760 | 1482.4089 | 8671.3594 | 2518.0177 | 12504.7413 | 0 | 0 | 0 | -1182.3541 | 0 | 2592.1528 | 8760 | 1552.2158 | 0 | 0 | 1552.4644 | 12417.9257 | 3293.3097 | 7314.1371 | 3864.3412 | 1240.2691 | 6999.9757 | 8760 | 9450.0853 | 424.3 | 0 | 1024.225 | 559352.4122 | 210834.9497 | 244.25
430 | E | SOR | TOU | FC | ET | WC | R100 | 1.9476 | 10 | 0.75 | 8760 | 167672.4998 | 181558.8 | 179699.2756 | 65533.1035 | 151897.8787 | 42827.5 | 147754.875 | 59958.5 | 3854.475 | 19807.7188 | 8760 | 1482.4089 | 6853.2357 | 3095.9888 | 13521.9453 | 0 | 0 | 0 | -1135.853 | 0 | 2469.1744 | 8760 | 1551.8822 | 0 | 0 | 1552.4644 | 12417.9257 | 3277.0449 | 7349.0624 | 3843.2408 | 1236.685 | 5364.884 | 8760 | 9507.9086 | 428.275 | 0 | 1024.225 | 559261.4825 | 210834.9497 | 116.45
431 | E | SOR | TOU | FC | ET | WC | R100 | 1.9476 | 25.5 | 1.3 | 8760 | 161669.6635 | 134812.35 | 153730.757 | 65533.1035 | 151897.8787 | 41322.5 | 142562.625 | 57851.5 | 3719.025 | 19111.6562 | 8760 | 1482.4089 | 12014.286 | 1534.6102 | 10622.4769 | 0 | 0 | 0 | -1304.1846 | 0 | 2792.5378 | 8760 | 1552.7303 | 0 | 0 | 1552.4644 | 12417.9257 | 3326.4164 | 7220.1869 | 3924.8496 | 1242.5735 | 10000.9068 | 8760 | 9293.3238 | 413.225 | 0 | 1024.225 | 559249.8374 | 210834.9497 | 608.025
432 | E | SOR | TOU | FC | ET | WC | R100 | 1.9476 | 21.5 | 1.1 | 8760 | 161906.2616 | 144509.4 | 159117.6478 | 65533.1035 | 151897.8787 | 41667.5 | 143752.875 | 58334.5 | 3750.075 | 19271.2188 | 8760 | 1482.4089 | 11000.8268 | 1807.3582 | 11237.8219 | 0 | 0 | 0 | -1278.0461 | 0 | 2762.3176 | 8760 | 1552.3497 | 0 | 0 | 1552.4644 | 12417.9257 | 3319.1146 | 7240.8761 | 3903.2595 | 1241.6597 | 9060.8694 | 8760 | 9340.719 | 416.675 | 0 | 1024.225 | 559177.856 | 210834.9497 | 501.625
433 | E | SOR | TOU | FC | ET | WC | R100 | 1.9476 | 18 | 0.9 | 8760 | 161675.5482 | 154936.8 | 164910.2616 | 65533.1035 | 151897.8787 | 42052.5 | 145081.125 | 58873.5 | 3784.725 | 19449.2812 | 8760 | 1482.4089 | 9890.8861 | 2144.1939 | 11897.5319 | 0 | 0 | 0 | -1252.5632 | 0 | 2727.5933 | 8760 | 1552.1259 | 0 | 0 | 1552.4644 | 12417.9257 | 3308.9177 | 7275.4807 | 3882.737 | 1240.5773 | 8027.7812 | 8760 | 9395.9699 | 420.525 | 0 | 1024.225 | 559209.6503 | 210834.9497 | 410.475
434 | E | SOR | TOU | FC | ET | WC | R100 | 1.9476 | 14 | 0.7 | 8760 | 162787.3675 | 168153.3 | 172252.2721 | 65533.1035 | 151897.8787 | 42385 | 146228.25 | 59339 | 3814.65 | 19603.0625 | 8760 | 1482.4089 | 8424.4251 | 2643.3497 | 12771.8969 | 0 | 0 | 0 | -1227.619 | 0 | 2673.3294 | 8760 | 1551.8371 | 0 | 0 | 1552.4644 | 12417.9257 | 3297.525 | 7315.0294 | 3864.949 | 1239.7429 | 6671.3154 | 8760 | 9444.7294 | 423.85 | 0 | 1024.225 | 559308.8464 | 210834.9497 | 285.5
435 | E | SOR | TOU | FC | ET | WC | R10 | 1.9476 | 10 | 0.5 | 8760 | 164611.5781 | 184667.85 | 181426.4105 | 65533.1035 | 151897.8787 | 42742.5 | 147461.625 | 59839.5 | 3846.825 | 19768.4062 | 8760 | 1482.4089 | 6682.6664 | 3316.8074 | 13800.6702 | 0 | 0 | 0 | -1240.6357 | 0 | 2517.6776 | 8760 | 1551.5202 | 0 | 0 | 1552.4644 | 12417.9257 | 3281.6892 | 7340.9019 | 3845.8252 | 1235.4693 | 5141.5779 | 8760 | 9496.9351 | 427.425 | 0 | 1024.225 | 559246.8559 | 210834.9497 | 156.325
436 | E | SOR | TOU | FC | ET | WC | R10 | 1.9476 | 25.5 | 0.65 | 8760 | 151869.9847 | 144945.45 | 159359.8817 | 65533.1035 | 151897.8787 | 41245 | 142295.25 | 57743 | 3712.05 | 19075.8125 | 8760 | 1482.4089 | 11057.8133 | 1852.5946 | 11357.9354 | 0 | 0 | 0 | -1337.0215 | 0 | 2903.1525 | 8760 | 1551.4852 | 0 | 0 | 1552.4644 | 12417.9257 | 3318.4797 | 7220.4985 | 3927.0104 | 1241.5343 | 8943.0848 | 8760 | 9291.2211 | 412.45 | 0 | 1024.225 | 559059.972 | 210834.9497 | 710.9
437 | E | SOR | TOU | FC | ET | WC | R10 | 1.9476 | 21.5 | 0.55 | 8760 | 150909.2287 | 156510.9 | 165784.7033 | 65533.1035 | 151897.8787 | 41565 | 143399.25 | 58191 | 3740.85 | 19223.8125 | 8760 | 1482.4089 | 10005.9953 | 2141.4282 | 12137.0901 | 0 | 0 | 0 | -1331.2876 | 0 | 2897.8505 | 8760 | 1551.2597 | 0 | 0 | 1552.4644 | 12417.9257 | 3310.0408 | 7248.2598 | 3907.0463 | 1240.56 | 7938.0723 | 8760 | 9328.0743 | 415.65 | 0 | 1024.225 | 559181.2507 | 210834.9497 | 620.05
438 | E | SOR | TOU | FC | ET | WC | R10 | 1.9476 | 18 | 0.45 | 8760 | 150414.6553 | 167597.1 | 171943.2927 | 65533.1035 | 151897.8787 | 41850 | 144382.5 | 58590 | 3766.5 | 19355.625 | 8760 | 1482.4089 | 8981.4755 | 2495.9781 | 12802.6289 | 0 | 0 | 0 | -1352.9967 | 0 | 2840.3477 | 8760 | 1551.7158 | 0 | 0 | 1552.4644 | 12417.9257 | 3301.962 | 7272.1256 | 3892.2004 | 1239.298 | 7009.7352 | 8760 | 9368.7759 | 418.5 | 0 | 1024.225 | 559205.8256 | 210834.9497 | 534.65
439 | E | SOR | TOU | FC | ET | WC | R10 | 1.9476 | 14 | 0.35 | 8760 | 150833.8494 | 181437.3 | 179631.7801 | 65533.1035 | 151897.8787 | 42160 | 145452 | 59024 | 3794.4 | 19499 | 8760 | 1482.4089 | 7558.1676 | 3014.021 | 13858.8228 | 0 | 0 | 0 | -1376.3227 | 0 | 2834.3228 | 8760 | 1551.6469 | 0 | 0 | 1552.4644 | 12417.9257 | 3290.8457 | 7295.7481 | 3875.9034 | 1236.182 | 5644.049 | 8760 | 9412.9492 | 421.6 | 0 | 1024.225 | 559193.9989 | 210834.9497 | 420.725
440 | E | SOR | TOU | FC | ET | WC | R10 | 1.9476 | 10 | 0.25 | 8760 | 146983.5647 | 206822.7 | 193733.8399 | 65533.1035 | 151897.8787 | 42362.5 | 146150.625 | 59307.5 | 3812.625 | 19592.6562 | 8760 | 1482.4089 | 5583.6578 | 3851.9092 | 15360.3777 | 0 | 0 | 0 | -1468.8189 | 0 | 3037.4303 | 8760 | 1551.9103 | 0 | 0 | 1552.4644 | 12417.9257 | 3279.7811 | 7311.0994 | 3865.5666 | 1228.6264 | 3525.6086 | 8760 | 9442.1581 | 423.625 | 0 | 1024.225 | 559222.3869 | 210834.9497 | 315.7
441 | E | SOR | TOU | FC | ET | WC | R600 | 2.2241 | 25.5 | 1.9 | 8760 | 164346.1407 | 109096.2 | 139444.9594 | 65533.1035 | 107663.8091 | 51005 | 175967.25 | 71407 | 4590.45 | 23589.8125 | 8760 | 1475.3019 | 12065.5277 | 1793.9232 | 6272.4995 | 0 | 0 | 0 | -1362.7589 | 0 | 2724.714 | 8760 | 1905.936 | 0 | 0 | 1906.3509 | 7473.4072 | 3746.9139 | 9153.3634 | 4805.3776 | 1588.9312 | 10022.9796 | 8760 | 11615.1375 | 510.05 | 0 | 1166.025 | 678842.1178 | 189624.8638 | 579.45
442 | E | SOR | TOU | FC | ET | WC | R600 | 2.2241 | 21.5 | 1.6 | 8760 | 164164.2956 | 118543.5 | 144693.1095 | 65533.1035 | 107663.8091 | 51602.5 | 178028.625 | 72243.5 | 4644.225 | 23866.1562 | 8760 | 1475.3019 | 11026.0677 | 2160.4996 | 6828.3944 | 0 | 0 | 0 | -1330.8956 | 0 | 2696.3176 | 8760 | 1906.0232 | 0 | 0 | 1906.3509 | 7473.4072 | 3736.1551 | 9219.0019 | 4774.7621 | 1587.4509 | 9055.1451 | 8760 | 11699.8944 | 516.025 | 0 | 1166.025 | 678944.8535 | 189624.8638 | 475.375
443 | E | SOR | TOU | FC | ET | WC | R600 | 2.2241 | 18 | 1.35 | 8760 | 164528.24 | 128224.35 | 150071.001 | 65533.1035 | 107663.8091 | 52007.5 | 179425.875 | 72810.5 | 4680.675 | 24053.4688 | 8760 | 1475.3019 | 9961.3364 | 2600.2925 | 7383.2013 | 0 | 0 | 0 | -1301.7489 | 0 | 2659.533 | 8760 | 1906.3665 | 0 | 0 | 1906.3509 | 7473.4072 | 3727.0389 | 9253.9289 | 4755.968 | 1585.1529 | 8069.2702 | 8760 | 11759.4548 | 520.075 | 0 | 1166.025 | 679037.0236 | 189624.8638 | 374.75
444 | E | SOR | TOU | FC | ET | WC | R600 | 2.2241 | 14 | 1.05 | 8760 | 166503.7936 | 139707.45 | 156450.0757 | 65533.1035 | 107663.8091 | 52470 | 181021.5 | 73458 | 4722.3 | 24267.375 | 8760 | 1475.3019 | 8559.5849 | 3215.5767 | 8030.0461 | 0 | 0 | 0 | -1259.7488 | 0 | 2581.8205 | 8760 | 1905.2242 | 0 | 0 | 1906.3509 | 7473.4072 | 3712.8995 | 9305.8397 | 4728.5371 | 1581.6921 | 6802.2182 | 8760 | 11832.2761 | 524.7 | 0 | 1166.025 | 679062.9408 | 189624.8638 | 240.8
445 | E | SOR | TOU | FC | ET | WC | R600 | 2.2241 | 10 | 0.75 | 8760 | 167947.3169 | 154916.55 | 164899.0124 | 65533.1035 | 107663.8091 | 52915 | 182556.75 | 74081 | 4762.35 | 24473.1875 | 8760 | 1475.3019 | 6781.4567 | 3989.1531 | 8747.3551 | 0 | 0 | 0 | -1191.1404 | 0 | 2432.8032 | 8760 | 1906.5444 | 0 | 0 | 1906.3509 | 7473.4072 | 3677.9189 | 9356.176 | 4712.6823 | 1568.3646 | 5235.0063 | 8760 | 11904.8039 | 529.15 | 0 | 1166.025 | 679121.6951 | 189624.8638 | 112.875
446 | E | SOR | TOU | FC | ET | WC | R600 | 2.2241 | 25.5 | 1.3 | 8760 | 160598.0445 | 110982.15 | 140492.6396 | 65533.1035 | 107663.8091 | 51082.5 | 176234.625 | 71515.5 | 4597.425 | 23625.6562 | 8760 | 1475.3019 | 11701.9517 | 1966.3024 | 6615.3684 | 0 | 0 | 0 | -1372.9094 | 0 | 2761.974 | 8760 | 1906.3056 | 0 | 0 | 1906.3509 | 7473.4072 | 3746.5662 | 9171.9589 | 4805.9949 | 1587.5316 | 9619.725 | 8760 | 11633.9565 | 510.825 | 0 | 1166.025 | 678805.8727 | 189624.8638 | 617.725
447 | E | SOR | TOU | FC | ET | WC | R600 | 2.2241 | 21.5 | 1.1 | 8760 | 160643.3932 | 120233.7 | 145632.0469 | 65533.1035 | 107663.8091 | 51560 | 177882 | 72184 | 4640.4 | 23846.5 | 8760 | 1475.3019 | 10711.8053 | 2331.5972 | 7144.6586 | 0 | 0 | 0 | -1347.3758 | 0 | 2737.7913 | 8760 | 1905.9115 | 0 | 0 | 1906.3509 | 7473.4072 | 3737.7556 | 9211.049 | 4778.3314 | 1585.9963 | 8698.0207 | 8760 | 11691.8726 | 515.6 | 0 | 1166.025 | 678844.3519 | 189624.8638 | 512.975
448 | E | SOR | TOU | FC | ET | WC | R600 | 2.2241 | 18 | 0.9 | 8760 | 161126.2833 | 130063.05 | 151092.4329 | 65533.1035 | 107663.8091 | 51975 | 179313.75 | 72765 | 4677.75 | 24038.4375 | 8760 | 1475.3019 | 9686.8719 | 2748.1828 | 7648.6847 | 0 | 0 | 0 | -1323.4732 | 0 | 2707.3827 | 8760 | 1906.0824 | 0 | 0 | 1906.3509 | 7473.4072 | 3728.5326 | 9259.0666 | 4756.5162 | 1582.9975 | 7746.1748 | 8760 | 11757.9161 | 519.75 | 0 | 1166.025 | 678907.2649 | 189624.8638 | 414.1
449 | E | SOR | TOU | FC | ET | WC | R600 | 2.2241 | 14 | 0.7 | 8760 | 163191.7112 | 141836.4 | 157632.7468 | 65533.1035 | 107663.8091 | 52400 | 180780 | 73360 | 4716 | 24235 | 8760 | 1475.3019 | 8327.4501 | 3360.5401 | 8261.2137 | 0 | 0 | 0 | -1290.6481 | 0 | 2644.3319 | 8760 | 1905.4848 | 0 | 0 | 1906.3509 | 7473.4072 | 3712.881 | 9299.5969 | 4732.3862 | 1578.0828 | 6508.042 | 8760 | 11819.1486 | 524 | 0 | 1166.025 | 679057.4384 | 189624.8638 | 279
450 | E | SOR | TOU | FC | ET | WC | R60 | 2.2241 | 10 | 0.5 | 8760 | 165014.2377 | 158191.65 | 166718.3911 | 65533.1035 | 107663.8091 | 52795 | 182142.75 | 73913 | 4751.55 | 24417.6875 | 8760 | 1475.3019 | 6623.6777 | 4193.9935 | 8897.5512 | 0 | 0 | 0 | -1275.2337 | 0 | 2471.8685 | 8760 | 1906.4075 | 0 | 0 | 1906.3509 | 7473.4072 | 3677.5984 | 9338.9317 | 4717.3714 | 1562.5005 | 5036.3224 | 8760 | 11881.2456 | 527.95 | 0 | 1166.025 | 678995.4044 | 189624.8638 | 150.275
451 | E | SOR | TOU | FC | ET | WC | R60 | 2.2241 | 25.5 | 0.65 | 8760 | 151298.3049 | 119140.2 | 145024.5874 | 65533.1035 | 107663.8091 | 50967.5 | 175837.875 | 71354.5 | 4587.075 | 23572.4688 | 8760 | 1475.3019 | 10801.9661 | 2415.2893 | 7238.6928 | 0 | 0 | 0 | -1399.7968 | 0 | 2864.5143 | 8760 | 1906.4042 | 0 | 0 | 1906.3509 | 7473.4072 | 3742.1985 | 9184.3227 | 4815.3302 | 1583.9983 | 8629.7187 | 8760 | 11623.6748 | 509.675 | 0 | 1166.025 | 678878.6899 | 189624.8638 | 714.675
452 | E | SOR | TOU | FC | ET | WC | R60 | 2.2241 | 21.5 | 0.55 | 8760 | 151116.3977 | 129293.55 | 150664.9614 | 65533.1035 | 107663.8091 | 51332.5 | 177097.125 | 71865.5 | 4619.925 | 23741.2812 | 8760 | 1475.3019 | 9857.3095 | 2746.4978 | 7769.1292 | 0 | 0 | 0 | -1387.0276 | 0 | 2854.1522 | 8760 | 1905.5786 | 0 | 0 | 1906.3509 | 7473.4072 | 3731.0219 | 9209.161 | 4790.5434 | 1581.4188 | 7739.9092 | 8760 | 11670.9624 | 513.325 | 0 | 1166.025 | 678782.6545 | 189624.8638 | 619.2
453 | E | SOR | TOU | FC | ET | WC | R60 | 2.2241 | 18 | 0.45 | 8760 | 151217.4122 | 140799.6 | 157056.7852 | 65533.1035 | 107663.8091 | 51657.5 | 178218.375 | 72320.5 | 4649.175 | 23891.5938 | 8760 | 1475.3019 | 8911.3871 | 3202.7158 | 8222.2062 | 0 | 0 | 0 | -1396.9466 | 0 | 2795.517 | 8760 | 1905.3387 | 0 | 0 | 1906.3509 | 7473.4072 | 3715.7477 | 9241.3511 | 4770.4292 | 1575.8552 | 6894.666 | 8760 | 11713.0146 | 516.575 | 0 | 1166.025 | 678985.5215 | 189624.8638 | 529.775
454 | E | SOR | TOU | FC | ET | WC | R60 | 2.2241 | 14 | 0.35 | 8760 | 152124.297 | 154076.85 | 164432.5435 | 65533.1035 | 107663.8091 | 52072.5 | 179650.125 | 72901.5 | 4686.525 | 24083.5312 | 8760 | 1475.3019 | 7548.0236 | 3834.1982 | 8980.5668 | 0 | 0 | 0 | -1405.8379 | 0 | 2784.3678 | 8760 | 1905.864 | 0 | 0 | 1906.3509 | 7473.4072 | 3690.3626 | 9273.5878 | 4751.2471 | 1564.2681 | 5594.6868 | 8760 | 11773.4805 | 520.725 | 0 | 1166.025 | 678856.1731 | 189624.8638 | 409.4
455 | E | SOR | TOU | FC | ET | WC | R60 | 2.2241 | 10 | 0.25 | 8760 | 147430.8483 | 179568.9 | 178593.8493 | 65533.1035 | 107663.8091 | 52277.5 | 180357.375 | 73188.5 | 4704.975 | 24178.3438 | 8760 | 1475.3019 | 5551.9963 | 4862.6383 | 10222.1243 | 0 | 0 | 0 | -1481.6974 | 0 | 2972.5383 | 8760 | 1905.4088 | 0 | 0 | 1906.3509 | 7473.4072 | 3664.5702 | 9296.6584 | 4738.0004 | 1549.251 | 3467.3386 | 8760 | 11805.5322 | 522.775 | 0 | 1166.025 | 678940.9918 | 189624.8638 | 309.175
456 | E | SOR | TOU | FC | FP | HC | OFF0 | 0.11424 | 13 | 1
457 | E | SOR | TOU | FC | FP | HC | OFF0 | 0.11424 | 11 | 0.85 | 8760 | 137635.1585 | 48660.75 | 105871.9478 | 0 | 67726.415 | 63302.5 | 177247 | 88623.5 | 5697.225 | 371869.8148 | 8760 | 1475.304 | 5294.1755 | 3161.9556 | 923.0722 | 0 | 0 | 0 | -1382.7265 | 0 | 2211.9798 | 8760 | 1775.081 | 0 | 0 | 1780.4022 | 1192.337 | 0 | 6437.9628 | 4821.3383 | 0 | 3860.9433 | 8760 | 0 | 633.025 | 0 | 1821 | 629344.5216 | 155421.1443 | 73.05 | -320.2328
458 | E | SOR | TOU | FC | FP | HC | OFF0 | 0.11424 | 9 | 0.7
459 | E | SOR | TOU | FC | FP | HC | R100 | 0.9912 | 13 | 1 | 8760 | 147803.1192 | 129540.6 | 150802.2022 | 65533.1035 | 121012.2992 | 28140 | 78792 | 39396 | 2532.6 | 165512.7127 | 8760 | 1482.4089 | 6472.3287 | 1353.9183 | 6109.5482 | 0 | 0 | 0 | -1228.8337 | 0 | 2292.4085 | 8760 | 787.7636 | 0 | 0 | 790.1071 | 6319.9461 | 1763.4837 | 2856.1668 | 2160.3449 | 636.8344 | 5039.3567 | 8760 | 0 | 281.4 | 0 | 1024.225 | 277873.6018 | 210834.9497 | 149.125 | -327.584
460 | E | SOR | TOU | FC | FP | HC | R100 | 0.9912 | 11 | 0.85 | 8760 | 148866.8102 | 137691.9 | 155330.4003 | 65533.1035 | 121012.2992 | 28250 | 79100 | 39550 | 2542.5 | 165681.8525 | 8760 | 1482.4089 | 5854.9717 | 1559.5804 | 6470.6662 | 0 | 0 | 0 | -1202.1123 | 0 | 2262.7784 | 8760 | 785.9195 | 0 | 0 | 790.1071 | 6319.9461 | 1762.8508 | 2854.5444 | 2146.9658 | 636.8626 | 4484.7386 | 8760 | 0 | 282.5 | 0 | 1024.225 | 277904.1582 | 210834.9497 | 109.575 | -316.0441
461 | E | SOR | TOU | FC | FP | HC | R100 | 0.9912 | 9 | 0.7 | 8760 | 149609.9406 | 147542.85 | 160802.7855 | 65533.1035 | 121012.2992 | 28362.5 | 79415 | 39707.5 | 2552.625 | 166041.4253 | 8760 | 1482.4089 | 5113.3216 | 1785.1598 | 6921.7315 | 0 | 0 | 0 | -1173.0751 | 0 | 2228.5084 | 8760 | 784.8426 | 0 | 0 | 790.1071 | 6319.9461 | 1762.0558 | 2858.2848 | 2137.0976 | 636.8509 | 3809.3869 | 8760 | 0 | 283.625 | 0 | 1024.225 | 277974.18 | 210834.9497 | 73.5 | -304.8124
462 | E | SOR | TOU | FC | FP | HC | R100 | 0.9912 | 7 | 0.55 | 8760 | 149747.1729 | 160007.4 | 167727.0738 | 65533.1035 | 121012.2992 | 28477.5 | 79737 | 39868.5 | 2562.975 | 166776.6488 | 8760 | 1482.4089 | 4254.4941 | 2058.8561 | 7473.2201 | 0 | 0 | 0 | -1149.3149 | 0 | 2176.4704 | 8760 | 785.6336 | 0 | 0 | 790.1071 | 6319.9461 | 1761.9364 | 2855.0797 | 2136.2572 | 636.8219 | 3031.6007 | 8760 | 0 | 284.775 | 0 | 1024.225 | 277872.895 | 210834.9497 | 39.675 | -309.8295
463 | E | SOR | TOU | FC | FP | HC | R100 | 0.9912 | 5 | 0.4 | 8760 | 151516.2601 | 172285.65 | 174547.8691 | 65533.1035 | 121012.2992 | 28567.5 | 79989 | 39994.5 | 2571.075 | 167344.5726 | 8760 | 1482.4089 | 3334.2981 | 2453.6789 | 7925.2174 | 0 | 0 | 0 | -1182.0367 | 0 | 2054.9804 | 8760 | 785.9224 | 0 | 0 | 790.1071 | 6319.9461 | 1760.8328 | 2842.0433 | 2137.1725 | 636.2896 | 2266.3962 | 8760 | 0 | 285.675 | 0 | 1024.225 | 277898.4231 | 210834.9497 | 6.9 | -314.1618
464 | E | SOR | TOU | FC | FP | HC | R100 | 0.9912 | 13 | 0.65 | 8760 | 144048.1412 | 135102.6 | 153891.9962 | 65533.1035 | 121012.2992 | 28100 | 78680 | 39340 | 2529 | 165010.3768 | 8760 | 1482.4089 | 6146.0183 | 1449.2811 | 6452.1238 | 0 | 0 | 0 | -1260.3335 | 0 | 2351.7426 | 8760 | 786.6003 | 0 | 0 | 790.1071 | 6319.9461 | 1763.1541 | 2854.1722 | 2158.5877 | 636.812 | 4655.0177 | 8760 | 0 | 281 | 0 | 1024.225 | 277806.2257 | 210834.9497 | 182.675 | -316.7583
465 | E | SOR | TOU | FC | FP | HC | R100 | 0.9912 | 11 | 0.55 | 8760 | 144249.8248 | 144765.9 | 159260.1383 | 65533.1035 | 121012.2992 | 28165 | 78862 | 39431 | 2534.85 | 165136.5431 | 8760 | 1482.4089 | 5502.9642 | 1634.8654 | 6892.5661 | 0 | 0 | 0 | -1248.8273 | 0 | 2335.0696 | 8760 | 786.0512 | 0 | 0 | 790.1071 | 6319.9461 | 1762.7833 | 2867.0008 | 2148.6214 | 636.8737 | 4059.8175 | 8760 | 0 | 281.65 | 0 | 1024.225 | 277952.8808 | 210834.9497 | 144.075 | -312.0773
466 | E | SOR | TOU | FC | FP | HC | R100 | 0.9912 | 9 | 0.45 | 8760 | 147527.8541 | 154325.25 | 164570.5343 | 65533.1035 | 121012.2992 | 28255 | 79114 | 39557 | 2542.95 | 165790.4807 | 8760 | 1482.4089 | 4945.3851 | 1879.0205 | 7153.3878 | 0 | 0 | 0 | -1272.6175 | 0 | 2262.6948 | 8760 | 786.5995 | 0 | 0 | 790.1071 | 6319.9461 | 1762.5243 | 2868.9651 | 2146.0671 | 636.8162 | 3607.3349 | 8760 | 0 | 282.55 | 0 | 1024.225 | 277943.726 | 210834.9497 | 105.8 | -319.7285
467 | E | SOR | TOU | FC | FP | HC | R100 | 0.9912 | 7 | 0.35 | 8760 | 147026.4284 | 167112.45 | 171674.0607 | 65533.1035 | 121012.2992 | 28360 | 79408 | 39704 | 2552.4 | 166336.0727 | 8760 | 1482.4089 | 4023.6934 | 2241.0107 | 7791.9478 | 0 | 0 | 0 | -1291.2378 | 0 | 2249.2245 | 8760 | 786.7851 | 0 | 0 | 790.1071 | 6319.9461 | 1761.913 | 2863.3618 | 2143.1938 | 636.6636 | 2728.8357 | 8760 | 0 | 283.6 | 0 | 1024.225 | 277927.0542 | 210834.9497 | 62.65 | -316.2934
468 | E | SOR | TOU | FC | FP | HC | R10 | 0.9912 | 5 | 0.25 | 8760 | 121514.8644 | 192564 | 185812.868 | 65533.1035 | 121012.2992 | 28435 | 79618 | 39809 | 2559.15 | 166835.1588 | 8760 | 1482.4089 | 2501.2294 | 2873.2951 | 8946.1154 | 0 | 0 | 0 | -1395.819 | 0 | 2287.4143 | 8760 | 786.1179 | 0 | 0 | 790.1071 | 6319.9461 | 1761.478 | 2851.85 | 2144.274 | 636.4388 | 1149.5644 | 8760 | 0 | 284.35 | 0 | 1024.225 | 277854.4959 | 210834.9497 | 25.625 | -313.5085
469 | E | SOR | TOU | FC | FP | HC | R10 | 0.9912 | 13 | 0.35 | 8760 | 136122.0097 | 151769.7 | 163150.8789 | 65533.1035 | 121012.2992 | 27892.5 | 78099 | 39049.5 | 2510.325 | 163602.1156 | 8760 | 1482.4089 | 5435.4726 | 1723.4341 | 7208.8803 | 0 | 0 | 0 | -1375.8861 | 0 | 2448.4813 | 8760 | 786.7095 | 0 | 0 | 790.1071 | 6319.9461 | 1763.0011 | 2877.4118 | 2162.4753 | 636.7942 | 3854.6463 | 8760 | 0 | 278.925 | 0 | 1024.225 | 277829.2637 | 210834.9497 | 259.75 | -320.8213
470 | E | SOR | TOU | FC | FP | HC | R10 | 0.9912 | 11 | 0.3 | 8760 | 135180.5845 | 162495.45 | 169109.2317 | 65533.1035 | 121012.2992 | 28047.5 | 78533 | 39266.5 | 2524.275 | 164777.1306 | 8760 | 1482.4089 | 4759.2596 | 1957.8914 | 7800.2802 | 0 | 0 | 0 | -1396.3209 | 0 | 2453.1353 | 8760 | 788.1453 | 0 | 0 | 790.1071 | 6319.9461 | 1762.6817 | 2872.2708 | 2164.4642 | 636.7787 | 3199.5808 | 8760 | 0 | 280.475 | 0 | 1024.225 | 277905.9952 | 210834.9497 | 221.35 | -328.3905
471 | E | SOR | TOU | FC | FP | HC | R10 | 0.9912 | 7 | 0.2 | 8760 | 115097.476 | 181236.15 | 179520.0376 | 65533.1035 | 121012.2992 | 28085 | 78638 | 39319 | 2527.65 | 165081.3392 | 8760 | 1482.4089 | 3544.7305 | 2411.011 | 8584.3892 | 0 | 0 | 0 | -1458.9469 | 0 | 2426.4037 | 8760 | 786.9726 | 0 | 0 | 790.1071 | 6319.9461 | 1762.4786 | 2877.3154 | 2156.8322 | 636.7323 | 2003.2195 | 8760 | 0 | 280.85 | 0 | 1024.225 | 277890.0645 | 210834.9497 | 196.475 | -321.1805
472 | E | SOR | TOU | FC | FP | HC | R600 | 1.1319 | 13 | 1 | 8760 | 145656.1743 | 101615.85 | 135289.4865 | 65533.1035 | 89289.5943 | 33707.5 | 94381 | 47190.5 | 3033.675 | 198841.5663 | 8760 | 1475.3019 | 6269.5928 | 1695.933 | 3978.098 | 0 | 0 | 0 | -1291.6626 | 0 | 2226.0349 | 8760 | 967.5585 | 0 | 0 | 970.2131 | 3803.496 | 2009.0886 | 3706.6264 | 2616.3533 | 821.6208 | 4804.0496 | 8760 | 0 | 337.075 | 0 | 1166.025 | 337553.5231 | 189624.8638 | 144.725 | -327.4101
473 | E | SOR | TOU | FC | FP | HC | R600 | 1.1319 | 11 | 0.85 | 8760 | 147109.0302 | 109378.35 | 139601.699 | 65533.1035 | 89289.5943 | 33955 | 95074 | 47537 | 3055.95 | 199755.8 | 8760 | 1475.3019 | 5698.6347 | 1924.7952 | 4258.6489 | 0 | 0 | 0 | -1260.8192 | 0 | 2197.6261 | 8760 | 966.2752 | 0 | 0 | 970.2131 | 3803.496 | 2008.5231 | 3704.6274 | 2606.3991 | 821.5604 | 4294.6762 | 8760 | 0 | 339.55 | 0 | 1166.025 | 337508.9538 | 189624.8638 | 104.45 | -319.4923
474 | E | SOR | TOU | FC | FP | HC | R600 | 1.1319 | 9 | 0.7 | 8760 | 148389.7356 | 118234.35 | 144521.371 | 65533.1035 | 89289.5943 | 34042.5 | 95319 | 47659.5 | 3063.825 | 200094.5095 | 8760 | 1475.3019 | 5014.5228 | 2186.6701 | 4595.524 | 0 | 0 | 0 | -1224.1174 | 0 | 2157.9375 | 8760 | 965.1757 | 0 | 0 | 970.2131 | 3803.496 | 2007.511 | 3697.4794 | 2595.8008 | 821.2598 | 3683.0857 | 8760 | 0 | 340.425 | 0 | 1166.025 | 337455.6961 | 189624.8638 | 67.875 | -310.8446
475 | E | SOR | TOU | FC | FP | HC | R600 | 1.1319 | 7 | 0.55 | 8760 | 148440.8144 | 128494.35 | 150220.991 | 65533.1035 | 89289.5943 | 34160 | 95648 | 47824 | 3074.4 | 200489.0058 | 8760 | 1475.3019 | 4194.6681 | 2516.5624 | 4986.7845 | 0 | 0 | 0 | -1185.8349 | 0 | 2094.4834 | 8760 | 964.3289 | 0 | 0 | 970.2131 | 3803.496 | 2005.6011 | 3699.3975 | 2588.8287 | 820.3912 | 2955.8885 | 8760 | 0 | 341.6 | 0 | 1166.025 | 337441.0939 | 189624.8638 | 35.6 | -305.3786
476 | E | SOR | TOU | FC | FP | HC | R600 | 1.1319 | 5 | 0.4 | 8760 | 150521.6529 | 138728.7 | 155906.3619 | 65533.1035 | 89289.5943 | 34110 | 95508 | 47754 | 3069.9 | 200556.9297 | 8760 | 1475.3019 | 3291.2493 | 3004.9722 | 5315.6785 | 0 | 0 | 0 | -1194.8868 | 0 | 1976.9164 | 8760 | 964.6924 | 0 | 0 | 970.2131 | 3803.496 | 2002.7081 | 3705.4399 | 2589.0597 | 819.2508 | 2203.9852 | 8760 | 0 | 341.1 | 0 | 1166.025 | 337488.1382 | 189624.8638 | 5.175 | -312.2665
477 | E | SOR | TOU | FC | FP | HC | R600 | 1.1319 | 13 | 0.65 | 8760 | 141838.0354 | 107595 | 138611.015 | 65533.1035 | 89289.5943 | 33700 | 94360 | 47180 | 3033 | 198657.5195 | 8760 | 1475.3019 | 5975.2838 | 1801.884 | 4271.6279 | 0 | 0 | 0 | -1315.4333 | 0 | 2278.0299 | 8760 | 968.1517 | 0 | 0 | 970.2131 | 3803.496 | 2009.445 | 3715.9691 | 2622.7473 | 821.4631 | 4458.5201 | 8760 | 0 | 337 | 0 | 1166.025 | 337497.8745 | 189624.8638 | 176.775 | -325.2425
478 | E | SOR | TOU | FC | FP | HC | R600 | 1.1319 | 11 | 0.55 | 8760 | 142321.0729 | 116145.9 | 143361.1983 | 65533.1035 | 89289.5943 | 33810 | 94668 | 47334 | 3042.9 | 198915.0253 | 8760 | 1475.3019 | 5385.4946 | 2029.0435 | 4586.4312 | 0 | 0 | 0 | -1296.8476 | 0 | 2255.9335 | 8760 | 966.4896 | 0 | 0 | 970.2131 | 3803.496 | 2008.5357 | 3718.8299 | 2610.0943 | 821.1277 | 3922.5268 | 8760 | 0 | 338.1 | 0 | 1166.025 | 337499.8703 | 189624.8638 | 138.65 | -317.6582
479 | E | SOR | TOU | FC | FP | HC | R600 | 1.1319 | 9 | 0.45 | 8760 | 146396.8393 | 122716.35 | 147011.205 | 65533.1035 | 89289.5943 | 33915 | 94962 | 47481 | 3052.35 | 199190.0265 | 8760 | 1475.3019 | 4851.9136 | 2339.9811 | 4740.2165 | 0 | 0 | 0 | -1302.2444 | 0 | 2190.3586 | 8760 | 964.5793 | 0 | 0 | 970.2131 | 3803.496 | 2007.0531 | 3721.815 | 2596.7447 | 820.4178 | 3489.8914 | 8760 | 0 | 339.15 | 0 | 1166.025 | 337523.691 | 189624.8638 | 102.55 | -311.8405
480 | E | SOR | TOU | FC | FP | HC | R600 | 1.1319 | 7 | 0.35 | 8760 | 145590.5247 | 135236.25 | 153966.2413 | 65533.1035 | 89289.5943 | 34040 | 95312 | 47656 | 3063.6 | 200153.0184 | 8760 | 1475.3019 | 3956.5714 | 2768.3077 | 5238.4538 | 0 | 0 | 0 | -1308.4596 | 0 | 2171.0235 | 8760 | 965.4472 | 0 | 0 | 970.2131 | 3803.496 | 2005.425 | 3724.2129 | 2597.2767 | 819.8955 | 2642.041 | 8760 | 0 | 340.4 | 0 | 1166.025 | 337537.1839 | 189624.8638 | 59.85 | -311.23
481 | E | SOR | TOU | FC | FP | HC | R60 | 1.1319 | 5 | 0.25 | 8760 | 120084.8334 | 159976.35 | 167709.825 | 65533.1035 | 89289.5943 | 34005 | 95214 | 47607 | 3060.45 | 200197.4418 | 8760 | 1475.3019 | 2472.5602 | 3504.8919 | 6178.2214 | 0 | 0 | 0 | -1400.225 | 0 | 2175.9258 | 8760 | 966.1075 | 0 | 0 | 970.2131 | 3803.496 | 2003.9913 | 3702.2313 | 2599.6395 | 819.6795 | 1134.5601 | 8760 | 0 | 340.05 | 0 | 1166.025 | 337442.4194 | 189624.8638 | 24.025 | -317.3457
482 | E | SOR | TOU | FC | FP | HC | R60 | 1.1319 | 13 | 0.35 | 8760 | 134470.513 | 120788.55 | 145940.2764 | 65533.1035 | 89289.5943 | 33537.5 | 93905 | 46952.5 | 3018.375 | 197383.1386 | 8760 | 1475.3019 | 5336.0506 | 2145.7086 | 4808.6618 | 0 | 0 | 0 | -1402.0201 | 0 | 2363.0193 | 8760 | 966.3486 | 0 | 0 | 970.2131 | 3803.496 | 2008.5507 | 3727.8475 | 2624.6938 | 820.9482 | 3744.4849 | 8760 | 0 | 335.375 | 0 | 1166.025 | 337491.6499 | 189624.8638 | 251.775 | -316.5392
483 | E | SOR | TOU | FC | FP | HC | R60 | 1.1319 | 11 | 0.3 | 8760 | 133566.1411 | 130430.25 | 151296.4193 | 65533.1035 | 89289.5943 | 33620 | 94136 | 47068 | 3025.8 | 197830.6358 | 8760 | 1475.3019 | 4686.1653 | 2439.8772 | 5243.0756 | 0 | 0 | 0 | -1415.2209 | 0 | 2367.6328 | 8760 | 966.047 | 0 | 0 | 970.2131 | 3803.496 | 2007.6109 | 3727.2315 | 2618.6371 | 820.7294 | 3115.5346 | 8760 | 0 | 336.2 | 0 | 1166.025 | 337471.6799 | 189624.8638 | 214.6 | -316.7471
484 | E | SOR | TOU | FC | FP | HC | R60 | 1.1319 | 7 | 0.2 | 8760 | 114155.8426 | 148898.25 | 161555.7353 | 65533.1035 | 89289.5943 | 33607.5 | 94101 | 47050.5 | 3024.675 | 198126.5131 | 8760 | 1475.3019 | 3525.6465 | 2956.4887 | 5896.5202 | 0 | 0 | 0 | -1469.4026 | 0 | 2313.0358 | 8760 | 966.4449 | 0 | 0 | 970.2131 | 3803.496 | 2006.835 | 3736.255 | 2615.6358 | 820.4888 | 2002.2666 | 8760 | 0 | 336.075 | 0 | 1166.025 | 337486.2389 | 189624.8638 | 183.6 | -324.385
485 | E | SOR | TOU | FC | FP | WC | OFF0 | 0.22447 | 25.5 | 1.9 | 8760 | 152056.2677 | 53250.75 | 108421.7778 | 0 | 73058.5349 | 93162.5 | 321410.625 | 130427.5 | 8384.625 | 43087.6562 | 8760 | 1475.304 | 9991.0142 | 3574.4647 | 908.1437 | 0 | 0 | 0 | -1465.7888 | 0 | 2246.26 | 8760 | 3498.9666 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 18067.4371 | 8756.7025 | 0 | 8385.4319 | 8760 | 23674.3479 | 931.625 | 409.5 | 1821 | 1267113.2783 | 155421.1443 | 219.3 | 478.125
486 | E | SOR | TOU | FC | FP | WC | OFF0 | 0.22447 | 21.5 | 1.6 | 8760 | 148638.3825 | 63560.7 | 114149.1459 | 0 | 73058.5349 | 93915 | 324006.75 | 131481 | 8452.35 | 43435.6875 | 8760 | 1475.304 | 8988.9915 | 4217.6803 | 1088.7129 | 0 | 0 | 0 | -1432.4788 | 0 | 2237.597 | 8760 | 3499.0085 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 18156.0678 | 8719.8815 | 0 | 7434.0872 | 8760 | 23811.4188 | 939.15 | 483.25 | 1821 | 1267166.9068 | 155421.1443 | 177.25 | 478.125
487 | E | SOR | TOU | FC | FP | WC | OFF0 | 0.22447 | 18 | 1.35 | 8760 | 146235.0241 | 74363.4 | 120150.2458 | 0 | 73058.5349 | 94552.5 | 326206.125 | 132373.5 | 8509.725 | 43730.5312 | 8760 | 1475.304 | 7992.8802 | 4931.0039 | 1246.1957 | 0 | 0 | 0 | -1399.9168 | 0 | 2236.9551 | 8760 | 3498.9657 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 18228.6312 | 8690.7562 | 0 | 6480.0876 | 8760 | 23923.7046 | 945.525 | 565.775 | 1821 | 1267094.882 | 155421.1443 | 136.65 | 478.125
488 | E | SOR | TOU | FC | FP | WC | OFF0 | 0.22447 | 14 | 1.05 | 8760 | 143731.5017 | 87770.25 | 127597.9993 | 0 | 73058.5349 | 95177.5 | 328362.375 | 133248.5 | 8565.975 | 44019.5938 | 8760 | 1475.304 | 6684.0076 | 5749.855 | 1474.4201 | 0 | 0 | 0 | -1358.9787 | 0 | 2222.8391 | 8760 | 3498.7801 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 18304.7058 | 8658.9203 | 0 | 5239.0715 | 8760 | 24035.2577 | 951.775 | 654.175 | 1821 | 1267191.8807 | 155421.1443 | 89.925 | 478.125
489 | E | SOR | TOU | FC | FP | WC | OFF0 | 0.22447 | 10 | 0.75 | 8760 | 141129.6321 | 103923 | 136571.151 | 0 | 73058.5349 | 95672.5 | 330070.125 | 133941.5 | 8610.525 | 44248.5312 | 8760 | 1475.304 | 5168.8728 | 6738.8771 | 1820.4907 | 0 | 0 | 0 | -1319.4625 | 0 | 2196.0895 | 8760 | 3499.0388 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 18364.3258 | 8633.9458 | 0 | 3802.4108 | 8760 | 24124.2851 | 956.725 | 744.35 | 1821 | 1267281.5219 | 155421.1443 | 45.95 | 478.125
490 | E | SOR | TOU | FC | FP | WC | OFF0 | 0.22447 | 25.5 | 1.3 | 8760 | 149956.5295 | 58372.65 | 111267.0881 | 0 | 73058.5349 | 92917.5 | 320565.375 | 130084.5 | 8362.575 | 42974.3438 | 8760 | 1475.304 | 9683.8277 | 3784.6517 | 1005.5255 | 0 | 0 | 0 | -1460.573 | 0 | 2270.3494 | 8760 | 3498.9448 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 18054.0106 | 8772.2553 | 0 | 8056.2884 | 8760 | 23648.8374 | 929.175 | 434.3 | 1821 | 1267066.4304 | 155421.1443 | 238.65 | 478.125
491 | E | SOR | TOU | FC | FP | WC | OFF0 | 0.22447 | 21.5 | 1.1 | 8760 | 146771.9834 | 68269.5 | 116764.9715 | 0 | 73058.5349 | 93652.5 | 323101.125 | 131113.5 | 8428.725 | 43314.2812 | 8760 | 1475.304 | 8721.1918 | 4434.2622 | 1189.6478 | 0 | 0 | 0 | -1429.531 | 0 | 2268.3099 | 8760 | 3498.9765 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 18131.146 | 8733.6078 | 0 | 7141.9392 | 8760 | 23770.4038 | 936.525 | 500.025 | 1821 | 1266957.4755 | 155421.1443 | 195.975 | 478.125
492 | E | SOR | TOU | FC | FP | WC | OFF0 | 0.22447 | 18 | 0.9 | 8760 | 144405.6546 | 79069.5 | 122764.5715 | 0 | 73058.5349 | 94257.5 | 325188.375 | 131960.5 | 8483.175 | 43594.0938 | 8760 | 1475.304 | 7738.4536 | 5058.9144 | 1351.367 | 0 | 0 | 0 | -1401.3311 | 0 | 2271.8665 | 8760 | 3498.9807 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 18203.2678 | 8704.0556 | 0 | 6198.312 | 8760 | 23878.7296 | 942.575 | 573.9 | 1821 | 1267187.8155 | 155421.1443 | 156.75 | 478.125
493 | E | SOR | TOU | FC | FP | WC | OFF0 | 0.22447 | 14 | 0.7 | 8760 | 141574.4711 | 93069 | 130541.553 | 0 | 73058.5349 | 94935 | 327525.75 | 132909 | 8544.15 | 43907.4375 | 8760 | 1475.304 | 6466.7558 | 5874.0092 | 1626.2428 | 0 | 0 | 0 | -1371.6567 | 0 | 2262.2124 | 8760 | 3498.9968 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 18277.6472 | 8670.5762 | 0 | 4988.2697 | 8760 | 23995.7313 | 949.35 | 661.875 | 1821 | 1267231.2881 | 155421.1443 | 107.2 | 478.125
494 | E | SOR | TOU | FC | FP | WC | OFF | 0.22447 | 10 | 0.5 | 8760 | 141148.7353 | 108225.45 | 138961.2417 | 0 | 73058.5349 | 95487.5 | 329431.875 | 133682.5 | 8593.875 | 44162.9688 | 8760 | 1475.304 | 5069.0158 | 6873.6383 | 1915.3527 | 0 | 0 | 0 | -1367.4382 | 0 | 2234.9979 | 8760 | 3499.022 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 18344.6708 | 8641.9573 | 0 | 3668.7041 | 8760 | 24094.5882 | 954.875 | 748.85 | 1821 | 1267093.9618 | 155421.1443 | 64.225 | 478.125
495 | E | SOR | TOU | FC | FP | WC | OFF | 0.22447 | 25.5 | 0.65 | 8760 | 144228.8838 | 71181.45 | 118382.6137 | 0 | 73058.5349 | 92320 | 318504 | 129248 | 8308.8 | 42698 | 8760 | 1475.304 | 8908.1523 | 4325.8805 | 1326.8638 | 0 | 0 | 0 | -1454.6635 | 0 | 2343.8581 | 8760 | 3498.9456 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 17995.7303 | 8803.8517 | 0 | 7245.5757 | 8760 | 23559.6582 | 923.2 | 470.7 | 1821 | 1266767.0696 | 155421.1443 | 290.8 | 478.125
496 | E | SOR | TOU | FC | FP | WC | OFF | 0.22447 | 21.5 | 0.55 | 8760 | 140770.2153 | 81834.3 | 124300.4691 | 0 | 73058.5349 | 93062.5 | 321065.625 | 130287.5 | 8375.625 | 43041.4062 | 8760 | 1475.304 | 8012.8153 | 4879.655 | 1535.7634 | 0 | 0 | 0 | -1439.2335 | 0 | 2343.4124 | 8760 | 3498.9829 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 18071.4257 | 8764.0758 | 0 | 6394.9272 | 8760 | 23681.4728 | 930.625 | 538.05 | 1821 | 1266883.7533 | 155421.1443 | 247.825 | 478.125
497 | E | SOR | TOU | FC | FP | WC | OFF | 0.22447 | 18 | 0.45 | 8760 | 140195.5725 | 90788.85 | 129274.8875 | 0 | 73058.5349 | 93680 | 323196 | 131152 | 8431.2 | 43327 | 8760 | 1475.304 | 7179.1294 | 5504.768 | 1654.6246 | 0 | 0 | 0 | -1441.1488 | 0 | 2345.3267 | 8760 | 3498.8146 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 18140.4243 | 8731.8493 | 0 | 5600.9159 | 8760 | 23785.4843 | 936.8 | 603.975 | 1821 | 1266996.8223 | 155421.1443 | 206.275 | 478.125
498 | E | SOR | TOU | FC | FP | WC | OFF | 0.22447 | 14 | 0.35 | 8760 | 136552.9691 | 106845.75 | 138194.7928 | 0 | 73058.5349 | 94312.5 | 325378.125 | 132037.5 | 8488.125 | 43619.5312 | 8760 | 1475.304 | 5948.2794 | 6248.5536 | 1937.4388 | 0 | 0 | 0 | -1444.1086 | 0 | 2342.6185 | 8760 | 3498.9249 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 18212.2858 | 8697.3758 | 0 | 4413.5443 | 8760 | 23899.4628 | 943.125 | 681.475 | 1821 | 1267108.2519 | 155421.1443 | 152.975 | 478.125
499 | E | SOR | TOU | FC | FP | WC | OFF | 0.22447 | 10 | 0.25 | 8760 | 119753.3659 | 130302 | 151225.174 | 0 | 73058.5349 | 94862.5 | 327275.625 | 132807.5 | 8537.625 | 43873.9062 | 8760 | 1475.304 | 4150.3294 | 7262.0306 | 2595.4923 | 0 | 0 | 0 | -1494.3453 | 0 | 2291.6453 | 8760 | 3498.7729 | 0 | 0 | 3498.2739 | 2342.7972 | 0 | 18279.6959 | 8667.6157 | 0 | 2677.7239 | 8760 | 23996.631 | 948.625 | 756.45 | 1821 | 1267325.435 | 155421.1443 | 108.6 | 478.125
500 | E | SOR | TOU | FC | FP | WC | R100 | 1.9476 | 25.5 | 1.9 | 8760 | 165995.9282 | 142028.1 | 157739.2397 | 65533.1035 | 151897.8787 | 41725 | 143951.25 | 58415 | 3755.25 | 19297.8125 | 8760 | 1482.4089 | 11080.5671 | 1814.7705 | 10674.4121 | 0 | 0 | 0 | -1245.3489 | 0 | 2339.9735 | 8760 | 1552.797 | 0 | 0 | 1552.4644 | 12417.9257 | 3316.681 | 7240.8606 | 3902.6631 | 1241.3783 | 9504.5434 | 8760 | 9348.2513 | 417.25 | 0 | 1024.225 | 559184.5977 | 210834.9497 | 283.675
501 | E | SOR | TOU | FC | FP | WC | R100 | 1.9476 | 21.5 | 1.6 | 8760 | 163230.3887 | 150967.8 | 162705.4086 | 65533.1035 | 151897.8787 | 42062.5 | 145115.625 | 58887.5 | 3785.625 | 19453.9062 | 8760 | 1482.4089 | 10065.6711 | 2113.1096 | 11345.7353 | 0 | 0 | 0 | -1211.9526 | 0 | 2320.6426 | 8760 | 1552.0195 | 0 | 0 | 1552.4644 | 12417.9257 | 3308.1927 | 7278.3996 | 3881.3767 | 1240.527 | 8548.1954 | 8760 | 9393.8603 | 420.625 | 0 | 1024.225 | 559193.7981 | 210834.9497 | 230.05
502 | E | SOR | TOU | FC | FP | WC | R100 | 1.9476 | 18 | 1.35 | 8760 | 161551.8027 | 159418.8 | 167400.0956 | 65533.1035 | 151897.8787 | 42395 | 146262.75 | 59353 | 3815.55 | 19607.6875 | 8760 | 1482.4089 | 9064.125 | 2415.2264 | 11967.4452 | 0 | 0 | 0 | -1178.5859 | 0 | 2296.5617 | 8760 | 1552.3765 | 0 | 0 | 1552.4644 | 12417.9257 | 3297.1028 | 7306.5533 | 3867.1156 | 1239.3391 | 7611.0644 | 8760 | 9443.4905 | 423.95 | 0 | 1024.225 | 559258.7085 | 210834.9497 | 174.95
503 | E | SOR | TOU | FC | FP | WC | R100 | 1.9476 | 14 | 1.05 | 8760 | 160208.1325 | 171544.5 | 174136.1465 | 65533.1035 | 151897.8787 | 42622.5 | 147047.625 | 59671.5 | 3836.025 | 19712.9062 | 8760 | 1482.4089 | 7711.8791 | 2831.84 | 12739.6768 | 0 | 0 | 0 | -1137.6007 | 0 | 2259.169 | 8760 | 1551.5372 | 0 | 0 | 1552.4644 | 12417.9257 | 3283.8488 | 7328.8777 | 3851.84 | 1237.5315 | 6351.2098 | 8760 | 9474.408 | 426.225 | 0 | 1024.225 | 559357.488 | 210834.9497 | 106.675
504 | E | SOR | TOU | FC | FP | WC | R100 | 1.9476 | 10 | 0.75 | 8760 | 158611.913 | 185467.05 | 181870.3809 | 65533.1035 | 151897.8787 | 42927.5 | 148099.875 | 60098.5 | 3863.475 | 19853.9688 | 8760 | 1482.4089 | 6097.0941 | 3332.251 | 13693.6757 | 0 | 0 | 0 | -1090.1673 | 0 | 2183.7881 | 8760 | 1551.5164 | 0 | 0 | 1552.4644 | 12417.9257 | 3266.8984 | 7362.881 | 3837.5054 | 1231.7426 | 4870.2726 | 8760 | 9522.2297 | 429.275 | 0 | 1024.225 | 559325.6693 | 210834.9497 | 51.175
505 | E | SOR | TOU | FC | FP | WC | R100 | 1.9476 | 25.5 | 1.3 | 8760 | 163290.6799 | 143638.65 | 158633.9301 | 65533.1035 | 151897.8787 | 41800 | 144210 | 58520 | 3762 | 19332.5 | 8760 | 1482.4089 | 10644.2972 | 1938.6244 | 11088.1662 | 0 | 0 | 0 | -1252.6491 | 0 | 2377.7425 | 8760 | 1552.3581 | 0 | 0 | 1552.4644 | 12417.9257 | 3316.3762 | 7253.4697 | 3898.6959 | 1240.624 | 9029.6162 | 8760 | 9355.0174 | 418 | 0 | 1024.225 | 559169.5515 | 210834.9497 | 310.525
506 | E | SOR | TOU | FC | FP | WC | R100 | 1.9476 | 21.5 | 1.1 | 8760 | 160484.8543 | 153144 | 163914.328 | 65533.1035 | 151897.8787 | 42110 | 145279.5 | 58954 | 3789.9 | 19475.875 | 8760 | 1482.4089 | 9674.9764 | 2229.946 | 11669.3877 | 0 | 0 | 0 | -1223.6597 | 0 | 2361.6428 | 8760 | 1552.6787 | 0 | 0 | 1552.4644 | 12417.9257 | 3306.6697 | 7282.5233 | 3882.6104 | 1239.7592 | 8117.9109 | 8760 | 9402.6455 | 421.1 | 0 | 1024.225 | 559223.5787 | 210834.9497 | 252.725
507 | E | SOR | TOU | FC | FP | WC | R100 | 1.9476 | 18 | 0.9 | 8760 | 158109.5813 | 163235.25 | 169520.2043 | 65533.1035 | 151897.8787 | 42325 | 146021.25 | 59255 | 3809.25 | 19575.3125 | 8760 | 1482.4089 | 8653.1533 | 2535.6471 | 12290.7953 | 0 | 0 | 0 | -1201.0829 | 0 | 2349.0376 | 8760 | 1552.586 | 0 | 0 | 1552.4644 | 12417.9257 | 3298.0582 | 7308.1069 | 3871.0396 | 1238.759 | 7149.1697 | 8760 | 9437.881 | 423.25 | 0 | 1024.225 | 559221.1316 | 210834.9497 | 199.1
508 | E | SOR | TOU | FC | FP | WC | R100 | 1.9476 | 14 | 0.7 | 8760 | 156426.3724 | 175363.65 | 176257.7551 | 65533.1035 | 151897.8787 | 42580 | 146901 | 59612 | 3832.2 | 19693.25 | 8760 | 1482.4089 | 7339.8782 | 2957.2614 | 13146.1612 | 0 | 0 | 0 | -1175.2235 | 0 | 2320.9607 | 8760 | 1551.7549 | 0 | 0 | 1552.4644 | 12417.9257 | 3287.1028 | 7322.9065 | 3854.8523 | 1236.6951 | 5917.6761 | 8760 | 9468.8202 | 425.8 | 0 | 1024.225 | 559136.5729 | 210834.9497 | 134.2
509 | E | SOR | TOU | FC | FP | WC | R10 | 1.9476 | 10 | 0.5 | 8760 | 156167.8847 | 189225.45 | 183958.2417 | 65533.1035 | 151897.8787 | 42857.5 | 147858.375 | 60000.5 | 3857.175 | 19821.5938 | 8760 | 1482.4089 | 5886.6278 | 3588.468 | 14008.6768 | 0 | 0 | 0 | -1196.8776 | 0 | 2224.3389 | 8760 | 1551.8603 | 0 | 0 | 1552.4644 | 12417.9257 | 3272.1934 | 7350.9922 | 3841.9721 | 1229.9425 | 4617.05 | 8760 | 9512.4824 | 428.575 | 0 | 1024.225 | 559348.7234 | 210834.9497 | 74.075
510 | E | SOR | TOU | FC | FP | WC | R10 | 1.9476 | 25.5 | 0.65 | 8760 | 152730.0256 | 156983.4 | 166047.1858 | 65533.1035 | 151897.8787 | 41737.5 | 143994.375 | 58432.5 | 3756.375 | 19303.5938 | 8760 | 1482.4089 | 9402.3935 | 2286.0253 | 12083.3367 | 0 | 0 | 0 | -1278.4688 | 0 | 2467.4286 | 8760 | 1551.9578 | 0 | 0 | 1552.4644 | 12417.9257 | 3306.3081 | 7260.9018 | 3902.2775 | 1239.5708 | 7714.0978 | 8760 | 9350.0419 | 417.375 | 0 | 1024.225 | 559240.7957 | 210834.9497 | 387.5
511 | E | SOR | TOU | FC | FP | WC | R10 | 1.9476 | 21.5 | 0.55 | 8760 | 149039.7747 | 167059.8 | 171644.8126 | 65533.1035 | 151897.8787 | 41930 | 144658.5 | 58702 | 3773.7 | 19392.625 | 8760 | 1482.4089 | 8446.1979 | 2542.7479 | 12833.2071 | 0 | 0 | 0 | -1272.9768 | 0 | 2468.7158 | 8760 | 1551.3552 | 0 | 0 | 1552.4644 | 12417.9257 | 3299.5658 | 7277.8658 | 3887.9358 | 1238.4856 | 6795.1239 | 8760 | 9378.2584 | 419.3 | 0 | 1024.225 | 559180.1991 | 210834.9497 | 329.8
512 | E | SOR | TOU | FC | FP | WC | R10 | 1.9476 | 18 | 0.45 | 8760 | 148729.1683 | 176354.55 | 176808.2184 | 65533.1035 | 151897.8787 | 42150 | 145417.5 | 59010 | 3793.5 | 19494.375 | 8760 | 1482.4089 | 7652.5687 | 2911.1412 | 13325.336 | 0 | 0 | 0 | -1299.3827 | 0 | 2439.7769 | 8760 | 1551.8984 | 0 | 0 | 1552.4644 | 12417.9257 | 3292.2569 | 7297.073 | 3878.0031 | 1236.3273 | 6068.9915 | 8760 | 9408.2167 | 421.5 | 0 | 1024.225 | 559249.5382 | 210834.9497 | 283.575
513 | E | SOR | TOU | FC | FP | WC | R10 | 1.9476 | 14 | 0.35 | 8760 | 145500.9632 | 189519.75 | 184121.7307 | 65533.1035 | 151897.8787 | 42402.5 | 146288.625 | 59363.5 | 3816.225 | 19611.1562 | 8760 | 1482.4089 | 6299.0143 | 3410.7258 | 14257.9839 | 0 | 0 | 0 | -1325.1198 | 0 | 2438.6288 | 8760 | 1551.9477 | 0 | 0 | 1552.4644 | 12417.9257 | 3280.3287 | 7316.4158 | 3865.165 | 1231.2442 | 4763.0825 | 8760 | 9445.3139 | 424.025 | 0 | 1024.225 | 559233.319 | 210834.9497 | 224.975
514 | E | SOR | TOU | FC | FP | WC | R10 | 1.9476 | 10 | 0.25 | 8760 | 120580.9796 | 213819.75 | 197620.8307 | 65533.1035 | 151897.8787 | 42575 | 146883.75 | 59605 | 3831.75 | 19690.9375 | 8760 | 1482.4089 | 4102.5357 | 4257.3493 | 15820.8036 | 0 | 0 | 0 | -1423.4701 | 0 | 2439.2619 | 8760 | 1552.1468 | 0 | 0 | 1552.4644 | 12417.9257 | 3265.1316 | 7325.2857 | 3856.1914 | 1221.9079 | 2573.7116 | 8760 | 9470.0311 | 425.75 | 0 | 1024.225 | 559189.0786 | 210834.9497 | 174.45
515 | E | SOR | TOU | FC | FP | WC | R600 | 2.2241 | 25.5 | 1.9 | 8760 | 162703.3071 | 118122.3 | 144459.1251 | 65533.1035 | 107663.8091 | 51720 | 178434 | 72408 | 4654.8 | 23920.5 | 8760 | 1475.3019 | 10618.4408 | 2332.6116 | 6661.7039 | 0 | 0 | 0 | -1316.1436 | 0 | 2274.9248 | 8760 | 1905.4701 | 0 | 0 | 1906.3509 | 7473.4072 | 3735.0132 | 9228.9713 | 4768.5184 | 1585.3653 | 9002.2576 | 8760 | 11719.7577 | 517.2 | 0 | 1166.025 | 678936.9541 | 189624.8638 | 281.075
516 | E | SOR | TOU | FC | FP | WC | R600 | 2.2241 | 21.5 | 1.6 | 8760 | 160604.212 | 126789.3 | 149273.8041 | 65533.1035 | 107663.8091 | 52057.5 | 179598.375 | 72880.5 | 4685.175 | 24076.5938 | 8760 | 1475.3019 | 9676.1949 | 2693.5326 | 7157.7434 | 0 | 0 | 0 | -1283.9222 | 0 | 2260.7017 | 8760 | 1905.7818 | 0 | 0 | 1906.3509 | 7473.4072 | 3725.6082 | 9264.5628 | 4751.8995 | 1583.2954 | 8116.4565 | 8760 | 11768.6462 | 520.575 | 0 | 1166.025 | 679009.5266 | 189624.8638 | 223.225
517 | E | SOR | TOU | FC | FP | WC | R600 | 2.2241 | 18 | 1.35 | 8760 | 159114.9647 | 135302.4 | 154002.9888 | 65533.1035 | 107663.8091 | 52380 | 180711 | 73332 | 4714.2 | 24225.75 | 8760 | 1475.3019 | 8738.7467 | 3090.5791 | 7645.1907 | 0 | 0 | 0 | -1249.5692 | 0 | 2242.6898 | 8760 | 1905.9412 | 0 | 0 | 1906.3509 | 7473.4072 | 3713.5608 | 9301.3356 | 4736.3291 | 1580.5182 | 7237.5323 | 8760 | 11814.2143 | 523.8 | 0 | 1166.025 | 679140.6395 | 189624.8638 | 169.525
518 | E | SOR | TOU | FC | FP | WC | R600 | 2.2241 | 14 | 1.05 | 8760 | 159002.1386 | 145373.4 | 159597.6158 | 65533.1035 | 107663.8091 | 52675 | 181728.75 | 73745 | 4740.75 | 24362.1875 | 8760 | 1475.3019 | 7507.085 | 3598.1071 | 8224.0057 | 0 | 0 | 0 | -1201.5644 | 0 | 2205.0375 | 8760 | 1905.2098 | 0 | 0 | 1906.3509 | 7473.4072 | 3692.4744 | 9325.531 | 4718.9064 | 1572.7305 | 6100.6218 | 8760 | 11859.296 | 526.75 | 0 | 1166.025 | 679013.3727 | 189624.8638 | 99.775
519 | E | SOR | TOU | FC | FP | WC | R600 | 2.2241 | 10 | 0.75 | 8760 | 157367.1548 | 158795.1 | 167053.6187 | 65533.1035 | 107663.8091 | 52977.5 | 182772.375 | 74168.5 | 4767.975 | 24502.0938 | 8760 | 1475.3019 | 5972.6848 | 4248.1339 | 8897.3649 | 0 | 0 | 0 | -1137.1772 | 0 | 2119.2135 | 8760 | 1906.0748 | 0 | 0 | 1906.3509 | 7473.4072 | 3655.7526 | 9360.8907 | 4707.6882 | 1556.611 | 4711.9616 | 8760 | 11912.565 | 529.775 | 0 | 1166.025 | 679122.4742 | 189624.8638 | 47.225
520 | E | SOR | TOU | FC | FP | WC | R600 | 2.2241 | 25.5 | 1.3 | 8760 | 159214.305 | 121632.3 | 146408.9951 | 65533.1035 | 107663.8091 | 51722.5 | 178442.625 | 72411.5 | 4655.025 | 23921.6562 | 8760 | 1475.3019 | 10172.348 | 2498.7836 | 7063.6061 | 0 | 0 | 0 | -1320.9968 | 0 | 2308.2095 | 8760 | 1906.0313 | 0 | 0 | 1906.3509 | 7473.4072 | 3734.3227 | 9235.2512 | 4773.1474 | 1583.5218 | 8521.8048 | 8760 | 11722.7237 | 517.225 | 0 | 1166.025 | 678839.442 | 189624.8638 | 311.8
521 | E | SOR | TOU | FC | FP | WC | R600 | 2.2241 | 21.5 | 1.1 | 8760 | 157565.8731 | 129705.3 | 150893.6961 | 65533.1035 | 107663.8091 | 52020 | 179469 | 72828 | 4681.8 | 24059.25 | 8760 | 1475.3019 | 9304.3045 | 2840.8492 | 7510.8448 | 0 | 0 | 0 | -1293.0943 | 0 | 2301.361 | 8760 | 1905.5299 | 0 | 0 | 1906.3509 | 7473.4072 | 3724.2761 | 9264.6978 | 4753.7744 | 1580.0666 | 7704.0211 | 8760 | 11760.3853 | 520.2 | 0 | 1166.025 | 679047.0059 | 189624.8638 | 251.075
522 | E | SOR | TOU | FC | FP | WC | R600 | 2.2241 | 18 | 0.9 | 8760 | 156153.082 | 138057.75 | 155533.6368 | 65533.1035 | 107663.8091 | 52317.5 | 180495.375 | 73244.5 | 4708.575 | 24196.8438 | 8760 | 1475.3019 | 8387.1207 | 3223.7134 | 7960.9761 | 0 | 0 | 0 | -1264.4212 | 0 | 2287.8548 | 8760 | 1905.8856 | 0 | 0 | 1906.3509 | 7473.4072 | 3712.0662 | 9294.2064 | 4739.5679 | 1575.4769 | 6842.0357 | 8760 | 11804.7137 | 523.175 | 0 | 1166.025 | 679003.5296 | 189624.8638 | 194.7
523 | E | SOR | TOU | FC | FP | WC | R600 | 2.2241 | 14 | 0.7 | 8760 | 154696.0057 | 148905 | 161559.485 | 65533.1035 | 107663.8091 | 52625 | 181556.25 | 73675 | 4736.25 | 24339.0625 | 8760 | 1475.3019 | 7166.7788 | 3759.3064 | 8529.9004 | 0 | 0 | 0 | -1225.7315 | 0 | 2251.3686 | 8760 | 1906.0472 | 0 | 0 | 1906.3509 | 7473.4072 | 3688.7773 | 9320.4002 | 4725.0505 | 1567.1189 | 5714.0033 | 8760 | 11852.2593 | 526.25 | 0 | 1166.025 | 679056.1424 | 189624.8638 | 129.45
524 | E | SOR | TOU | FC | FP | WC | R60 | 2.2241 | 10 | 0.5 | 8760 | 155376.8675 | 162552.15 | 169140.7296 | 65533.1035 | 107663.8091 | 52860 | 182367 | 74004 | 4757.4 | 24447.75 | 8760 | 1475.3019 | 5783.0482 | 4494.3095 | 9057.056 | 0 | 0 | 0 | -1224.6831 | 0 | 2156.7665 | 8760 | 1905.5863 | 0 | 0 | 1906.3509 | 7473.4072 | 3655.9817 | 9350.1953 | 4711.1313 | 1551.3319 | 4486.1664 | 8760 | 11889.1628 | 528.6 | 0 | 1166.025 | 679158.0537 | 189624.8638 | 71.325
525 | E | SOR | TOU | FC | FP | WC | R60 | 2.2241 | 25.5 | 0.65 | 8760 | 149308.0338 | 132718.5 | 152567.5845 | 65533.1035 | 107663.8091 | 51557.5 | 177873.375 | 72180.5 | 4640.175 | 23845.3438 | 8760 | 1475.3019 | 9084.3592 | 2950.283 | 7815.9332 | 0 | 0 | 0 | -1331.6813 | 0 | 2388.9197 | 8760 | 1905.5946 | 0 | 0 | 1906.3509 | 7473.4072 | 3722.2888 | 9235.1857 | 4781.4547 | 1576.5294 | 7371.9203 | 8760 | 11699.9441 | 515.575 | 0 | 1166.025 | 678857.1927 | 189624.8638 | 383.625
526 | E | SOR | TOU | FC | FP | WC | R60 | 2.2241 | 21.5 | 0.55 | 8760 | 146427.242 | 141103.35 | 157225.524 | 65533.1035 | 107663.8091 | 51782.5 | 178649.625 | 72495.5 | 4660.425 | 23949.4062 | 8760 | 1475.3019 | 8232.3718 | 3279.6313 | 8299.3456 | 0 | 0 | 0 | -1317.7168 | 0 | 2386.6397 | 8760 | 1905.2176 | 0 | 0 | 1906.3509 | 7473.4072 | 3707.5559 | 9247.6238 | 4765.6877 | 1571.6304 | 6563.3967 | 8760 | 11730.0622 | 517.825 | 0 | 1166.025 | 678844.4015 | 189624.8638 | 322.175
527 | E | SOR | TOU | FC | FP | WC | R60 | 2.2241 | 18 | 0.45 | 8760 | 147519.4876 | 149750.1 | 162028.9537 | 65533.1035 | 107663.8091 | 52035 | 179520.75 | 72849 | 4683.15 | 24066.1875 | 8760 | 1475.3019 | 7523.2725 | 3738.2757 | 8598.3111 | 0 | 0 | 0 | -1333.5074 | 0 | 2363.9783 | 8760 | 1906.0273 | 0 | 0 | 1906.3509 | 7473.4072 | 3692.25 | 9274.8193 | 4755.0076 | 1565.1351 | 5920.237 | 8760 | 11770.4536 | 520.35 | 0 | 1166.025 | 678939.9863 | 189624.8638 | 274.025
528 | E | SOR | TOU | FC | FP | WC | R60 | 2.2241 | 14 | 0.35 | 8760 | 144344.9767 | 162122.85 | 168902.2455 | 65533.1035 | 107663.8091 | 52362.5 | 180650.625 | 73307.5 | 4712.625 | 24217.6562 | 8760 | 1475.3019 | 6218.6429 | 4325.4329 | 9306.1597 | 0 | 0 | 0 | -1346.4575 | 0 | 2363.4642 | 8760 | 1906.0136 | 0 | 0 | 1906.3509 | 7473.4072 | 3668.1528 | 9300.2814 | 4737.8252 | 1553.2796 | 4663.1326 | 8760 | 11812.8479 | 523.625 | 0 | 1166.025 | 679059.1528 | 189624.8638 | 213.175
529 | E | SOR | TOU | FC | FP | WC | R60 | 2.2241 | 10 | 0.25 | 8760 | 118882.8483 | 186700.95 | 182555.8352 | 65533.1035 | 107663.8091 | 52542.5 | 181271.625 | 73559.5 | 4728.825 | 24300.9062 | 8760 | 1475.3019 | 4048.4311 | 5339.6309 | 10576.4987 | 0 | 0 | 0 | -1432.797 | 0 | 2327.8218 | 8760 | 1905.4597 | 0 | 0 | 1906.3509 | 7473.4072 | 3641.7024 | 9319.71 | 4725.9821 | 1538.1185 | 2533.8614 | 8760 | 11843.5002 | 525.425 | 0 | 1166.025 | 678946.3933 | 189624.8638 | 168.4
530
531
532
533
534
535
536
537
538
539
540
541
542
543
544
545
546
547
548
549
550
551
552
553
554
555
556
557
558
559
560
561
562
563
564
565
566
567
568
569
570
571
572
573
574
575
576
577
578
579
580
581
582
583
584
585
586
587
588
589
590
591
592
593
594
595
596
597
598
599
600
601
602
603
604
605
606
607
608
609
610
611
612
613
614
615
616
617
618
619
620
621
622
623
624
625
626
627
628
629
630
631
632
633
634
635
636
637
638
639
640
641
642
643
644
645
646
647
648
649
650
651
652
653
654
655
656
657
658
659
660